## Manhole Condition Summary
[36 empty] | Condition Code | Occurrences | Total
[36 empty] | A | 191 | 0
[36 empty] | B | 986 | 0
[36 empty] | C | 543 | 0
[36 empty] | D | 427 | 888856.848
[36 empty] | E | 1 | 7012
[36 empty] | X | 229 | 0
[36 empty] | Total | 2377 | 895868.848
[36 empty] | Design and Contingency -15% |  | 134380.3272
[36 empty] | Total Estimated Cost |  | 1030249.1752
Sanitary Sewer Condition Assessment and Remedial Measures Plan
| Manhole Inspection Basins 1, 2, 3, 5, 6, 7, 8, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, U2 | [20 empty] | Preliminary Rehabilitation Code | [16 empty] | Total | Remedial Measures Plan Recommendation
| Item | Basin | Condition Rating | Manhole ID | Asset ID | GPS Lat | GPS Long | Map Grid | Address | Lid Type | Vent Holes | Inflow Dish | Surface Cover | Surface Material | Manhole Grade | Grade (inches) | Manhole Diameter | MH Material | Rim to Invert (feet) | Wall Coating (sq.ft.) | Wall Condition Rating | 1012 | 1022 | 1023WT | 1024 | 1026 | 1028 | 1020 | 1021 | 1001 | 1205 | 1040 | 1041 | 1110 | 1010 | 1047 | 1505 | 1600
| 1 | 1 | C | SSMHT0000224 | SS.MH.T0000224 | 32.4637 | -95.3788 | I4 | 13161 COUNTY RD 461 | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 10.28 | 135.3968 | [18 empty] | 0
| 2 | 1 | C | SSMHT0015642 | SS.MH.T0015642 | 32.4637 | -95.3817 | I4 | 13161 COUNTY RD 461 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 7.82 | 104.4992 | [18 empty] | 0
| 3 | 1 | X-CNL | SSMHT0015643 | SS.MH.T0015643 | 32.4637 | -95.3807 | I4 | 13161 COUNTY RD 461 |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 4 | 1 | C | SSMHT0015644 | SS.MH.T0015644 | 32.4637 | -95.3797 | I4 | 13161 COUNTY 461 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0
| 5 | 2 | B | SSMHT0000256 | SS.MH.T0000256 | 32.3809 | -95.3314 | L12 | 2700 W. NW LP 323 | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.7 | 77.872 | [18 empty] | 0
| 6 | 2 | C | SSMHT0000257 | SS.MH.T0000257 | 32.3809 | -95.3312 | L12 | 2700 W. NW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Brick | 6.18 | 83.9008 | [18 empty] | 0
| 7 | 2 | C | SSMHT0000258 | SS.MH.T0000258 | 32.3811 | -95.3307 | L12 | 2616 W. NW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | 42 | Brick | 6.48 | 87.6688 | [18 empty] | 0
| 8 | 2 | C | SSMHT0001019 | SS.MH.T0001019 | 32.3699 | -95.3335 | L13 | 2800 BLK VAN HWY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 8.33 | 110.9048 | [18 empty] | 0
| 9 | 2 | B | SSMHT0001049 | SS.MH.T0001049 | 32.37 | -95.3373 | L13 | 180 CHARLOTTE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 36 | Sealed Brick | 3.36 | 48.4816 | [18 empty] | 0
| 10 | 2 | X-CNL | SSMHT0002346 | SS.MH.T0002346 |  |  | L11 | 3450 CORPORATE DR |  |  |  | Creek | Unpaved | Below Grade | [23 empty] | 0
| 11 | 2 | X-CNL | SSMHT0002349 | SS.MH.T0002349 |  |  | L11 | 3611 MINEOLA HWY (69) |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 12 | 2 | D | SSMHT0002370 | SS.MH.T0002370 | 32.3768 | -95.3227 | L12 | 2524 CECIL AVE | Vented | 2 | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Brick | 5.6 | 76.616 | 2 | [10 empty] | 2298.48 |  |  | 280 |  |  |  | 2578.48 | Rehabilitate
| 13 | 2 | C | SSMHT0002384 | SS.MH.T0002384 | 32.3802 | -95.3249 | L12 | NONE COUNTY RD | Vented | 2 | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Brick | 4.97 | 68.7032 | [18 empty] | 0
| 14 | 2 | X-CNO | SSMHT0002385 | SS.MH.T0002385 | 32.3802 | -95.3267 | L12 | NONE COUNTY RD | Vented | 2 |  | Street | Unpaved | Below Grade | 6 | [22 empty] | 0
| 15 | 2 | C | SSMHT0002738 | SS.MH.T0002738 | 32.3703 | -95.3191 | L13 | 1600 BLK W. MLK JR BLVD | Solid | 2 | No | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 7.44 | 99.7264 | [18 empty] | 0
| 16 | 2 | D | SSMHT0002739 | SS.MH.T0002739 | 32.3685 | -95.319 | L13 | 1800 N. GLENWOOD BLVD | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 10.18 | 134.1408 | 2 | [11 empty] | 4024.224 | [5 empty] | 4024.224 | Rehabilitate
| 17 | 2 | D | SSMHT0002740 | SS.MH.T0002740 | 32.3685 | -95.3181 | M13 | 1803 N. HILL AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 32 | Brick | 7.26 | 97.4656 | 2 | [11 empty] | 2923.968 | [5 empty] | 2923.968 | Rehabilitate
| 18 | 2 | D | SSMHT0002741 | SS.MH.T0002741 | 32.3685 | -95.3176 | M13 | 1530 W. NUTBUSH ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 5.34 | 73.3504 | 2 | [7 empty] | 1950 |  |  | 2200.512 | [6 empty] | 4150.512 | Rehabilitate
| 19 | 2 | C | SSMHT0002742 | SS.MH.T0002742 | 32.3685 | -95.3169 | M13 | 1724 N. GASTON AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 32 | Brick | 4.8 | 66.568 | [18 empty] | 0
| 20 | 2 | C | SSMHT0002743 | SS.MH.T0002743 | 32.3685 | -95.3157 | M13 | 1726 N. ENGLEWOOD AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 36 | Brick | 3.62 | 51.7472 | [18 empty] | 0
| 21 | 2 | D | SSMHT0002744 | SS.MH.T0002744 | 32.3685 | -95.3146 | M13 | 1221 W. NUTBUSH ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.1 | 82.896 | 2 | [11 empty] | 2486.88 |  | 280 |  |  |  | 2766.88 | Rehabilitate
| 22 | 2 | X-Buried | SSMHT0002745 | SS.MH.T0002745 | 32.3675 | -95.3189 | L13 | 1615 N. GLENWOOD BLVD |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 23 | 2 | X-CNL | SSMHT0002746 | SS.MH.T0002746 |  |  | L13 | 1800 N GREENWOOD BLVD |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 24 | 2 | C | SSMHT0002747 | SS.MH.T0002747 | 32.3665 | -95.319 | L13 | 1601 N. GLENWOOD BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 40 | Brick | 7.98 | 106.5088 | [18 empty] | 0
| 25 | 2 | C | SSMHT0002748 | SS.MH.T0002748 | 32.366 | -95.3189 | M13 | 1533 N. GLENWOOD BLVD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | 46 | Brick | 6.6 | 89.176 | [18 empty] | 0
| 26 | 2 | D | SSMHT0002749 | SS.MH.T0002749 | 32.3661 | -95.318 | M13 | 1533 N. HILL AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.32 | 85.6592 | 2 | [11 empty] | 2569.776 | [5 empty] | 2569.776 | Rehabilitate
| 27 | 2 | C | SSMHT0002750 | SS.MH.T0002750 | 32.3741 | -95.3216 | L12 | 2322 CECIL AV | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 11 | 144.44 | [18 empty] | 0
| 28 | 2 | C | SSMHT0002751 | SS.MH.T0002751 | 32.3743 | -95.3208 | L12 | 2323 BRECKENRIDGE ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 11.78 | 154.2368 | [18 empty] | 0
| 29 | 2 | C | SSMHT0002752 | SS.MH.T0002752 | 32.3755 | -95.3211 | L12 | 2433 BRECKENRIDGE ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.56 | 76.1136 | [18 empty] | 0
| 30 | 2 | D | SSMHT0002753 | SS.MH.T0002753 | 32.3768 | -95.3217 | L12 | 2524 CECIL AVE | Vented | 1 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.18 | 96.4608 | 2 | [11 empty] | 2893.824 | [5 empty] | 2893.824 | Rehabilitate
| 31 | 2 | D | SSMHT0002754 | SS.MH.T0002754 | 32.3764 | -95.3217 | L12 | 2524 CECIL AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 6.98 | 93.9488 | 2 | [11 empty] | 2818.464 | [5 empty] | 2818.464 | Rehabilitate
| 32 | 2 | B | SSMHT0002755 | SS.MH.T0002755 | 32.376 | -95.3208 | L12 | 1708 NORTHRIDGE DR | Solid |  | No | Yard | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 7.24 | 97.2144 | [18 empty] | 0
| 33 | 2 | X-CNL | SSMHT0002756 | SS.MH.T0002756 |  |  | L12 | 1624 MANOR WAY ST |  |  |  | Yard | Unpaved | [24 empty] | 0
| 34 | 2 | C | SSMHT0002757 | SS.MH.T0002757 | 32.3759 | -95.3191 | L12 | 1527 MANOR WAY ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 36 | Brick | 8.56 | 113.7936 | [18 empty] | 0
| 35 | 2 | C | SSMHT0002758 | SS.MH.T0002758 | 32.375 | -95.3191 | L12 | 2420 N. FENTON AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7 | 94.2 | [18 empty] | 0
| 36 | 2 | C | SSMHT0002759 | SS.MH.T0002759 | 32.3767 | -95.3191 | L12 | 1601 NORTHRIDGE DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 40 | Brick | 4.4 | 61.544 | [18 empty] | 0
| 37 | 2 | C | SSMHT0002760 | SS.MH.T0002760 | 32.3766 | -95.3181 | M12 | 1509 NORTHRIDGE DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.52 | 75.6112 | [18 empty] | 0
| 38 | 2 | C | SSMHT0002761 | SS.MH.T0002761 | 32.3773 | -95.3219 | L12 | 2608 CECIL AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 40 | Brick | 6.54 | 88.4224 | [18 empty] | 0
| 39 | 2 | C | SSMHT0002762 | SS.MH.T0002762 | 32.3774 | -95.3179 | M12 | 1503 W 29TH ST | Vented | 1 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.14 | 108.5184 | [18 empty] | 0
| 40 | 2 | X-CNL | SSMHT0002763 | SS.MH.T0002763 |  |  | M12 | 2401 N ENGLEWOOD ST |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 41 | 2 | C | SSMHT0002764 | SS.MH.T0002764 | 32.3748 | -95.316 | M12 | 2415 N ENGLEWOOD AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.24 | 109.7744 | [18 empty] | 0
| 42 | 2 | C | SSMHT0002765 | SS.MH.T0002765 | 32.375 | -95.3161 | M12 | 2509 N ENGLEWOOD AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.16 | 96.2096 | [18 empty] | 0
| 43 | 2 | C | SSMHT0002766 | SS.MH.T0002766 | 32.3744 | -95.3159 | M12 | 2327 N ENGLEWOOD AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 4.26 | 59.7856 | [18 empty] | 0
| 44 | 2 | C | SSMHT0002767 | SS.MH.T0002767 | 32.3801 | -95.321 | L12 | 2821 STANLEY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 6.4 | 86.664 | [18 empty] | 0
| 45 | 2 | C | SSMHT0002768 | SS.MH.T0002768 | 32.3801 | -95.3222 | L12 | 2824 CECIL AVE | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | 42 | Brick | 8.55 | 113.668 | [18 empty] | 0
| 46 | 2 | C | SSMHT0002769 | SS.MH.T0002769 | 32.3801 | -95.32 | L12 | 2821 COMMONWEALTH DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.78 | 103.9968 | [18 empty] | 0
| 47 | 2 | C | SSMHT0002772 | SS.MH.T0002772 | 32.3789 | -95.321 | L12 | 2801 STANLEY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 40 | Brick | 9.51 | 125.7256 | [18 empty] | 0
| 48 | 2 | D | SSMHT0002773 | SS.MH.T0002773 | 32.3791 | -95.3199 | L12 | 2801 COMMONWEALTH DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.95 | 118.692 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 49 | 2 | B | SSMHT0002778 | SS.MH.T0002778 | 32.3763 | -95.3308 | L12 | 306 JORDAN ST | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 4.12 | 58.0272 | [18 empty] | 0
| 50 | 2 | C | SSMHT0002914 | SS.MH.T0002914 | 32.3732 | -95.3191 | L12 | 1704 W. 24TH ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.12 | 83.1472 | [18 empty] | 0
| 51 | 2 | C | SSMHT0002915 | SS.MH.T0002915 | 32.3722 | -95.319 | L13 | 1629 W. MIMMS ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 10.28 | 135.3968 | [18 empty] | 0
| 52 | 2 | B | SSMHT0002916 | SS.MH.T0002916 | 32.3722 | -95.3185 | M13 | 1629 W. MIMS ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.76 | 116.3056 | [18 empty] | 0
| 53 | 2 | C | SSMHT0002917 | SS.MH.T0002917 | 32.3722 | -95.3175 | M13 | 2201 N. HILL ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 36 | Brick | 5.28 | 72.5968 | [18 empty] | 0
| 54 | 2 | C | SSMHT0002918 | SS.MH.T0002918 | 32.3713 | -95.3185 | M13 | 1614 W. BARRETT ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.7 | 102.992 | [18 empty] | 0
| 55 | 2 | C | SSMHT0002919 | SS.MH.T0002919 | 32.3713 | -95.3168 | M13 | 1400 BLK W. BARRETT ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 5.33 | 73.2248 | [18 empty] | 0
| 56 | 2 | D | SSMHT0002920 | SS.MH.T0002920 | 32.3703 | -95.3185 | M13 | 1621 W. MLK JR BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 9.02 | 119.5712 | 2 | [7 empty] | 1950 |  |  |  | 3587.136 |  | 280 |  |  |  | 5817.136 | Rehabilitate
| 57 | 2 | C | SSMHT0002921 | SS.MH.T0002921 | 32.3713 | -95.3146 | M13 | 2029 W. BARRETT ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 32 | Brick | 4.36 | 61.0416 | [18 empty] | 0
| 58 | 2 | C | SSMHT0002922 | SS.MH.T0002922 | 32.3721 | -95.3145 | M13 | 1221 KENNEDY RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 10.16 | 133.8896 | [18 empty] | 0
| 59 | 2 | C | SSMHT0002923 | SS.MH.T0002923 | 32.3732 | -95.3157 | M12 | 2223 N. ENGLEWOOD AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 5.38 | 73.8528 | [18 empty] | 0
| 60 | 2 | C | SSMHT0002924 | SS.MH.T0002924 | 32.3722 | -95.3168 | M13 | 1420 W. MIMS ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.14 | 95.9584 | [18 empty] | 0
| 61 | 2 | C | SSMHT0002925 | SS.MH.T0002925 | 32.3732 | -95.3216 | L12 | 2228 CECIL AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.9 | 118.064 | [18 empty] | 0
| 62 | 2 | X-Access | SSMHT0002926 | SS.MH.T0002926 |  |  | L12 | 2003 W. MLK JR BLVD |  |  |  | Trees/Woods | Unpaved | Above Grade | [23 empty] | 0
| 63 | 2 | X-Access | SSMHT0002927 | SS.MH.T0002927 | 32.3731 | -95.3238 | L12 | 2203 W. MLK JR. BLVD |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 64 | 2 | C | SSMHT0002928 | SS.MH.T0002928 | 32.3734 | -95.3238 | L12 | 2203 W.MLK JR. BLVD | Vented | 2 | No | Field | Unpaved | Above Grade | 11 | Std 48 Round | Brick | 8.55 | 113.668 | [18 empty] | 0
| 65 | 2 | C | SSMHT0002929 | SS.MH.T0002929 | 32.3722 | -95.3216 | L13 | 2210 N. WOLFORD AVE | Vented | 2 | Yes | Street | Paved - Concrete | At Grade |  | 46 | Brick | 7.48 | 100.2288 | [18 empty] | 0
| 66 | 2 | D | SSMHT0002930 | SS.MH.T0002930 | 32.3712 | -95.3219 | L13 | 2801 N. WOLFORD AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 9.78 | 129.1168 | 2 | [11 empty] | 3873.504 | [5 empty] | 3873.504 | Rehabilitate
| 67 | 2 | C | SSMHT0002931 | SS.MH.T0002931 | 32.3696 | -95.3217 | L13 | 1824 W MARTIN LUTHERKING JR BLVD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 14.5 | 188.4 | [18 empty] | 0
| 68 | 2 | D | SSMHT0002932 | SS.MH.T0002932 | 32.3699 | -95.322 | L13 | 1824 W. MLK JR. BLVD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 3 | 42 | Brick | 14.3 | 185.888 | 2 | [8 empty] | 1000 |  |  | 5576.64 |  | 280 |  |  |  | 6856.64 | Rehabilitate
| 69 | 2 | D | SSMHT0002933 | SS.MH.T0002933 | 32.3708 | -95.3232 | L13 | 2203 W. MLK JR. BLVD | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.2 | 121.832 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
| 70 | 2 | C | SSMHT0002936 | SS.MH.T0002936 | 32.3694 | -95.3229 | L13 | 1813 N. PARKDALE DR | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | 46 | Brick | 5.86 | 79.8816 | [18 empty] | 0
| 71 | 2 | D | SSMHT0002982 | SS.MH.T0002982 | 32.3749 | -95.3155 | M12 | 2500 N CONFEDERATE AVE | Vented | 2 | No | Yard | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 5.84 | 79.6304 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 72 | 2 | X-CNL | SSMHT0002983 | SS.MH.T0002983 |  |  | M13 | 24000 N. CONFEDERATE AVE |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 73 | 2 | C | SSMHT0002984 | SS.MH.T0002984 | 32.374 | -95.3152 | M12 | 2400 N CONFEDERATE AVE | Vented | 2 | No | Yard | Unpaved | Above Grade | 27 | Std 48 Round | Concrete | 14.27 | 185.5112 | [18 empty] | 0
| 74 | 2 | B | SSMHT0003004 | SS.MH.T0003004 | 32.3675 | -95.3146 | M13 | 1703 N. CONFEDERATE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.34 | 60.7904 | [18 empty] | 0
| 75 | 2 | C | SSMHT0003128 | SS.MH.T0003128 | 32.3685 | -95.3181 | M13 | 1803 N. HILL AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 37 | Brick | 5.53 | 75.7368 | [18 empty] | 0
| 76 | 2 | C | SSMHT0007504 | SS.MH.T0007504 | 32.3723 | -95.3235 | L13 | 2203 W. MLK JR. BLVD | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.94 | 118.5664 | [18 empty] | 0
| 77 | 2 | C | SSMHT0008232 | SS.MH.T0008232 | 32.3808 | -95.3355 | L12 | 2925 CLUB LAKE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.05 | 94.828 | [18 empty] | 0
| 78 | 2 | B | SSMHT0008233 | SS.MH.T0008233 | 32.3814 | -95.3355 | L12 | 2931 CLUB LAKE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.15 | 83.524 | [18 empty] | 0
| 79 | 2 | C | SSMHT0008234 | SS.MH.T0008234 | 32.3822 | -95.3351 | L12 | 319 CLUB LAKE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.32 | 98.2192 | [18 empty] | 0
| 80 | 2 | C | SSMHT0008235 | SS.MH.T0008235 | 32.383 | -95.3354 | L12 | 3105 CLUB LAKE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.2 | 172.072 | [18 empty] | 0
| 81 | 2 | C | SSMHT0008236 | SS.MH.T0008236 | 32.384 | -95.3353 | L12 | 3119 CLUB LAKE DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.71 | 178.4776 | [18 empty] | 0
| 82 | 2 | D | SSMHT0008237 | SS.MH.T0008237 | 32.3849 | -95.3351 | L11 | 3137 CLUB LAKE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
| 83 | 2 | C | SSMHT0008238 | SS.MH.T0008238 | 32.3839 | -95.3368 | L12 | 3040 LAKEWOOD DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.63 | 89.5528 | [18 empty] | 0
| 84 | 2 | C | SSMHT0008239 | SS.MH.T0008239 | 32.383 | -95.3367 | L12 | 3034 FAIRLAWN DR | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.06 | 82.3936 | [18 empty] | 0
| 85 | 2 | B | SSMHT0008240 | SS.MH.T0008240 | 32.3821 | -95.3366 | L12 | 3026 PINE HAVEN DR | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 6.65 | 89.804 | [18 empty] | 0
| 86 | 2 | B | SSMHT0008241 | SS.MH.T0008241 | 32.3821 | -95.3394 | K12 | 3238 PINE HAVEN RD | Solid | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.14 | 108.5184 | [18 empty] | 0
| 87 | 2 | C | SSMHT0008242 | SS.MH.T0008242 | 32.3821 | -95.3386 | K12 | 3221 PINE HAVEN RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.2 | 172.072 | [18 empty] | 0
| 88 | 2 | C | SSMHT0008243 | SS.MH.T0008243 | 32.3813 | -95.3369 | L12 | 3106 BERRYHILL DR | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.32 | 85.6592 | [18 empty] | 0
| 89 | 2 | C | SSMHT0008244 | SS.MH.T0008244 | 32.3812 | -95.3384 | K12 | 3218 BERRYHILL DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 6.67 | 90.0552 | [18 empty] | 0
| 90 | 2 | B | SSMHT0008245 | SS.MH.T0008245 | 32.3812 | -95.3394 | K12 | 3238 BERRYHILL DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 5.14 | 70.8384 | [18 empty] | 0
| 91 | 2 | B | SSMHT0008246 | SS.MH.T0008246 | 32.3802 | -95.3393 | K12 | 3240 BENBROOK DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 12.66 | 165.2896 | [18 empty] | 0
| 92 | 2 | C | SSMHT0008247 | SS.MH.T0008247 | 32.3804 | -95.3375 | L12 | 3200 BENBROOK DR | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.34 | 85.9104 | [18 empty] | 0
| 93 | 2 | C | SSMHT0008248 | SS.MH.T0008248 | 32.3804 | -95.3365 | L12 | 3036 BENBROOK DR | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.27 | 122.7112 | [18 empty] | 0
| 94 | 2 | C | SSMHT0008249 | SS.MH.T0008249 | 32.3803 | -95.3412 | K12 | 3324 BENBROOK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.36 | 86.1616 | [18 empty] | 0
| 95 | 2 | D | SSMHT0008250 | SS.MH.T0008250 | 32.3802 | -95.3423 | K12 | 3400 BLK BENBROOK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.77 | 91.3112 | 2 | [11 empty] | 2739.336 |  | 280 |  |  |  | 3019.336 | Rehabilitate
| 96 | 2 | D | SSMHT0008251 | SS.MH.T0008251 | 32.3811 | -95.3423 | K12 | 2928 ORR DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.97 | 93.8232 | 2 |  |  |  | 500 | [7 empty] | 2814.696 |  | 280 |  |  |  | 3594.696 | Rehabilitate
| 97 | 2 | D | SSMHT0008252 | SS.MH.T0008252 | 32.3813 | -95.3423 | K12 | 2932 ORR DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.14 | 83.3984 | [14 empty] | 280 |  |  |  | 280 | Repair
| 98 | 2 | D | SSMHT0008253 | SS.MH.T0008253 | 32.3815 | -95.3423 | K12 | 3000 ORR DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 6.2 | 84.152 | 2 | [11 empty] | 2524.56 | [5 empty] | 2524.56 | Rehabilitate
| 99 | 2 | C | SSMHT0008254 | SS.MH.T0008254 | 32.3819 | -95.3423 | K12 | 3006 ORR DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.86 | 130.1216 | [18 empty] | 0
| 100 | 2 | C | SSMHT0008255 | SS.MH.T0008255 | 32.3819 | -95.3422 | K12 | 3360 PINE HAVEN RD | Vented | 2 | Yes | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.62 | 127.1072 | [18 empty] | 0
| 101 | 2 | C | SSMHT0008256 | SS.MH.T0008256 | 32.382 | -95.3404 | K12 | 3350 PINE HAVEN RD | Vented | 2 | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.56 | 126.3536 | [18 empty] | 0
| 102 | 2 | B | SSMHT0008257 | SS.MH.T0008257 | 32.3789 | -95.3389 | K12 | 3201 W. NW LP 33 | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.78 | 103.9968 | [18 empty] | 0
| 103 | 2 | D | SSMHT0008292 | SS.MH.T0008292 | 32.3819 | -95.3432 | K12 | 3504 PINE HAVEN RD | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 29 | Std 48 Round | Concrete | 9.58 | 126.6048 | 2 | [11 empty] | 3798.144 | [5 empty] | 3798.144 | Rehabilitate
| 104 | 2 | D | SSMHT0008293 | SS.MH.T0008293 | 32.3812 | -95.3432 | K12 | 3504 PINE HAVEN RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 5.67 | 77.4952 | 2 | [6 empty] | 650 |  |  |  | 2324.856 | [6 empty] | 2974.856 | Rehabilitate
| 105 | 2 | C | SSMHT0008595 | SS.MH.T0008595 | 32.3765 | -95.3482 | K12 | 3762 CR 427 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 7.85 | 104.876 | [18 empty] | 0
| 106 | 2 | D | SSMHT0008596 | SS.MH.T0008596 | 32.3778 | -95.3482 | K12 | 3812 CR 427 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 4.42 | 61.7952 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
| 107 | 2 | B | SSMHT0008933 | SS.MH.T0008933 | 32.3819 | -95.3413 | K12 | 3350 PINE HAVEN RD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 5.63 | 76.9928 | [18 empty] | 0
| 108 | 2 | X-CNL | SSMHT0008981 | SS.MH.T0008981 |  |  | L12 | 2505 W. NW LP 323 |  |  |  | Parking Lot | Unpaved | [24 empty] | 0
| 109 | 2 | C | SSMHT0008982 | SS.MH.T0008982 | 32.3834 | -95.3286 | L12 | 3357 POINTE N DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 7.12 | 95.7072 | [18 empty] | 0
| 110 | 2 | D | SSMHT0008983 | SS.MH.T0008983 | 32.3838 | -95.3289 | L12 | 3357 POINTE N DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 13.2 | 172.072 | 2 | [11 empty] | 5162.16 |  | 280 |  |  |  | 5442.16 | Rehabilitate
| 111 | 2 | D | SSMHT0008984 | SS.MH.T0008984 | 32.3861 | -95.3282 | L11 | 3450 CORPORATE DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.06 | 120.0736 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
| 112 | 2 | D | SSMHT0008991 | SS.MH.T0008991 | 32.3861 | -95.3353 | L11 | 3141 LAKE CLUB DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 6.42 | 86.9152 |  |  |  |  | 500 | [5 empty] | 725 | [7 empty] | 1225 | Repair
| 113 | 2 | B | SSMHT0008992 | SS.MH.T0008992 | 32.389 | -95.3368 | L11 | 3141 LAKE CLUB DR | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 6.74 | 90.9344 | [18 empty] | 0
| 114 | 2 | D | SSMHT0008993 | SS.MH.T0008993 | 32.3888 | -95.335 | L11 | 3728 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.53 | 100.8568 | 2 | [6 empty] | 650 |  |  |  |  | 3025.704 |  | 280 |  |  |  | 3955.704 | Rehabilitate
| 115 | 2 | B | SSMHT0008994 | SS.MH.T0008994 | 32.3899 | -95.3358 | L11 | 6205 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.9 | 130.624 | [18 empty] | 0
| 116 | 2 | C | SSMHT0008995 | SS.MH.T0008995 | 32.3906 | -95.3364 | L11 | 6263 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 7.61 | 101.8616 | [18 empty] | 0
| 117 | 2 | C | SSMHT0008997 | SS.MH.T0008997 | 32.3823 | -95.3332 | L12 | 3300 MINEOLA HWY (69) | Vented | 2 | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.84 | 117.3104 | [18 empty] | 0
| 118 | 2 | B | SSMHT0008998 | SS.MH.T0008998 | 32.3856 | -95.3349 | L11 | 3141 LAKE CLUB DR | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 8.72 | 115.8032 | [18 empty] | 0
| 119 | 2 | C | SSMHT0008999 | SS.MH.T0008999 | 32.3862 | -95.3364 | L11 | 3141 LAKE CLUB DR | Vented | 2 | Yes | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 12.59 | 164.4104 | [18 empty] | 0
| 120 | 2 | C | SSMHT0009000 | SS.MH.T0009000 | 32.3872 | -95.3368 | L11 | 3141 CLUB LAKE DR | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 12.38 | 161.7728 | [18 empty] | 0
| 121 | 2 | D | SSMHT0009001 | SS.MH.T0009001 | 32.3878 | -95.3371 | L11 | 3141 LAKE CLUB DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 6.87 | 92.5672 | 2 | [11 empty] | 2777.016 | [5 empty] | 2777.016 | Rehabilitate
| 122 | 2 | C | SSMHT0009002 | SS.MH.T0009002 | 32.3892 | -95.3364 | L11 | 3141 LAKE CLUB DR | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 16 | Std 48 Round | Concrete | 10.74 | 141.1744 | [18 empty] | 0
| 123 | 2 | X-CNL | SSMHT0009003 | SS.MH.T0009003 |  |  | L11 | NONE MINEOLA HWY (69) |  |  |  | Drainage Ditch | Unpaved | [24 empty] | 0
| 124 | 2 | X-CNL | SSMHT0009004 | SS.MH.T0009004 |  |  | L11 | 3720 MINEOLA HWY (69) |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 125 | 2 | B | SSMHT0009005 | SS.MH.T0009005 | 32.3852 | -95.3337 | L11 | 3364 MINEOLA HWY (69) | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 5.25 | 72.22 | [18 empty] | 0
| 126 | 2 | X-CNL | SSMHT0009006 | SS.MH.T0009006 |  |  | L12 | 3300 W. NW LP 323 |  |  |  | Parking Lot | Unpaved | [24 empty] | 0
| 127 | 2 | B | SSMHT0009007 | SS.MH.T0009007 | 32.3819 | -95.3342 | L12 | 2739 W. NW LP 323 | Solid |  | No | Parking Lot | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 4.3 | 60.288 | [18 empty] | 0
| 128 | 2 | D | SSMHT0009008 | SS.MH.T0009008 | 32.3841 | -95.3333 | L11 | 3364 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | Above Grade | 23 | Std 48 Round | Brick | 10.74 | 141.1744 | 2 | [11 empty] | 4235.232 | [5 empty] | 4235.232 | Rehabilitate
| 129 | 2 | D | SSMHT0009009 | SS.MH.T0009009 | 32.3845 | -95.3331 | L11 | 3364 MINEOLA HWY (69) | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.14 | 108.5184 | 2 | [11 empty] | 3255.552 | [5 empty] | 3255.552 | Rehabilitate
| 130 | 2 | D | SSMHT0009010 | SS.MH.T0009010 | 32.3878 | -95.3336 | L11 | 3611 MINEOLA HWY (69) | Vented | 2 | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 7.4 | 99.224 | 2 | [11 empty] | 2976.72 | [5 empty] | 2976.72 | Rehabilitate
| 131 | 2 | B | SSMHT0009150 | SS.MH.T0009150 | 32.3828 | -95.3422 | K12 | 3035 ORR DR | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 7.56 | 101.2336 | [18 empty] | 0
| 132 | 2 | B | SSMHT0009151 | SS.MH.T0009151 | 32.3829 | -95.3413 | K12 | 3035 HORSESHOE TRL | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.53 | 88.2968 | [18 empty] | 0
| 133 | 2 | X-CNO | SSMHT0009152 | SS.MH.T0009152 | 32.3793 | -95.3377 | L12 | 3201 W. NW LP 323 | Solid |  |  | Parking Lot | Unpaved | Below Grade | 6 | [22 empty] | 0
| 134 | 2 | C | SSMHT0009153 | SS.MH.T0009153 | 32.3786 | -95.3387 | K12 | 3220 W. NW LP 323 | Vented | 2 | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Brick | 6.8 | 91.688 | [18 empty] | 0
| 135 | 2 | X-CNO | SSMHT0009154 | SS.MH.T0009154 | 32.3793 | -95.3367 | L12 | 3100 W. NW LP 323 | Solid |  |  | Road Shoulder | Unpaved | At Grade | [23 empty] | 0
| 136 | 2 | B | SSMHT0009155 | SS.MH.T0009155 | 32.3795 | -95.3359 | L12 | 3000 W. NW LP 323 | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.6 | 164.536 | [18 empty] | 0
| 137 | 2 | B | SSMHT0009167 | SS.MH.T0009167 | 32.3764 | -95.3318 | L12 | 3201 W. GENTRY PKWY | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 6.62 | 89.4272 | [18 empty] | 0
| 138 | 2 | C | SSMHT0009174 | SS.MH.T0009174 | 32.3722 | -95.3157 | M13 | 2209 N. ENGLEWOOD AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 24 | Concrete | 3.55 | 50.868 | [18 empty] | 0
| 139 | 2 | B | SSMHT0009175 | SS.MH.T0009175 | 32.3732 | -95.3158 | M12 | 1408 E. 24TH ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.98 | 68.8288 | [18 empty] | 0
| 140 | 2 | B | SSMHT0009176 | SS.MH.T0009176 | 32.3738 | -95.3168 | M12 | 2311 N. GASTON AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.64 | 77.1184 | [18 empty] | 0
| 141 | 2 | B | SSMHT0009177 | SS.MH.T0009177 | 32.3743 | -95.317 | M12 | 2317 N GASTON AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.8 | 66.568 | [18 empty] | 0
| 142 | 2 | B | SSMHT0009178 | SS.MH.T0009178 | 32.3744 | -95.317 | M12 | 1419 SOUTHRIDGE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.79 | 66.4424 | [18 empty] | 0
| 143 | 2 | C | SSMHT0009179 | SS.MH.T0009179 | 32.3756 | -95.3181 | M12 | 1506 MANOR WAY ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.38 | 86.4128 | [18 empty] | 0
| 144 | 2 | B | SSMHT0009193 | SS.MH.T0009193 | 32.3672 | -95.3157 | M13 | 1624 N. ENGLEWOOD AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.29 | 60.1624 | [18 empty] | 0
| 145 | 2 | C | SSMHT0009194 | SS.MH.T0009194 | 32.3703 | -95.3168 | M13 | 1400 BLK W. MLK JR BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 7.58 | 101.4848 | [18 empty] | 0
| 146 | 2 | X-CNL | SSMHT0009197 | SS.MH.T0009197 |  |  | L13 | 1709 N. GLENWOOD BLVD |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 147 | 2 | X-Buried | SSMHT0009198 | SS.MH.T0009198 | 32.3692 | -95.321 | L13 | 1806 NANCY DR |  |  |  | Road Shoulder | Unpaved | Below Grade | 5 | [22 empty] | 0
| 148 | 2 | B | SSMHT0009199 | SS.MH.T0009199 | 32.366 | -95.3216 | L13 | 1500 BLK N. WOLFORD AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.98 | 93.9488 | [18 empty] | 0
| 149 | 2 | C | SSMHT0009200 | SS.MH.T0009200 | 32.3661 | -95.3229 | L13 | 1604 N. PARKDALE DR | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Brick | 7 | 94.2 | [18 empty] | 0
| 150 | 2 | C | SSMHT0009201 | SS.MH.T0009201 | 32.3672 | -95.3228 | L13 | 1700 BLK N. PARKDALE DR | Vented | 2 | Yes | Street | Paved - Asphalt | Below Grade | 1 | 37 | Brick | 6.2 | 84.152 | [18 empty] | 0
| 151 | 2 | B | SSMHT0009202 | SS.MH.T0009202 | 32.3672 | -95.3216 | L13 | 1621 N WOLFORD AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 37 | Brick | 6.36 | 86.1616 | [18 empty] | 0
| 152 | 2 | X-CNO | SSMHT0009203 | SS.MH.T0009203 | 32.3682 | -95.3228 | L13 | 1721 N. PARKDALE DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 153 | 2 | C | SSMHT0009204 | SS.MH.T0009204 | 32.3683 | -95.3216 | L13 | 2197 WOLFORD AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 6.96 | 93.6976 | [18 empty] | 0
| 154 | 2 | D | SSMHT0009205 | SS.MH.T0009205 | 32.3692 | -95.3218 | L13 | 1806 NANCY DR | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Brick | 7.2 | 96.712 | 2 | [6 empty] | 650 |  |  |  |  | 2901.36 |  | 280 |  |  |  | 3831.36 | Rehabilitate
| 155 | 2 | C | SSMHT0009215 | SS.MH.T0009215 | 32.3737 | -95.3322 | L12 | 3025 W. GENTRY PKWY | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Brick | 9.36 | 123.8416 | [18 empty] | 0
| 156 | 2 | C | SSMHT0009241 | SS.MH.T0009241 | 32.3812 | -95.3261 | L12 | 2300 W. NW LP 323 | Solid |  | No | Yard | Unpaved | Above Grade | 3 | 32 | Brick | 3 | 43.96 | [18 empty] | 0
| 157 | 2 | B | SSMHT0009243 | SS.MH.T0009243 | 32.3827 | -95.3237 | L12 | 2202 W. NW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 10.16 | 133.8896 | [18 empty] | 0
| 158 | 2 | C | SSMHT0009244 | SS.MH.T0009244 | 32.3827 | -95.3238 | L12 | 2202 W. NW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 11.08 | 145.4448 | [18 empty] | 0
| 159 | 2 | C | SSMHT0009245 | SS.MH.T0009245 | 32.383 | -95.3233 | L12 | 2202 W. NW LP 323 | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.61 | 89.3016 | [18 empty] | 0
| 160 | 2 | B | SSMHT0009246 | SS.MH.T0009246 | 32.3838 | -95.3235 | L12 | 2202 W. NW LP 323 | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.48 | 125.3488 | [18 empty] | 0
| 161 | 2 | C | SSMHT0009247 | SS.MH.T0009247 | 32.3838 | -95.3237 | L12 | 2202 W. NW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 11.9 | 155.744 | [18 empty] | 0
| 162 | 2 | B | SSMHT0009248 | SS.MH.T0009248 | 32.3837 | -95.3239 | L12 | 2202 W. NW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 11.8 | 154.488 | [18 empty] | 0
| 163 | 2 | B | SSMHT0009268 | SS.MH.T0009268 | 32.3872 | -95.3285 | L11 | 3475 CORPORATE DR | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.64 | 102.2384 | [18 empty] | 0
| 164 | 2 | C | SSMHT0009280 | SS.MH.T0009280 | 32.3906 | -95.3271 | L11 | 2811 PUBLIC RD | Solid |  | No | Yard | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.24 | 109.7744 | [18 empty] | 0
| 165 | 2 | B | SSMHT0009281 | SS.MH.T0009281 | 32.3906 | -95.3274 | L11 | 2811 PUBLIC RD | Solid |  | No | Yard | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 5.84 | 79.6304 | [18 empty] | 0
| 166 | 2 | X-CNL | SSMHT0009295 | SS.MH.T0009295 | [33 empty] | 0
| 167 | 2 | X-CNL | SSMHT0009478 | SS.MH.T0009478 |  |  | M12 | 2711 STALEY DR |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 168 | 2 | X-Buried | SSMHT0009807 | SS.MH.T0009807 | 32.3802 | -95.3427 | K12 | 3504 BENBROOK DR |  |  |  | Road Shoulder | Paved - Asphalt | [24 empty] | 0
| 169 | 2 | X-CNL | SSMHT0009845 | SS.MH.T0009845 |  |  | K12 | 3035 LIVELY LN |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 170 | 2 | D | SSMHT0009861 | SS.MH.T0009861 | 32.3796 | -95.3368 | L12 | 3111 W. NW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 5 | CO 6" | Other | 7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 171 | 2 | X-Buried | SSMHT0010103 | SS.MH.T0010103 | 32.3659 | -95.317 | M13 | 1514 W. HARMONY ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 172 | 2 | X-CNL | SSMHT0010104 | SS.MH.T0010104 |  |  | M13 | 1719 N. CONFEDERATE AVE |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 173 | 2 | D | SSMHT0010121 | SS.MH.T0010121 | 32.368 | -95.319 | L13 | 1715 N. GLENWOOD BLVD | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 7.8 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 174 | 2 | X-Buried | SSMHT0010341 | SS.MH.T0010341 | 32.371 | -95.3335 | L13 | 1907 CUSHING DR |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 175 | 2 | D | SSMHT0010473 | SS.MH.T0010473 | 32.3839 | -95.3374 | L12 | 3108 LAKEWOOD DR | Solid |  | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 11.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 176 | 2 | B | SSMHT0010474 | SS.MH.T0010474 | 32.3817 | -95.3394 | K12 | 3238 PINE HAVEN RD | Vented | 2 | No | Driveway | Paved - Concrete | At Grade |  | CO 6" | Other | [20 empty] | 0
| 177 | 2 | D | SSMHT0010475 | SS.MH.T0010475 | 32.3805 | -95.3358 | L12 | 3016 BENBROOK DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | CO 6" | Other | 10.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 178 | 2 | D | SSMHT0010489 | SS.MH.T0010489 | 32.3759 | -95.3482 | K12 | 3750 CR 427 | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other |  |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
| 179 | 2 | D | SSMHT0011340 | SS.MH.T0011340 | 32.3745 | -95.3175 | M12 | 1424 SOUTHRIDGE DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 180 | 2 | B | SSMHT0012398 | SS.MH.T0012398 | 32.3763 | -95.3317 | L12 | 3201 W. GENTRY PKWY | Vented | 2 | Yes | Drainage Ditch | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 4.12 | 58.0272 | [18 empty] | 0
| 181 | 2 | D | SSMHT0012508 | SS.MH.T0012508 | 32.3693 | -95.319 | L13 | 1825 N. GLENWOOD BLVD | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 5.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 182 | 2 | B | SSMHT0013010 | SS.MH.T0013010 | 32.3863 | -95.3282 | L11 | 3450 CORPORATE DR | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 8.34 | 111.0304 | [18 empty] | 0
| 183 | 2 | B | SSMHT0013011 | SS.MH.T0013011 | 32.3859 | -95.3292 | L11 | 3475 CORPORATE DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 13.28 | 173.0768 | [18 empty] | 0
| 184 | 2 | X-Buried | SSMHT0013012 | SS.MH.T0013012 | 32.3861 | -95.3291 | L11 | 3475 CORPORATE DR |  |  |  | Road Shoulder | Unpaved | Below Grade | 10 | [22 empty] | 0
| 185 | 2 | C | SSMHT0013265 | SS.MH.T0013265 | 32.3801 | -95.334 | L12 | 3220 W. GENTRY PKWY | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | 42 | Brick | 6.63 | 89.5528 | [18 empty] | 0
| 186 | 2 | D | SSMHT0013422 | SS.MH.T0013422 | 32.3736 | -95.3229 | L12 | 2203 W. MLK JR. BLVD | Solid |  | No | Creek | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 8.47 | 112.6632 | [7 empty] | 650 |  |  | 725 |  |  | 700 |  | 900 |  |  | 2975 | Repair
| 187 | 2 | D | SSMHT0013423 | SS.MH.T0013423 | 32.372 | -95.3235 | L13 | 2203 W. MLK JR. BLVD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | Std 48 Round | Brick | 8.24 | 109.7744 | 2 | [6 empty] | 650 |  |  |  |  | 3293.232 |  | 280 |  |  |  | 4223.232 | Rehabilitate
| 188 | 2 | X-Buried | SSMHT0013430 | SS.MH.T0013430 | 32.383 | -95.3382 | L12 | 3208 FAIRLAWN DR |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 189 | 2 | D | SSMHT0013528 | SS.MH.T0013528 | X-CNL | X-CNL | NA | 274' US of 02927 |  |  |  | Trees/Woods | Unpaved | [23 empty] | 2600 | 2600 | Repair
| 190 | 2 | X-CNL | SSMHT0013862 | SS.MH.T0013862 |  |  | M13 | 2400 N. CONFEDERATE AVE |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 191 | 2 | B | SSMHT0013970 | SS.MH.T0013970 | 32.3708 | -95.3348 | L13 | 2825 BALDWIN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.12 | 70.5872 | [18 empty] | 0
| 192 | 2 | C | SSMHT0014099 | SS.MH.T0014099 | 32.3775 | -95.3317 | L12 | 3211 W. GENTRY PKWY | Vented | 2 | No | Parking Lot | Paved - Asphalt | At Grade |  | 42 | Brick | 6.31 | 85.5336 | [18 empty] | 0
| 193 | 2 | D | SSMHT0014316 | SS.MH.T0014316 | 32.3737 | -95.3146 | M13 | 2400 N. CONFEDERATE AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | 42 | Brick | 6.34 | 85.9104 | 2 | [6 empty] | 650 |  |  |  |  | 2577.312 | [5 empty] | 3227.312 | Rehabilitate
| 194 | 2 | C | SSMHT0015247 | SS.MH.T0015247 | 32.3801 | -95.3226 | L12 | 2824 CECIL AVE | Solid |  | No | Alley | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 10.89 | 143.0584 | [18 empty] | 0
| 195 | 2 | B | SSMHT0015249 | SS.MH.T0015249 | 32.3701 | -95.3222 | L13 | 1800 BLK MLK JR. BLVD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 6 | Std 48 Round | Concrete | 14.34 | 186.3904 | [18 empty] | 0
| 196 | 2 | B | SSMHT0015291 | SS.MH.T0015291 | 32.381 | -95.3235 | L12 | 2202 W NW LOOP 323 | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 9.72 | 128.3632 | [18 empty] | 0
| 197 | 2 | A | SSMHT0015292 | SS.MH.T0015292 | 32.3811 | -95.3236 | L12 | 2202 W NW LOOP 323 | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 16 | Std 48 Round | Concrete | 9.44 | 124.8464 | [18 empty] | 0
| 198 | 2 | B | SSMHT0015293 | SS.MH.T0015293 | 32.3823 | -95.3231 | L12 | 3159 POINTE N DR | Solid |  | Yes | Trees/Woods | Unpaved | At Grade | 17 | Std 48 Round | Concrete | 8.88 | 117.8128 | [18 empty] | 0
| 199 | 2 | C | SSMHT0015298 | SS.MH.T0015298 | 32.3835 | -95.3242 | L12 | 2202 W. NW LP 323 | Solid |  | No | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 9.84 | 129.8704 | [18 empty] | 0
| 200 | 2 | C | SSMHT0015299 | SS.MH.T0015299 | 32.3837 | -95.3239 | L12 | 2202 W. NW LP 323 | Solid |  | No | Yard | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 11.22 | 147.2032 | [18 empty] | 0
| 201 | 2 | B | SSMHT0015308 | SS.MH.T0015308 | 32.3692 | -95.3196 | L13 | 1710 NANCY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | [20 empty] | 0
| 202 | 2 | X-Buried | SSMHT0015521 | SS.MH.T0015521 | 32.3742 | -95.3203 | L12 | 2339 BRECKENRIDGE ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 203 | 2 | B | SSMHT0015526 | SS.MH.T0015526 | 32.383 | -95.3373 | L12 | 3107 FAIRLAWN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.13 | 95.8328 | [18 empty] | 0
| 204 | 2 | B | SSMHT0015527 | SS.MH.T0015527 | 32.3803 | -95.3406 | K12 | 3316 BENBROOK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.43 | 99.6008 | [18 empty] | 0
| 205 | 2 | D | SSMHT0015530 | SS.MH.T0015530 | 32.389 | -95.3351 | L11 | 3802 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.26 | 97.4656 | 2 | [11 empty] | 2923.968 |  | 280 |  |  |  | 3203.968 | Rehabilitate
| 206 | 2 | X-CNO | SSMHT0015469 | SS.MH.T0015469 | 32.3821 | -95.3238 | L12 | 2202 W. NW LP 323 | Solid |  |  | Trees/Woods | Unpaved | Above Grade | 6 | [22 empty] | 0
| 207 | 2 | D | SSMHT0015532 | SS.MH.T0015532 | 32.3827 | -95.324 | L12 | 2202 W. NW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 10.92 | 143.4352 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
| 208 | 2 | X-CNO | SSMHT0015533 | SS.MH.T0015533 | 32.3828 | -95.324 | L12 | 2202 W. NW LP 323 | Solid |  |  | Parking Lot | Unpaved | Below Grade | 7 | [22 empty] | 0
| 209 | 2 | D | SSMHT0015649 | SS.MH.T0015649 | 32.3827 | -95.3246 | L12 | 2202 W. NW LP 323 | Solid |  | No | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 8.26 | 110.0256 | 2 | [6 empty] | 650 |  |  |  |  | 3300.768 | [5 empty] | 3950.768 | Rehabilitate
| 210 | 2 | C | SSMHT0015658 | SS.MH.T0015658 | 32.3722 | -95.3323 | L12 | 2901 W. GENTRY PKWY | Vented | 2 | Yes | Road Shoulder | Unpaved | Above Grade | 10 | Std 48 Round | Brick | 8.5 | 113.04 | [18 empty] | 0
| 211 | 2 | B | SSMHT0015665 | SS.MH.T0015665 | 32.3718 | -95.3346 | L13 | 2820 CUSHING DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.17 | 96.3352 | [18 empty] | 0
| 212 | 2 | B | SSMHT0015680 | SS.MH.T0015680 | 32.3796 | -95.3354 | L12 | 3000 W. NW LP 323 | Vented | 2 | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.75 | 153.86 | [18 empty] | 0
| 213 | 3 | X-Access | SSMHT0000259 | SS.MH.T0000259 |  |  | H15 | 700 SKYWAY BLVD |  |  |  | Other | Paved - Concrete | [24 empty] | 0
| 214 | 3 | X-Access | SSMHT0000260 | SS.MH.T0000260 |  |  | H14 | 700 SKYWAY BLVD | Solid |  |  | Other | Unpaved | At Grade | [23 empty] | 0
| 215 | 3 | C | SSMHT0000261 | SS.MH.T0000261 | 32.3521 | -95.4081 | H14 | 700 SKYWAY BLVD | Solid |  | No | Parking Lot | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 13.78 | 179.3568 | [18 empty] | 0
| 216 | 3 | B | SSMHT0000262 | SS.MH.T0000262 | 32.3625 | -95.4101 | H14 | 700 SKYWAY BLVD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 8.12 | 108.2672 | [18 empty] | 0
| 217 | 3 | D | SSMHT0000263 | SS.MH.T0000263 | 32.3625 | -95.4087 | H14 | 700 SKYWAY BLVD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 25.36 | 324.8016 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 218 | 3 | C | SSMHT0000264 | SS.MH.T0000264 | 32.3624 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.34 | 173.8304 | [18 empty] | 0
| 219 | 3 | C | SSMHT0007480 | SS.MH.T0007480 | 32.3527 | -95.4089 | H14 | 700 SKYWAY BLVD | Solid |  | No | Parking Lot | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 9.88 | 130.3728 | [18 empty] | 0
| 220 | 3 | A | SSMHT0007481 | SS.MH.T0007481 | 32.3528 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 10.92 | 143.4352 | [18 empty] | 0
| 221 | 3 | C | SSMHT0007482 | SS.MH.T0007482 | 32.3538 | -95.4074 | H14 | 700 SKYWAY DR | Solid |  | No | Field | Unpaved | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 222 | 3 | D | SSMHT0007483 | SS.MH.T0007483 | 32.355 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 10.32 | 135.8992 | [7 empty] | 650 | [7 empty] | 900 |  |  | 1550 | Repair
| 223 | 3 | D | SSMHT0007484 | SS.MH.T0007484 | 32.3563 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 13.84 | 180.1104 | 2 | [6 empty] | 650 |  |  |  |  | 5403.312 | [5 empty] | 6053.312 | Rehabilitate
| 224 | 3 | D | SSMHT0007485 | SS.MH.T0007485 | 32.3575 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 23 | 295.16 | 2 | [11 empty] | 8854.8 | [5 empty] | 8854.8 | Rehabilitate
| 225 | 3 | D | SSMHT0007486 | SS.MH.T0007486 | 32.3587 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 13.6 | 177.096 | 2 | [6 empty] | 650 |  |  |  |  | 5312.88 | [5 empty] | 5962.88 | Rehabilitate
| 226 | 3 | D | SSMHT0007487 | SS.MH.T0007487 | 32.36 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 15.05 | 195.308 | 2 | [11 empty] | 5859.24 | [5 empty] | 5859.24 | Rehabilitate
| 227 | 3 | B | SSMHT0007488 | SS.MH.T0007488 | 32.3612 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 26 | Std 48 Round | Concrete | 12.28 | 160.5168 | [18 empty] | 0
| 228 | 3 | X-Access | SSMHT0007489 | SS.MH.T0007489 |  |  | H14 | 700 SKYWAY BLVD |  |  |  | Other | Unpaved | At Grade | [23 empty] | 0
| 229 | 3 | X-Access | SSMHT0007490 | SS.MH.T0007490 |  |  | H14 | 700 SKYWAY BLVD |  |  |  | Other | Unpaved | At Grade | [23 empty] | 0
| 230 | 3 | C | SSMHT0007491 | SS.MH.T0007491 | 32.3628 | -95.4036 | H14 | 353 AIRPORT DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 17.78 | 229.5968 | [18 empty] | 0
| 231 | 3 | B | SSMHT0008259 | SS.MH.T0008259 | 32.3697 | -95.3961 | I13 | 738 DUKE PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.66 | 165.2896 | [18 empty] | 0
| 232 | 3 | X-CNO | SSMHT0008268 | SS.MH.T0008268 | 32.3727 | -95.3925 | I13 | 13390 OLD DALLAS HWY | Solid |  |  | Road Shoulder | Unpaved | At Grade | [23 empty] | 0
| 233 | 3 | C | SSMHT0008315 | SS.MH.T0008315 | 32.3605 | -95.3911 | I14 | 584 DIXIE DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 8 | Std 48 Round | Concrete | 9.12 | 120.8272 | [18 empty] | 0
| 234 | 3 | C | SSMHT0008316 | SS.MH.T0008316 | 32.3601 | -95.391 | I14 | 584 DIXIE DR | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 235 | 3 | B | SSMHT0008317 | SS.MH.T0008317 | 32.359 | -95.3909 | I14 | 584 DIXIE DR | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 11.36 | 148.9616 | [18 empty] | 0
| 236 | 3 | C | SSMHT0008318 | SS.MH.T0008318 | 32.3579 | -95.3909 | I14 | 704 DIXIE DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 16.98 | 219.5488 | [18 empty] | 0
| 237 | 3 | B | SSMHT0008319 | SS.MH.T0008319 | 32.3568 | -95.3909 | I14 | 1320 DIXIE DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 6.4 | 86.664 | [18 empty] | 0
| 238 | 3 | B | SSMHT0008320 | SS.MH.T0008320 | 32.356 | -95.3909 | I14 | 1594 DIXIE DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0
| 239 | 3 | C | SSMHT0008425 | SS.MH.T0008425 | 32.362 | -95.4017 | H14 | 335 AIRPORT DR | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 32 | Std 48 Round | Concrete | 8.88 | 117.8128 | [18 empty] | 0
| 240 | 3 | D | SSMHT0008426 | SS.MH.T0008426 | 32.3614 | -95.401 | H14 | 150 AIRPORT DR | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 19 | Std 48 Round | Concrete | 7.98 | 106.5088 | 2 | [6 empty] | 650 |  |  |  |  | 3195.264 | [5 empty] | 3845.264 | Rehabilitate
| 241 | 3 | C | SSMHT0008427 | SS.MH.T0008427 | 32.3605 | -95.4002 | H14 | 209 AIRPORT DR | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 24 | Std 48 Round | Concrete | 9.1 | 120.576 | [18 empty] | 0
| 242 | 3 | C | SSMHT0008428 | SS.MH.T0008428 | 32.3605 | -95.4001 | H14 | 209 AIRPORT DR | Solid |  | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.92 | 93.1952 | [18 empty] | 0
| 243 | 3 | B | SSMHT0008429 | SS.MH.T0008429 | 32.36 | -95.3994 | H14 | 209 AIRPORT DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.16 | 133.8896 | [18 empty] | 0
| 244 | 3 | C | SSMHT0008430 | SS.MH.T0008430 | 32.3599 | -95.3996 | H14 | 209 AIRPORT DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 245 | 3 | X-CNO | SSMHT0008431 | SS.MH.T0008431 | 32.359 | -95.3989 | H14 | 150 AIRPORT DR | Vented | 2 |  | Parking Lot | Paved - Asphalt | At Grade | [23 empty] | 0
| 246 | 3 | D | SSMHT0008432 | SS.MH.T0008432 | 32.3593 | -95.3987 | H14 | 150 AIRPORT DR | Solid |  |  | Sidewalk | Paved - Concrete | At Grade |  |  |  | 5.34 | 73.3504 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
| 247 | 3 | C | SSMHT0008433 | SS.MH.T0008433 | 32.3594 | -95.3987 | H14 | 209 AIRPORT DR | Solid |  | No | Yard | Unpaved | Above Grade | 2 |  |  | 4.53 | 63.1768 | [18 empty] | 0
| 248 | 3 | B | SSMHT0008488 | SS.MH.T0008488 | 32.3644 | -95.3935 | I13 | 336 WELLINGTON PL BLVD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.24 | 97.2144 | [18 empty] | 0
| 249 | 3 | C | SSMHT0008496 | SS.MH.T0008496 | 32.3639 | -95.3959 | I13 | NONE WELLINGTON PL BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.88 | 80.1328 | [18 empty] | 0
| 250 | 3 | B | SSMHT0008497 | SS.MH.T0008497 | 32.3644 | -95.3942 | I13 | 310 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.35 | 111.156 | [18 empty] | 0
| 251 | 3 | C | SSMHT0008498 | SS.MH.T0008498 | 32.3644 | -95.3959 | I13 | 349 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.24 | 72.0944 | [18 empty] | 0
| 252 | 3 | B | SSMHT0008499 | SS.MH.T0008499 | 32.3644 | -95.3968 | H13 | 422 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.5 | 138.16 | [18 empty] | 0
| 253 | 3 | B | SSMHT0008500 | SS.MH.T0008500 | 32.3645 | -95.3969 | H13 | 422 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.49 | 138.0344 | [18 empty] | 0
| 254 | 3 | C | SSMHT0008501 | SS.MH.T0008501 | 32.3653 | -95.3969 | H13 | 542 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.72 | 90.6832 | [18 empty] | 0
| 255 | 3 | B | SSMHT0008502 | SS.MH.T0008502 | 32.3665 | -95.3969 | H13 | 602 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.82 | 79.3792 | [18 empty] | 0
| 256 | 3 | B | SSMHT0008503 | SS.MH.T0008503 | 32.3675 | -95.3969 | H13 | 652 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 257 | 3 | B | SSMHT0008504 | SS.MH.T0008504 | 32.368 | -95.3969 | H13 | 682 PRINCESS PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.94 | 106.0064 | [18 empty] | 0
| 258 | 3 | X-CNO | SSMHT0008505 | SS.MH.T0008505 | 32.3687 | -95.3969 | H13 | 712 PRINCESS LN | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 259 | 3 | B | SSMHT0008506 | SS.MH.T0008506 | 32.3689 | -95.3969 | H13 | 761 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.66 | 77.3696 | [18 empty] | 0
| 260 | 3 | B | SSMHT0008507 | SS.MH.T0008507 | 32.3691 | -95.3965 | I13 | 781 SPENCER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.61 | 76.7416 | [18 empty] | 0
| 261 | 3 | B | SSMHT0008508 | SS.MH.T0008508 | 32.3691 | -95.396 | I13 | 714 DUKE PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.58 | 88.9248 | [18 empty] | 0
| 262 | 3 | B | SSMHT0008509 | SS.MH.T0008509 | 32.3687 | -95.3978 | H13 | 710 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [18 empty] | 0
| 263 | 3 | B | SSMHT0008510 | SS.MH.T0008510 | 32.3686 | -95.3979 | H13 | 710 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.8 | 91.688 | [18 empty] | 0
| 264 | 3 | C | SSMHT0008511 | SS.MH.T0008511 | 32.3675 | -95.3979 | H13 | 650 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.1 | 57.776 | [18 empty] | 0
| 265 | 3 | B | SSMHT0008512 | SS.MH.T0008512 | 32.3665 | -95.3979 | H13 | 590 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.56 | 176.5936 | [18 empty] | 0
| 266 | 3 | C | SSMHT0008513 | SS.MH.T0008513 | 32.366 | -95.3979 | H13 | 570 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.27 | 72.4712 | [18 empty] | 0
| 267 | 3 | B | SSMHT0008514 | SS.MH.T0008514 | 32.3654 | -95.3979 | H13 | 430 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.98 | 93.9488 | [18 empty] | 0
| 268 | 3 | B | SSMHT0008515 | SS.MH.T0008515 | 32.3652 | -95.3978 | H13 | 431 SPENCER LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.61 | 89.3016 | [18 empty] | 0
| 269 | 3 | C | SSMHT0008516 | SS.MH.T0008516 | 32.3612 | -95.4013 | H14 | 150 AIRPORT DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | [18 empty] | 0
| 270 | 3 | D | SSMHT0009747 | SS.MH.T0009747 | 32.3531 | -95.4095 | H14 | 700 SKYWAY BLVD | None |  | No | Parking Lot | Unpaved | Above Grade | 7 | CO 6" | Other |  |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
| 271 | 3 | D | SSMHT0010483 | SS.MH.T0010483 | 32.3644 | -95.3955 | I13 | 345 PRINCESS PL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 272 | 3 | B | SSMHT0010484 | SS.MH.T0010484 | 32.3652 | -95.3974 | H13 | 411 SPENCER LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | [20 empty] | 0
| 273 | 3 | B | SSMHT0013437 | SS.MH.T0013437 | 32.3615 | -95.3961 | I14 | 235 AIRPORT DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 2.97 | 43.5832 | [18 empty] | 0
| 274 | 3 | D | SSMHT0013517 | SS.MH.T0013517 | 32.3659 | -95.3926 | I13 | 13390 OLD DALLAS HWY | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 11.58 | 151.7248 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 275 | 3 | B | SSMHT0013771 | SS.MH.T0013771 | 32.3651 | -95.3936 | I13 | 569 WELLINGTON PL BLVD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 276 | 3 | X-CNL | SSMHT0013772 | SS.MH.T0013772 |  |  | I13 | 569 WELLINGTON PL BLVD |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 277 | 3 | B | SSMHT0013773 | SS.MH.T0013773 | 32.3656 | -95.3935 | I13 | NONE DUKE PL | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 12.58 | 164.2848 | [18 empty] | 0
| 278 | 3 | B | SSMHT0013774 | SS.MH.T0013774 | 32.3656 | -95.3931 | I13 | 438 DUKE PL | Solid |  | Yes | Yard | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 18.12 | 233.8672 | [18 empty] | 0
| 279 | 3 | A | SSMHT0013775 | SS.MH.T0013775 | 32.3651 | -95.3943 | I13 | 552 WELLINGTON PL BLVD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 280 | 3 | B | SSMHT0013776 | SS.MH.T0013776 | 32.365 | -95.3948 | I13 | 536 WELLINGTON PL BLVD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.18 | 109.0208 | [18 empty] | 0
| 281 | 3 | B | SSMHT0013777 | SS.MH.T0013777 | 32.365 | -95.396 | I13 | 473 WELLINGTON PL BLVD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.06 | 120.0736 | [18 empty] | 0
| 282 | 3 | D | SSMHT0013778 | SS.MH.T0013778 | 32.3648 | -95.396 | I13 | 449 WELLINGTON PL BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 283 | 3 | B | SSMHT0013901 | SS.MH.T0013901 | 32.3636 | -95.3935 | I13 | 328 DUKE PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.03 | 144.8168 | [18 empty] | 0
| 284 | 3 | B | SSMHT0013902 | SS.MH.T0013902 | 32.3634 | -95.3937 | I13 | 328 DUKE PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.14 | 158.7584 | [18 empty] | 0
| 285 | 3 | B | SSMHT0013903 | SS.MH.T0013903 | 32.3634 | -95.3937 | I13 | 328 DUKE PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13 | 169.56 | [18 empty] | 0
| 286 | 3 | B | SSMHT0013904 | SS.MH.T0013904 | 32.3631 | -95.394 | I13 | 328 DUKE PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Concrete | 7.42 | 99.4752 | [18 empty] | 0
| 287 | 3 | B | SSMHT0013905 | SS.MH.T0013905 | 32.3639 | -95.3935 | I13 | 328 DUKE PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.43 | 124.7208 | [18 empty] | 0
| 288 | 3 | D | SSMHT0015611 | SS.MH.T0015611 | 32.3658 | -95.3923 | I13 | 13390 OLD DALLAS HWY | Solid |  | No | Field | Unpaved | Above Grade | 16 | Std 48 Round | Concrete | 12.16 | 159.0096 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 289 | 3 | C | SSMHT0015620 | SS.MH.T0015620 | 32.3722 | -95.3923 | I13 | 13390 OLD DALLAS HWY | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 11.36 | 148.9616 | [18 empty] | 0
| 290 | 3 | D | SSMHT0015621 | SS.MH.T0015621 | 32.3644 | -95.3918 | I13 | 13390 OLD DALLAS HWY | Solid |  | No | Field | Unpaved | Above Grade | 34 | CO 6" | PVC | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 291 | 3 | X-CNO | SSMHT0015622 | SS.MH.T0015622 | 32.3579 | -95.3898 | I14 | 961 DIXIE DR | Solid |  |  | Yard | Unpaved | Below Grade | 2 | CO 6" | Other | [20 empty] | 0
| 292 | 3 | B | SSMHT0015623 | SS.MH.T0015623 | 32.3597 | -95.3982 | H14 | 209 AIRPORT DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.62 | 152.2272 | [18 empty] | 0
| 293 | 3 | B | SSMHT0015624 | SS.MH.T0015624 | 32.3606 | -95.3972 | H14 | 209 AIRPORT DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.7 | 102.992 | [18 empty] | 0
| 294 | 3 | B | SSMHT0015625 | SS.MH.T0015625 | 32.3599 | -95.3997 | H14 | 209 AIRPORT DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 7.67 | 102.6152 | [18 empty] | 0
| 295 | 5 | B | SSMHT0000524 | SS.MH.T0000524 | 32.319 | -95.364 | J17 | 2890 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.1 | 133.136 | [18 empty] | 0
| 296 | 5 | C | SSMHT0000525 | SS.MH.T0000525 | 32.3193 | -95.364 | J17 | 2902 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.22 | 134.6432 | [18 empty] | 0
| 297 | 5 | C | SSMHT0000526 | SS.MH.T0000526 | 32.3201 | -95.3629 | J17 | 2931 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.68 | 115.3008 | [18 empty] | 0
| 298 | 5 | C | SSMHT0000610 | SS.MH.T0000610 | 32.3174 | -95.3561 | K18 | 4055 HOGAN DR | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.16 | 108.7696 | [18 empty] | 0
| 299 | 5 | C | SSMHT0000616 | SS.MH.T0000616 | 32.3168 | -95.352 | K18 | 2801 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.38 | 86.4128 | [18 empty] | 0
| 300 | 5 | C | SSMHT0000617 | SS.MH.T0000617 | 32.3168 | -95.3518 | K18 | 2801 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.4 | 99.224 | [18 empty] | 0
| 301 | 5 | B | SSMHT0000618 | SS.MH.T0000618 | 32.3166 | -95.3518 | K18 | 2801 WEXFORD DR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 12.05 | 157.628 | [18 empty] | 0
| 302 | 5 | X-Buried | SSMHT0000619 | SS.MH.T0000619 | 32.3166 | -95.3521 | K18 | 1359 LAMB DR |  |  |  | Yard | Unpaved | Below Grade | 14 | [22 empty] | 0
| 303 | 5 | X-Access | SSMHT0001010 | SS.MH.T0001010 |  |  | K15 | 3801 CHANDLER HWY |  |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 304 | 5 | X-CNO | SSMHT0001090 | SS.MH.T0001090 | 32.3462 | -95.3422 | K15 | 3801 CHANDLER HWY | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 305 | 5 | X-CNO | SSMHT0001091 | SS.MH.T0001091 | 32.3456 | -95.3414 | K15 | 3701 CHANDLER HWY | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 306 | 5 | B | SSMHT0001158 | SS.MH.T0001158 | 32.3116 | -95.3406 | K18 | 3210 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.1 | 120.576 | [18 empty] | 0
| 307 | 5 | B | SSMHT0001159 | SS.MH.T0001159 | 32.3123 | -95.3409 | K18 | 3200 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 11.6 | 151.976 | [18 empty] | 0
| 308 | 5 | C | SSMHT0001160 | SS.MH.T0001160 | 32.3084 | -95.3386 | L18 | 3029 MC CORMICK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.44 | 162.5264 | [18 empty] | 0
| 309 | 5 | D | SSMHT0001161 | SS.MH.T0001161 | 32.3441 | -95.3513 | NA | 4550STATE HWY 31 W | Vented | 1 | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 13.13 | 171.1928 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
| 310 | 5 | B | SSMHT0001162 | SS.MH.T0001162 | 32.3159 | -95.3415 | K18 | 3010 S. SW LP 323 | Solid |  | No | Parking Lot | Unpaved | At Grade |  | Std 48 Round | Concrete | 23.46 | 300.9376 | [18 empty] | 0
| 311 | 5 | C | SSMHT0001163 | SS.MH.T0001163 | 32.3161 | -95.3415 | K18 | 3010 S. SW LP 323 | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 24.45 | 313.372 | [18 empty] | 0
| 312 | 5 | C | SSMHT0001164 | SS.MH.T0001164 | 32.3365 | -95.332 | L16 | 2850 W. SHAW ST | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.34 | 173.8304 | [18 empty] | 0
| 313 | 5 | C | SSMHT0001165 | SS.MH.T0001165 | 32.3366 | -95.3318 | L16 | 2850 W. SHAW ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 4.81 | 66.6936 | [18 empty] | 0
| 314 | 5 | X-CNL | SSMHT0001174 | SS.MH.T0001174 |  |  | K15 | 600 BLK S. SW LP 323 |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 315 | 5 | D | SSMHT0001175 | SS.MH.T0001175 | 32.3421 | -95.3404 | K15 | NONE S. SW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Brick | 10.8 | 141.928 | 2 | [11 empty] | 4257.84 |  | 280 |  |  |  | 4537.84 | Rehabilitate
| 316 | 5 | X-CNO | SSMHT0001176 | SS.MH.T0001176 | 32.3418 | -95.3407 | K15 | 3600 BLK BELLWOOD RD | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 317 | 5 | C | SSMHT0001177 | SS.MH.T0001177 | 32.3421 | -95.3435 | K15 | 3925 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.52 | 113.2912 | [18 empty] | 0
| 318 | 5 | D | SSMHT0001178 | SS.MH.T0001178 | 32.3421 | -95.3419 | K15 | 3807 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.88 | 168.0528 | 2 | [11 empty] | 5041.584 | [5 empty] | 5041.584 | Rehabilitate
| 319 | 5 | D | SSMHT0001179 | SS.MH.T0001179 | 32.3421 | -95.3428 | K15 | 3917 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.2 | 134.392 | 2 | [11 empty] | 4031.76 | [5 empty] | 4031.76 | Rehabilitate
| 320 | 5 | B | SSMHT0001180 | SS.MH.T0001180 | 32.339 | -95.3435 | K16 | 900 WHITESIDE RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.44 | 87.1664 | [18 empty] | 0
| 321 | 5 | B | SSMHT0001181 | SS.MH.T0001181 | 32.338 | -95.3435 | K16 | 919 WHITESIDE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.03 | 94.5768 | [18 empty] | 0
| 322 | 5 | B | SSMHT0001182 | SS.MH.T0001182 | 32.3366 | -95.3435 | K16 | 1012 WHITESIDE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.98 | 93.9488 | [18 empty] | 0
| 323 | 5 | B | SSMHT0001183 | SS.MH.T0001183 | 32.3251 | -95.3417 | K17 | 2695 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 13.3 | 173.328 | [18 empty] | 0
| 324 | 5 | B | SSMHT0001188 | SS.MH.T0001188 | 32.329 | -95.3404 | K17 | 1822 S SOUTHWEST LOOP 323 | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.36 | 123.8416 | [18 empty] | 0
| 325 | 5 | D | SSMHT0001189 | SS.MH.T0001189 | 32.3216 | -95.3332 | L17 | NONE TOL AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 8.5 | 113.04 | 2 | [6 empty] | 650 |  |  |  |  | 3391.2 | [5 empty] | 4041.2 | Rehabilitate
| 326 | 5 | D | SSMHT0001190 | SS.MH.T0001190 | 32.3215 | -95.3302 | L17 | 2502 WALTON RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 11 | 144.44 | 2 | [6 empty] | 650 |  |  |  |  | 4333.2 | [5 empty] | 4983.2 | Rehabilitate
| 327 | 5 | D | SSMHT0001191 | SS.MH.T0001191 | 32.3218 | -95.33 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 10.86 | 142.6816 | 2 | [11 empty] | 4280.448 | [5 empty] | 4280.448 | Rehabilitate
| 328 | 5 | D | SSMHT0001192 | SS.MH.T0001192 | 32.3208 | -95.3304 | L17 | 2505 WALTON RD | Bolted |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 8.05 | 107.388 | 2 | [6 empty] | 650 |  |  |  |  | 3221.64 | [5 empty] | 3871.64 | Rehabilitate
| 329 | 5 | D | SSMHT0001193 | SS.MH.T0001193 | 32.3201 | -95.3302 | L17 | 2500 BLK WALTON RD | Bolted |  | No | Field | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 19.28 | 248.4368 | 2 | [6 empty] | 650 |  |  |  |  | 7453.104 | [5 empty] | 8103.104 | Rehabilitate
| 330 | 5 | B | SSMHT0001194 | SS.MH.T0001194 | 32.3216 | -95.3337 | L17 | 2702 TOL AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 10.96 | 143.9376 | [18 empty] | 0
| 331 | 5 | B | SSMHT0001195 | SS.MH.T0001195 | 32.3216 | -95.3346 | L17 | 2704 TOL AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.9 | 80.384 | [18 empty] | 0
| 332 | 5 | X-Access | SSMHT0001196 | SS.MH.T0001196 |  |  | L17 | 3262 EARL CAMPBELL PKWY |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 333 | 5 | B | SSMHT0001203 | SS.MH.T0001203 | 32.3207 | -95.3317 | L17 | 2720 DEPRIEST AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.28 | 72.5968 | [18 empty] | 0
| 334 | 5 | B | SSMHT0001204 | SS.MH.T0001204 | 32.3193 | -95.3343 | L17 | 2922 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.16 | 71.0896 | [18 empty] | 0
| 335 | 5 | B | SSMHT0001205 | SS.MH.T0001205 | 32.3184 | -95.3343 | L17 | 2806 MOOREHEAD ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.24 | 72.0944 | [18 empty] | 0
| 336 | 5 | B | SSMHT0001206 | SS.MH.T0001206 | 32.3193 | -95.3318 | L17 | 2800 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.31 | 72.9736 | [18 empty] | 0
| 337 | 5 | B | SSMHT0001207 | SS.MH.T0001207 | 32.3193 | -95.331 | L17 | 2620 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.32 | 98.2192 | [18 empty] | 0
| 338 | 5 | B | SSMHT0001208 | SS.MH.T0001208 | 32.3182 | -95.3311 | L17 | 2800 WALTON RD | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.44 | 62.0464 | [18 empty] | 0
| 339 | 5 | B | SSMHT0001209 | SS.MH.T0001209 | 32.3182 | -95.3291 | L17 | 2900 RHINEHART ST | Solid |  | No | Sidewalk | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.38 | 86.4128 | [18 empty] | 0
| 340 | 5 | C | SSMHT0001210 | SS.MH.T0001210 | 32.3193 | -95.3296 | L17 | 2000 BLK WALTON RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.6 | 139.416 | [18 empty] | 0
| 341 | 5 | B | SSMHT0001211 | SS.MH.T0001211 | 32.3193 | -95.329 | L17 | 2500 BLK WALTON RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.62 | 89.4272 | [18 empty] | 0
| 342 | 5 | B | SSMHT0001212 | SS.MH.T0001212 | 32.3193 | -95.3306 | L17 | 2620 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.4 | 99.224 | [18 empty] | 0
| 343 | 5 | B | SSMHT0001213 | SS.MH.T0001213 | 32.3193 | -95.3279 | L17 | 2322 WALTON RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.02 | 81.8912 | [18 empty] | 0
| 344 | 5 | C | SSMHT0001214 | SS.MH.T0001214 | 32.3184 | -95.3279 | L17 | 2400 BLK HALL ST | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.18 | 109.0208 | [18 empty] | 0
| 345 | 5 | B | SSMHT0001215 | SS.MH.T0001215 | 32.314 | -95.331 | L18 | 2801 SARA ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.56 | 76.1136 | [18 empty] | 0
| 346 | 5 | D | SSMHT0001217 | SS.MH.T0001217 | 32.316 | -95.331 | L18 | 3000 BLK BUDDIE ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Concrete | 11.69 | 153.1064 | 2 | [11 empty] | 4593.192 | [5 empty] | 4593.192 | Rehabilitate
| 347 | 5 | D | SSMHT0001218 | SS.MH.T0001218 | 32.3157 | -95.3298 | L18 | 2516 FRANCHEL ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.18 | 159.2608 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
| 348 | 5 | D | SSMHT0001219 | SS.MH.T0001219 | 32.3366 | -95.34 | K16 | 1000 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 5.72 | 78.1232 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
| 349 | 5 | B | SSMHT0001220 | SS.MH.T0001220 | 32.3365 | -95.3345 | L16 | 3107 W. SHAW ST | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 10.02 | 132.1312 | [18 empty] | 0
| 350 | 5 | D | SSMHT0001225 | SS.MH.T0001225 | 32.3188 | -95.3311 | L17 | 2800 WALTON RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 8.6 | 114.296 | 2 | [6 empty] | 650 |  |  |  |  | 3428.88 | [5 empty] | 4078.88 | Rehabilitate
| 351 | 5 | X-CNL | SSMHT0001226 | SS.MH.T0001226 |  |  | K16 | 1000 S. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 352 | 5 | B | SSMHT0001232 | SS.MH.T0001232 | 32.3134 | -95.3374 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 353 | 5 | C | SSMHT0001233 | SS.MH.T0001233 | 32.3134 | -95.3367 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 354 | 5 | C | SSMHT0001234 | SS.MH.T0001234 | 32.3468 | -95.3461 | K15 | 4121 OLD CHANDLER RD | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.62 | 101.9872 | [18 empty] | 0
| 355 | 5 | D | SSMHT0001236 | SS.MH.T0001236 | 32.3159 | -95.3323 | L18 | 2835 LUTHER ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Fiberglass | 10.83 | 142.3048 | [15 empty] | 900 |  |  | 900 | Repair
| 356 | 5 | C | SSMHT0001237 | SS.MH.T0001237 | 32.3235 | -95.3334 | L17 | NONE TOL AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 12.74 | 166.2944 | [18 empty] | 0
| 357 | 5 | B | SSMHT0001238 | SS.MH.T0001238 | 32.319 | -95.3258 | L17 | 2214 DAVIS AVE | Solid |  | No | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 7.43 | 99.6008 | [18 empty] | 0
| 358 | 5 | D | SSMHT0001240 | SS.MH.T0001240 | 32.3469 | -95.3436 | K15 | 352 WHITESIDE RD | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.06 | 69.8336 | 2 | [10 empty] | 2095.008 | [6 empty] | 2095.008 | Rehabilitate
| 359 | 5 | B | SSMHT0001246 | SS.MH.T0001246 | 32.3163 | -95.3417 | K18 | 3010 S. SW LP 323 | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 22.75 | 292.02 | [18 empty] | 0
| 360 | 5 | B | SSMHT0001312 | SS.MH.T0001312 | 32.3417 | -95.3474 | K15 | 4197 BELLWOOD RD | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 7.05 | 94.828 | [18 empty] | 0
| 361 | 5 | D | SSMHT0001313 | SS.MH.T0001313 | 32.3418 | -95.3469 | K15 | 4191 BELLWOOD RD | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 7.6 | 101.736 | 2 | [11 empty] | 3052.08 |  | 280 |  |  |  | 3332.08 | Rehabilitate
| 362 | 5 | C | SSMHT0001383 | SS.MH.T0001383 | 32.3246 | -95.354 | K17 | 3363 BELLWOOD | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.24 | 109.7744 | [18 empty] | 0
| 363 | 5 | B | SSMHT0001418 | SS.MH.T0001418 | 32.3134 | -95.3543 | K18 | 3444 PINE TERRACE DR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.18 | 109.0208 | [18 empty] | 0
| 364 | 5 | C | SSMHT0001419 | SS.MH.T0001419 | 32.3133 | -95.355 | K18 | 3458 PINE TERRACE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 365 | 5 | B | SSMHT0001420 | SS.MH.T0001420 | 32.3147 | -95.357 | K18 | 4085 HOGAN DR | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.46 | 137.6576 | [18 empty] | 0
| 366 | 5 | X-CNL | SSMHT0001422 | SS.MH.T0001422 |  |  | K18 | 3843 LOUISE CT |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 367 | 5 | B | SSMHT0001423 | SS.MH.T0001423 | 32.3155 | -95.3555 | K18 | 4055 HOGAN DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 10.85 | 142.556 | [18 empty] | 0
| 368 | 5 | B | SSMHT0001460 | SS.MH.T0001460 | 32.3167 | -95.3515 | K18 | 2801 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.8 | 91.688 | [18 empty] | 0
| 369 | 5 | C | SSMHT0001461 | SS.MH.T0001461 | 32.3163 | -95.3515 | K18 | 2801 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.17 | 96.3352 | [18 empty] | 0
| 370 | 5 | C | SSMHT0001462 | SS.MH.T0001462 | 32.3163 | -95.3511 | K18 | 2801 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.47 | 100.1032 | [18 empty] | 0
| 371 | 5 | C | SSMHT0001463 | SS.MH.T0001463 | 32.3163 | -95.3506 | K18 | 3903 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 60 Round | Concrete | 6 | 81.64 | [18 empty] | 0
| 372 | 5 | D | SSMHT0001464 | SS.MH.T0001464 | 32.316 | -95.3502 | K18 | BLDG 40 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.36 | 111.2816 | 2 | [11 empty] | 3338.448 | [5 empty] | 3338.448 | Rehabilitate
| 373 | 5 | B | SSMHT0001465 | SS.MH.T0001465 | 32.316 | -95.3496 | K18 | BLDG 41 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5 | 69.08 | [18 empty] | 0
| 374 | 5 | B | SSMHT0002047 | SS.MH.T0002047 | 32.3193 | -95.337 | L17 | 3122 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.1 | 133.136 | [18 empty] | 0
| 375 | 5 | B | SSMHT0002048 | SS.MH.T0002048 | 32.3183 | -95.337 | L17 | 2800 BLK JERSEY ST | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.92 | 143.4352 | [18 empty] | 0
| 376 | 5 | B | SSMHT0002049 | SS.MH.T0002049 | 32.3179 | -95.337 | L18 | 3122 MOOREHEAD ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.46 | 112.5376 | [18 empty] | 0
| 377 | 5 | B | SSMHT0002050 | SS.MH.T0002050 | 32.3183 | -95.3356 | L17 | 3022 MOOREHEAD ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.36 | 111.2816 | [18 empty] | 0
| 378 | 5 | B | SSMHT0002051 | SS.MH.T0002051 | 32.3193 | -95.3356 | L17 | 3021 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.54 | 100.9824 | [18 empty] | 0
| 379 | 5 | X-CNO | SSMHT0002052 | SS.MH.T0002052 | 32.3193 | -95.336 | L17 | 3106 WALTON RD | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 380 | 5 | B | SSMHT0002056 | SS.MH.T0002056 | 32.3126 | -95.341 | K18 | 3200 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 11.8 | 154.488 | [18 empty] | 0
| 381 | 5 | D | SSMHT0002057 | SS.MH.T0002057 | 32.3441 | -95.3506 | K15 | 4430 STATE HWY 31 W | Vented | 1 | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 13.46 | 175.3376 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
| 382 | 5 | C | SSMHT0002058 | SS.MH.T0002058 | 32.3442 | -95.3496 | K15 | 4301 CHANDLER HWY | Vented | 1 | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Sealed Concrete | 13.92 | 181.1152 | [18 empty] | 0
| 383 | 5 | B | SSMHT0002059 | SS.MH.T0002059 | 32.3152 | -95.3398 | K18 | 3211 TOWNE WAY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.16 | 209.2496 | [18 empty] | 0
| 384 | 5 | B | SSMHT0002060 | SS.MH.T0002060 | 32.3151 | -95.3403 | K18 | 3120 S. SW LP 323 | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 17 | 219.8 | [18 empty] | 0
| 385 | 5 | B | SSMHT0002068 | SS.MH.T0002068 | 32.3348 | -95.3407 | K16 | NONE S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 16 | Std 48 Round | Concrete | 11.86 | 155.2416 | [18 empty] | 0
| 386 | 5 | C | SSMHT0002069 | SS.MH.T0002069 | 32.3339 | -95.3403 | K16 | 3509 ROBERTSON RD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 8.05 | 107.388 | [18 empty] | 0
| 387 | 5 | B | SSMHT0002070 | SS.MH.T0002070 | 32.3349 | -95.3367 | L16 | 1216 S BENNETT AVE | Solid |  | Yes | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.69 | 77.7464 | [18 empty] | 0
| 388 | 5 | C | SSMHT0002071 | SS.MH.T0002071 | 32.3335 | -95.3367 | L16 | 3305 ROBERTSON RD | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 5.3 | 72.848 | [18 empty] | 0
| 389 | 5 | B | SSMHT0002072 | SS.MH.T0002072 | 32.336 | -95.3436 | K16 | 1029 WHITESIDE RD | Solid |  | Yes | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 7.7 | 102.992 | [18 empty] | 0
| 390 | 5 | X-CNL | SSMHT0002073 | SS.MH.T0002073 | 32.3353 | -95.3435 | K16 | 1029 WHITESIDE RD |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 391 | 5 | D | SSMHT0002074 | SS.MH.T0002074 | 32.3415 | -95.3366 | L15 | 703 DUCKENFIELD AVE | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 31 | Std 48 Round | Brick | 10.04 | 132.3824 | 2 | [11 empty] | 3971.472 | [5 empty] | 3971.472 | Rehabilitate
| 392 | 5 | D | SSMHT0002075 | SS.MH.T0002075 | 32.3413 | -95.3367 | L15 | 703 DUCKENFIELD AVE | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 30 | Std 48 Round | Brick | 10.04 | 132.3824 | 2 | [11 empty] | 3971.472 | [5 empty] | 3971.472 | Rehabilitate
| 393 | 5 | C | SSMHT0002076 | SS.MH.T0002076 | 32.3421 | -95.3367 | L15 | 3300 BLK BELLWOOD RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 7.08 | 95.2048 | [18 empty] | 0
| 394 | 5 | D | SSMHT0002077 | SS.MH.T0002077 | 32.3421 | -95.3384 | L15 | 3400 BLK BELLWOOD RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.86 | 142.6816 | 2 | [11 empty] | 4280.448 | [5 empty] | 4280.448 | Rehabilitate
| 395 | 5 | D | SSMHT0002078 | SS.MH.T0002078 | 32.3411 | -95.3372 | L15 | 726 BOYD AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Brick | 8.63 | 114.6728 | 2 | [11 empty] | 3440.184 | [5 empty] | 3440.184 | Rehabilitate
| 396 | 5 | C | SSMHT0002079 | SS.MH.T0002079 | 32.3405 | -95.3383 | L15 | 808 S. BENNETTE AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 11.38 | 149.2128 | [18 empty] | 0
| 397 | 5 | X-CNL | SSMHT0002080 | SS.MH.T0002080 |  |  | L15 | 800 BLK S. BENNETT AVE |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 398 | 5 | X-CNL | SSMHT0002089 | SS.MH.T0002089 |  |  | K17 | 2603 S. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 399 | 5 | D | SSMHT0002090 | SS.MH.T0002090 | 32.3378 | -95.3294 | L16 | 1001 CROSBY ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 28 | Brick | 3.22 | 46.7232 | 2 | [10 empty] | 1401.696 | [6 empty] | 1401.696 | Rehabilitate
| 400 | 5 | B | SSMHT0002091 | SS.MH.T0002091 | 32.3378 | -95.3279 | L16 | 1002 S. BUCKLEY AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.03 | 107.1368 | [18 empty] | 0
| 401 | 5 | C | SSMHT0002093 | SS.MH.T0002093 | 32.3395 | -95.3295 | L16 | 837 CROSBY ST | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | 32 | Brick | 2.4 | 36.424 | [18 empty] | 0
| 402 | 5 | C | SSMHT0002094 | SS.MH.T0002094 | 32.3396 | -95.3279 | L16 | 840 S. BUCKLEY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.72 | 103.2432 | [18 empty] | 0
| 403 | 5 | C | SSMHT0002095 | SS.MH.T0002095 | 32.3408 | -95.328 | L15 | 2414 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Brick | 6.4 | 86.664 | [18 empty] | 0
| 404 | 5 | D | SSMHT0002096 | SS.MH.T0002096 | 32.3399 | -95.328 | L15 | 841 BUCKLEY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.8 | 104.248 | 2 | [11 empty] | 3127.44 | [5 empty] | 3127.44 | Rehabilitate
| 405 | 5 | C | SSMHT0002097 | SS.MH.T0002097 | 32.3403 | -95.328 | L15 | 822 BUCKLEY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.58 | 101.4848 | [18 empty] | 0
| 406 | 5 | C | SSMHT0002098 | SS.MH.T0002098 | 32.3407 | -95.3273 | L15 | 2400 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.48 | 75.1088 | [18 empty] | 0
| 407 | 5 | D | SSMHT0002099 | SS.MH.T0002099 | 32.3413 | -95.33 | L15 | 2600 BLK BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.71 | 90.5576 | 2 | [11 empty] | 2716.728 | [5 empty] | 2716.728 | Rehabilitate
| 408 | 5 | B | SSMHT0002101 | SS.MH.T0002101 | 32.3365 | -95.3337 | L16 | 2850 W. SHAW ST | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 6.58 | 88.9248 | [18 empty] | 0
| 409 | 5 | B | SSMHT0002102 | SS.MH.T0002102 | 32.3363 | -95.336 | L16 | 3300 W. SHAW ST | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 8.88 | 117.8128 | [18 empty] | 0
| 410 | 5 | B | SSMHT0002103 | SS.MH.T0002103 | 32.3365 | -95.3353 | L16 | 3300 W. SHAW ST | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 8.62 | 114.5472 | [18 empty] | 0
| 411 | 5 | C | SSMHT0002104 | SS.MH.T0002104 | 32.3375 | -95.3351 | L16 | 3122 W. JACKSON ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.75 | 103.62 | [18 empty] | 0
| 412 | 5 | D | SSMHT0002105 | SS.MH.T0002105 | 32.3375 | -95.3337 | L16 | 1108 BRITTON AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.52 | 125.8512 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
| 413 | 5 | C | SSMHT0002106 | SS.MH.T0002106 | 32.3375 | -95.3361 | K18 | 3209 W. JACKSON ST | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 7.66 | 102.4896 | [18 empty] | 0
| 414 | 5 | B | SSMHT0002107 | SS.MH.T0002107 | 32.338 | -95.3361 | L16 | 944 DUCKENFIELD AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.7 | 77.872 | [18 empty] | 0
| 415 | 5 | C | SSMHT0002108 | SS.MH.T0002108 | 32.3383 | -95.3337 | L16 | 1018 BRITTON AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.1 | 145.696 | [18 empty] | 0
| 416 | 5 | B | SSMHT0002109 | SS.MH.T0002109 | 32.3401 | -95.3361 | L15 | 806 DUCKENFIELD AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.04 | 107.2624 | [18 empty] | 0
| 417 | 5 | C | SSMHT0002110 | SS.MH.T0002110 | 32.3401 | -95.3349 | L15 | 3114 W. ROSE ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.76 | 103.7456 | [18 empty] | 0
| 418 | 5 | B | SSMHT0002111 | SS.MH.T0002111 | 32.3401 | -95.3337 | L15 | 901 BRITTON AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.75 | 141.3 | [18 empty] | 0
| 419 | 5 | C | SSMHT0002112 | SS.MH.T0002112 | 32.3411 | -95.3361 | L15 | 727 DUCKENFIELD AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.6 | 114.296 | [18 empty] | 0
| 420 | 5 | D | SSMHT0002113 | SS.MH.T0002113 | 32.3415 | -95.3361 | L15 | 703 DUCKENFIELD AVE | Solid |  | No | Road Shoulder | Unpaved | At Grade | 3 | Std 48 Round | Brick | 10.96 | 143.9376 | 2 | [6 empty] | 650 |  |  |  |  | 4318.128 | [5 empty] | 4968.128 | Rehabilitate
| 421 | 5 | D | SSMHT0002114 | SS.MH.T0002114 | 32.3421 | -95.3361 | L15 | 3210 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.1 | 95.456 | 2 | [11 empty] | 2863.68 | [5 empty] | 2863.68 | Rehabilitate
| 422 | 5 | D | SSMHT0002115 | SS.MH.T0002115 | 32.3422 | -95.3338 | L15 | 700 BRITTON AVE | Solid |  | No | Gutter | Paved - Concrete | At Grade |  | Std 48 Round | Brick | 4.2 | 59.032 | 2 | [10 empty] | 1770.96 | [6 empty] | 1770.96 | Rehabilitate
| 423 | 5 | C | SSMHT0002116 | SS.MH.T0002116 | 32.3421 | -95.3332 | L15 | 2924 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.96 | 118.8176 | [18 empty] | 0
| 424 | 5 | C | SSMHT0002117 | SS.MH.T0002117 | 32.3418 | -95.3319 | L15 | 2808 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.93 | 168.6808 | [18 empty] | 0
| 425 | 5 | C | SSMHT0002118 | SS.MH.T0002118 | 32.3418 | -95.3319 | L15 | 2808 BELLWOOD RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.56 | 76.1136 | [18 empty] | 0
| 426 | 5 | D | SSMHT0002119 | SS.MH.T0002119 | 32.3403 | -95.3319 | L15 | 812 S. TURNER AVE | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 7.96 | 106.2576 | 2 | [11 empty] | 3187.728 |  | 280 |  |  |  | 3467.728 | Rehabilitate
| 427 | 5 | X-Buried | SSMHT0002120 | SS.MH.T0002120 | 32.3375 | -95.3318 | L16 | 1001 S. TURNER ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 428 | 5 | B | SSMHT0002121 | SS.MH.T0002121 | 32.3375 | -95.3319 | L16 | 1001 S. TURNER ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.52 | 100.7312 | [18 empty] | 0
| 429 | 5 | B | SSMHT0002122 | SS.MH.T0002122 | 32.3363 | -95.3367 | L16 | 3300 W. SHAW ST | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.56 | 126.3536 | [18 empty] | 0
| 430 | 5 | C | SSMHT0002123 | SS.MH.T0002123 | 32.3363 | -95.3373 | L16 | 3320 W. SHAW ST | Solid |  | Yes | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 9.94 | 131.1264 | [18 empty] | 0
| 431 | 5 | B | SSMHT0002124 | SS.MH.T0002124 | 32.3363 | -95.3383 | L16 | 3400 BLK W. SHAW ST | Solid |  | Yes | Road Shoulder | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.64 | 127.3584 | [18 empty] | 0
| 432 | 5 | D | SSMHT0002126 | SS.MH.T0002126 | 32.3391 | -95.3403 | K16 | 915 S. SW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 12.72 | 166.0432 | 2 | [6 empty] | 650 |  |  |  |  | 4981.296 |  | 280 |  |  |  | 5911.296 | Rehabilitate
| 433 | 5 | X-CNL | SSMHT0002127 | SS.MH.T0002127 |  |  | N3 | 909 S SW LOOP 323 |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 434 | 5 | C | SSMHT0002128 | SS.MH.T0002128 | 32.3405 | -95.3405 | K15 | 909 S. SW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 11 | Std 48 Round | Brick | 6.72 | 90.6832 | [18 empty] | 0
| 435 | 5 | C | SSMHT0002129 | SS.MH.T0002129 | 32.3433 | -95.3402 | K15 | 530 S. SW LP 323 | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.56 | 126.3536 | [18 empty] | 0
| 436 | 5 | C | SSMHT0002130 | SS.MH.T0002130 | 32.3458 | -95.3404 | K15 | 3555 CHANDLER HWY | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 9.6 | 126.856 | [18 empty] | 0
| 437 | 5 | C | SSMHT0002131 | SS.MH.T0002131 | 32.3455 | -95.3404 | K15 | 510 S. SW LP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 12 | 157 | [18 empty] | 0
| 438 | 5 | X-CNL | SSMHT0002132 | SS.MH.T0002132 |  |  | K15 | 510 S. SW LP 323 |  |  |  | Parking Lot | Paved - Asphalt | [24 empty] | 0
| 439 | 5 | B | SSMHT0002133 | SS.MH.T0002133 | 32.3435 | -95.3404 | K15 | 530 S. SW LP 323 | Solid |  | Yes | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.38 | 136.6528 | [18 empty] | 0
| 440 | 5 | D | SSMHT0002134 | SS.MH.T0002134 | 32.3454 | -95.3422 | K15 | 3801 CHANDLER HWY | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 6.1 | 82.896 | 2 | [11 empty] | 2486.88 | [5 empty] | 2486.88 | Rehabilitate
| 441 | 5 | D | SSMHT0002135 | SS.MH.T0002135 | 32.3451 | -95.3436 | K15 | 3921 CHANDLER HWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 13.61 | 177.2216 | 2 | [7 empty] | 1950 |  |  |  | 5316.648 | [5 empty] | 7266.648 | Rehabilitate
| 442 | 5 | D | SSMHT0002136 | SS.MH.T0002136 | 32.3427 | -95.3435 | K15 | 637 WHITESIDE RD | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 7.23 | 97.0888 | 2 | [11 empty] | 2912.664 |  | 280 |  |  |  | 3192.664 | Rehabilitate
| 443 | 5 | C | SSMHT0002137 | SS.MH.T0002137 | 32.3432 | -95.3435 | K15 | 603 WHITESIDE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.82 | 117.0592 | [18 empty] | 0
| 444 | 5 | B | SSMHT0002138 | SS.MH.T0002138 | 32.3445 | -95.3461 | K15 | 4115 CHANDLER HWY | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Brick | 6.48 | 87.6688 | [18 empty] | 0
| 445 | 5 | C | SSMHT0002139 | SS.MH.T0002139 | 32.343 | -95.3404 | K15 | 530 S. SW LP 323 | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.84 | 154.9904 | [18 empty] | 0
| 446 | 5 | C | SSMHT0002140 | SS.MH.T0002140 | 32.343 | -95.3402 | K15 | 530 S. SW LP 323 | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.07 | 145.3192 | [18 empty] | 0
| 447 | 5 | X-CNL | SSMHT0002141 | SS.MH.T0002141 |  |  | K15 | 530 S. SW LP 323 |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
Upated | 448 | 5 | D | SSMHT0002143 | SS.MH.T0002143 | 32.3406 | -95.3301 | L15 | 805 CLARK ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.63 | 114.6728 | 2 | [11 empty] | 3440.184 | [5 empty] | 3440.184 | Rehabilitate
Upated | 449 | 5 | X-Buried | SSMHT0002145 | SS.MH.T0002145 | 32.3395 | -95.3305 | L16 | 835 CLARK ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 450 | 5 | X-Buried | SSMHT0002146 | SS.MH.T0002146 | 32.3382 | -95.3272 | L16 | 616 TUBBS ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 451 | 5 | X-CNL | SSMHT0002148 | SS.MH.T0002148 |  |  | K18 | 3201 ROBERTSON RD |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 452 | 5 | B | SSMHT0002149 | SS.MH.T0002149 | 32.3331 | -95.3349 | L16 | 3201 ROBERTSON RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Sealed Concrete | 10.3 | 135.648 | [18 empty] | 0
| 453 | 5 | C | SSMHT0002151 | SS.MH.T0002151 | 32.3331 | -95.3358 | L16 | 3305 ROBERTSON RD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 4 | Std 48 Round | Concrete | 7.58 | 101.4848 | [18 empty] | 0
| 454 | 5 | B | SSMHT0002152 | SS.MH.T0002152 | 32.3331 | -95.3366 | L16 | 3305 ROBERTSON RD | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.82 | 104.4992 | [18 empty] | 0
| 455 | 5 | C | SSMHT0002153 | SS.MH.T0002153 | 32.3451 | -95.3496 | K15 | NONE WILDROSE DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 12.02 | 157.2512 | [18 empty] | 0
| 456 | 5 | D | SSMHT0002155 | SS.MH.T0002155 | 32.3465 | -95.3481 | K15 | 4229 OLD CHANDLER RD | Solid |  | No | Street | Paved - Asphalt | Below Grade | 2 | Std 48 Round | Concrete | 9.91 | 130.7496 | [8 empty] | 1950 | [5 empty] | 280 |  |  |  | 2230 | Repair
| 457 | 5 | B | SSMHT0002156 | SS.MH.T0002156 | 32.314 | -95.3324 | L18 | 2818 SARA ST | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 6.8 | 91.688 | [18 empty] | 0
| 458 | 5 | D | SSMHT0002157 | SS.MH.T0002157 | 32.3159 | -95.3329 | L18 | 3111 SEATON ST | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.34 | 85.9104 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
| 459 | 5 | C | SSMHT0002158 | SS.MH.T0002158 | 32.3174 | -95.3356 | L18 | 3023 OLIVER ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 22.4 | 287.624 | [18 empty] | 0
| 460 | 5 | C | SSMHT0002159 | SS.MH.T0002159 | 32.3174 | -95.3346 | L18 | 3006 MOOREHEAD ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 14.5 | 188.4 | [18 empty] | 0
| 461 | 5 | X-CNL | SSMHT0002160 | SS.MH.T0002160 |  |  | L18 | 2902 MOOREHEAD ST |  |  |  | Street | Unpaved | [24 empty] | 0
| 462 | 5 | X-CNL | SSMHT0002161 | SS.MH.T0002161 |  |  | L18 | 3111 SEATON ST |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 463 | 5 | B | SSMHT0002162 | SS.MH.T0002162 | 32.3166 | -95.3323 | L18 | 3031 BUDDIE ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 36 | Std 48 Round | Fiberglass | 10.33 | 136.0248 | [18 empty] | 0
| 464 | 5 | B | SSMHT0002164 | SS.MH.T0002164 | 32.3331 | -95.3313 | L16 | 2821 ROBERTSON RD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 8.54 | 113.5424 | [18 empty] | 0
| 465 | 5 | B | SSMHT0002165 | SS.MH.T0002165 | 32.3331 | -95.33 | L16 | 2811 ROBERTSON RD | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.7 | 115.552 | [18 empty] | 0
| 466 | 5 | B | SSMHT0002166 | SS.MH.T0002166 | 32.3331 | -95.3287 | L16 | 2511 ROBERTSON RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 10.06 | 132.6336 | [18 empty] | 0
| 467 | 5 | C | SSMHT0002167 | SS.MH.T0002167 | 32.3332 | -95.3278 | L16 | 2503 ROBERTSON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.44 | 137.4064 | [18 empty] | 0
| 468 | 5 | X-CNO | SSMHT0002168 | SS.MH.T0002168 | 32.3173 | -95.3369 | L18 | 3122 MOOREHEAD ST | Solid |  |  | Trees/Woods | Unpaved | Below Grade | 1 | [22 empty] | 0
| 469 | 5 | C | SSMHT0002169 | SS.MH.T0002169 | 32.3348 | -95.3278 | L16 | 2412 CARTWRIGHT ST | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 4.9 | 67.824 | [18 empty] | 0
| 470 | 5 | X-CNO | SSMHT0002170 | SS.MH.T0002170 | 32.3165 | -95.3297 | L18 | 3004 KING ST | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.28 | 122.8368 | [18 empty] | 0
| 471 | 5 | X-CNO | SSMHT0002171 | SS.MH.T0002171 | 32.3172 | -95.331 | L18 | 2614 MADISON ST | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 472 | 5 | B | SSMHT0002172 | SS.MH.T0002172 | 32.3172 | -95.3287 | L18 | 2423 MADISON ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.88 | 80.1328 | [18 empty] | 0
| 473 | 5 | C | SSMHT0002192 | SS.MH.T0002192 | 32.3072 | -95.3377 | L19 | 3908 S. SW LP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 11.51 | 150.8456 | [18 empty] | 0
| 474 | 5 | X-CNL | SSMHT0002193 | SS.MH.T0002193 |  |  | L19 | 3908 S. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 475 | 5 | D | SSMHT0002227 | SS.MH.T0002227 | 32.3088 | -95.3383 | L18 | 3021 MC CORMICK LN | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 6.8 | 91.688 | 2 | [6 empty] | 650 |  |  |  |  | 2750.64 | [5 empty] | 3400.64 | Rehabilitate
| 476 | 5 | D | SSMHT0002228 | SS.MH.T0002228 | 32.3093 | -95.3379 | L18 | 3432 S. SE LP 323 | Solid |  | No | Parking Lot | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 8 | 106.76 | 2 | [6 empty] | 650 |  |  |  |  | 3202.8 | [5 empty] | 3852.8 | Rehabilitate
| 477 | 5 | B | SSMHT0002229 | SS.MH.T0002229 | 32.3098 | -95.3376 | L18 | 3422 S. SE LP 323 | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.74 | 153.7344 | [18 empty] | 0
| 478 | 5 | B | SSMHT0002230 | SS.MH.T0002230 | 32.3107 | -95.3373 | L18 | 3418 S. SW LP 323 | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 8.32 | 110.7792 | [18 empty] | 0
| 479 | 5 | D | SSMHT0002235 | SS.MH.T0002235 | 32.3193 | -95.3267 | L17 | 2224 WALTON RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | 30 | Brick | 5.17 | 71.2152 | 2 | [10 empty] | 2136.456 | [6 empty] | 2136.456 | Rehabilitate
| 480 | 5 | B | SSMHT0002248 | SS.MH.T0002248 | 32.3169 | -95.3426 | K18 | 2929 S SOUTHWEST LOOP 323 | Solid |  | Yes | Drainage Ditch | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 8.22 | 109.5232 | [18 empty] | 0
| 481 | 5 | B | SSMHT0002250 | SS.MH.T0002250 | 32.34 | -95.3373 | L15 | 903 BOYD AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.2 | 121.832 | [18 empty] | 0
| 482 | 5 | C | SSMHT0002251 | SS.MH.T0002251 | 32.3404 | -95.3436 | K15 | 804 WHITESIDE RD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 6 | Std 48 Round | Concrete | 7.92 | 105.7552 | [18 empty] | 0
| 483 | 5 | B | SSMHT0002252 | SS.MH.T0002252 | 32.3367 | -95.3278 | L16 | 1020 S. BUCKLEY AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.08 | 145.4448 | [18 empty] | 0
| 484 | 5 | D | SSMHT0002253 | SS.MH.T0002253 | 32.3367 | -95.3267 | L16 | 2325 W.SHAW ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.86 | 92.4416 | 2 |  |  |  | 500 | [7 empty] | 2773.248 | [5 empty] | 3273.248 | Rehabilitate
| 485 | 5 | B | SSMHT0002254 | SS.MH.T0002254 | 32.3134 | -95.3383 | L18 | 3208 TOWNE PARK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 19.5 | 251.2 | [18 empty] | 0
| 486 | 5 | B | SSMHT0002255 | SS.MH.T0002255 | 32.3133 | -95.3382 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 19.6 | 252.456 | [18 empty] | 0
| 487 | 5 | C | SSMHT0002256 | SS.MH.T0002256 | 32.3332 | -95.3403 | K16 | 1410 S. SW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Brick | 8.33 | 110.9048 | [18 empty] | 0
| 488 | 5 | X-CNO | SSMHT0002260 | SS.MH.T0002260 | 32.3129 | -95.3409 | K18 | 3201 S. SW LP 323 | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 489 | 5 | B | SSMHT0002261 | SS.MH.T0002261 | 32.3083 | -95.3387 | L18 | 3029 MC CORMICK LN | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 27 | Std 48 Round | Concrete | 11.78 | 154.2368 | [18 empty] | 0
| 490 | 5 | C | SSMHT0002267 | SS.MH.T0002267 | 32.3208 | -95.3332 | L17 | 2723 RACHEL AVE | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 5.02 | 69.3312 | [18 empty] | 0
| 491 | 5 | B | SSMHT0002278 | SS.MH.T0002278 | 32.336 | -95.3278 | L16 | 1204 S. BUCKLEY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.3 | 72.848 | [18 empty] | 0
| 492 | 5 | B | SSMHT0002279 | SS.MH.T0002279 | 32.3409 | -95.3383 | L15 | 803 S. BENNETTE AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [18 empty] | 0
| 493 | 5 | B | SSMHT0002283 | SS.MH.T0002283 | 32.3187 | -95.3291 | L17 | 2806 RHINEHART ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.7 | 128.112 | [18 empty] | 0
| 494 | 5 | C | SSMHT0002284 | SS.MH.T0002284 | 32.3172 | -95.3297 | L18 | 2509 MADISON ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.42 | 86.9152 | [18 empty] | 0
| 495 | 5 | B | SSMHT0002285 | SS.MH.T0002285 | 32.3318 | -95.3367 | L16 | 1532 BENNETTE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.12 | 120.8272 | [18 empty] | 0
| 496 | 5 | B | SSMHT0002286 | SS.MH.T0002286 | 32.3307 | -95.3367 | L16 | 1553BENNETT AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.76 | 128.8656 | [18 empty] | 0
| 497 | 5 | C | SSMHT0002288 | SS.MH.T0002288 | 32.3389 | -95.3272 | L16 | 907 TUBBS ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.14 | 70.8384 | [18 empty] | 0
| 498 | 5 | B | SSMHT0002289 | SS.MH.T0002289 | 32.3407 | -95.3372 | L15 | 809 BOYD AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 6.46 | 87.4176 | [18 empty] | 0
| 499 | 5 | B | SSMHT0002291 | SS.MH.T0002291 | 32.3169 | -95.3419 | K18 | 2850 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 13 | 169.56 | [18 empty] | 0
| 500 | 5 | B | SSMHT0002293 | SS.MH.T0002293 | 32.3129 | -95.3372 | L18 | 3110 (5) TOWNE PARK DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.42 | 86.9152 | [18 empty] | 0
| 501 | 5 | D | SSMHT0002294 | SS.MH.T0002294 | 32.312 | -95.3371 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 8.5 | 113.04 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
| 502 | 5 | D | SSMHT0002295 | SS.MH.T0002295 | 32.3117 | -95.3362 | L18 | 3110 (22) TOWNE PARK DR | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 11.42 | 149.7152 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 503 | 5 | D | SSMHT0002296 | SS.MH.T0002296 | 32.3114 | -95.3365 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 6.52 | 88.1712 | [7 empty] | 650 | [7 empty] | 900 |  |  | 1550 | Repair
| 504 | 5 | B | SSMHT0002310 | SS.MH.T0002310 | 32.313 | -95.3401 | K18 | 3200 S. SW LP 323 | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.57 | 139.0392 | [18 empty] | 0
| 505 | 5 | B | SSMHT0002311 | SS.MH.T0002311 | 32.3163 | -95.3316 | L18 | 3013 BUDDIE ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 21 | Std 48 Round | Fiberglass | 7.15 | 96.084 | [18 empty] | 0
| 506 | 5 | B | SSMHT0002312 | SS.MH.T0002312 | 32.3177 | -95.3419 | K18 | 2850 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 14.72 | 191.1632 | [18 empty] | 0
| 507 | 5 | X-CNL | SSMHT0002314 | SS.MH.T0002314 |  |  | K16 | 1410 S. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 508 | 5 | D | SSMHT0002315 | SS.MH.T0002315 | 32.3414 | -95.3372 | L15 | 714 BOYD AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 10.68 | 140.4208 | 2 | [11 empty] | 4212.624 | [5 empty] | 4212.624 | Rehabilitate
| 509 | 5 | X-CNO | SSMHT0002316 | SS.MH.T0002316 | 32.3421 | -95.3373 | L15 | 3300 BLK BELLWOOD RD | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 510 | 5 | B | SSMHT0002318 | SS.MH.T0002318 | 32.3218 | -95.3318 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 3.72 | 53.0032 | [18 empty] | 0
| 511 | 5 | B | SSMHT0002319 | SS.MH.T0002319 | 32.3228 | -95.3312 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 46 | Std 48 Round | Concrete | 9.9 | 130.624 | [18 empty] | 0
| 512 | 5 | D | SSMHT0002320 | SS.MH.T0002320 | 32.3225 | -95.3314 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 26 | Std 48 Round | Concrete | 11 | 144.44 | 2 |  |  |  | 500 |  |  | 650 |  |  |  |  | 4333.2 | [5 empty] | 5483.2 | Rehabilitate
| 513 | 5 | D | SSMHT0002321 | SS.MH.T0002321 | 32.3231 | -95.3331 | L17 | NONE TOL AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 8.89 | 117.9384 | 2 | [11 empty] | 3538.152 | [5 empty] | 3538.152 | Rehabilitate
| 514 | 5 | D | SSMHT0002322 | SS.MH.T0002322 | 32.3237 | -95.3312 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 35 | Std 48 Round | Concrete | 11.8 | 154.488 | 2 | [11 empty] | 4634.64 | [5 empty] | 4634.64 | Rehabilitate
| 515 | 5 | D | SSMHT0002323 | SS.MH.T0002323 | 32.3242 | -95.3324 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 7.86 | 105.0016 | [14 empty] | 280 |  |  |  | 280 | Repair
| 516 | 5 | X-Access | SSMHT0002324 | SS.MH.T0002324 |  |  | L17 | 3262 EARL CAMPBELL PKWY |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 517 | 5 | C | SSMHT0002325 | SS.MH.T0002325 | 32.3244 | -95.3341 | L17 | NONE TOL AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 33 | Std 48 Round | Concrete | 11.79 | 154.3624 | [18 empty] | 0
| 518 | 5 | B | SSMHT0002326 | SS.MH.T0002326 | 32.3149 | -95.3305 | L18 | 2808 LUTHER ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.04 | 69.5824 | [18 empty] | 0
| 519 | 5 | B | SSMHT0002327 | SS.MH.T0002327 | 32.3159 | -95.3302 | L18 | 2518 FRANCHEL ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.5 | 87.92 | [18 empty] | 0
| 520 | 5 | C | SSMHT0002328 | SS.MH.T0002328 | 32.3172 | -95.329 | L18 | 2600 BLK MADISON ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.54 | 75.8624 | [18 empty] | 0
| 521 | 5 | X-CNL | SSMHT0002330 | SS.MH.T0002330 |  |  | L19 | 3915 W. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 522 | 5 | X-CNL | SSMHT0002331 | SS.MH.T0002331 |  |  | L19 | 3915 S. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 523 | 5 | B | SSMHT0002333 | SS.MH.T0002333 | 32.3193 | -95.3253 | L17 | 2118 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.6 | 164.536 | [18 empty] | 0
| 524 | 5 | C | SSMHT0002334 | SS.MH.T0002334 | 32.3193 | -95.3256 | L17 | B2204 WALTON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11 | 144.44 | [18 empty] | 0
| 525 | 5 | B | SSMHT0002340 | SS.MH.T0002340 | 32.3482 | -95.3459 | K15 | 4100 BLK SUEL DR | Vented | 2 | Yes | Sidewalk | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.25 | 84.78 | [18 empty] | 0
| 526 | 5 | B | SSMHT0002341 | SS.MH.T0002341 | 32.348 | -95.348 | K15 | 4314 SUEL DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.95 | 93.572 | [18 empty] | 0
| 527 | 5 | B | SSMHT0002342 | SS.MH.T0002342 | 32.3151 | -95.3329 | L18 | 3113 SEATON ST | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 4.26 | 59.7856 | [18 empty] | 0
| 528 | 5 | D | SSMHT0002706 | SS.MH.T0002706 | 32.3187 | -95.3419 | K18 | 2772 S. SE LP 323 | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 9.37 | 123.9672 | 2 | [11 empty] | 3719.016 |  | 280 |  |  |  | 3999.016 | Rehabilitate
| 529 | 5 | B | SSMHT0002707 | SS.MH.T0002707 | 32.32 | -95.3361 | L17 | 2724 FLINT ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.1 | 82.896 | [18 empty] | 0
| 530 | 5 | B | SSMHT0002708 | SS.MH.T0002708 | 32.3206 | -95.3361 | L17 | 2712 FLINT ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 720 | 9049.48 | [18 empty] | 0
| 531 | 5 | B | SSMHT0002713 | SS.MH.T0002713 | 32.3123 | -95.3376 | L18 | 3110 (36) TOWNE PARK DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.68 | 190.6608 | [18 empty] | 0
| 532 | 5 | B | SSMHT0002714 | SS.MH.T0002714 | 32.3128 | -95.3381 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 45 | Std 48 Round | Concrete | 19.7 | 253.712 | [18 empty] | 0
| 533 | 5 | X-Buried | SSMHT0002715 | SS.MH.T0002715 | 32.342 | -95.3514 | K15 | 4420 ST HWY 31 W. |  |  |  | Yard | Unpaved | Below Grade | 10 | [22 empty] | 0
| 534 | 5 | C | SSMHT0002716 | SS.MH.T0002716 | 32.3431 | -95.3513 | K15 | 4430 STATE HWY 31 W | Vented | 2 | No | Yard | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 10.74 | 141.1744 | [18 empty] | 0
| 535 | 5 | C | SSMHT0002717 | SS.MH.T0002717 | 32.3443 | -95.3489 | K15 | 4301 CHANDLER HWY | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 11.31 | 148.3336 | [18 empty] | 0
| 536 | 5 | X-CNL | SSMHT0002722 | SS.MH.T0002722 |  |  | K15 | 4136 CHANDLER HWY |  |  |  | Drainage Ditch | Unpaved | [24 empty] | 0
| 537 | 5 | B | SSMHT0002723 | SS.MH.T0002723 | 32.3151 | -95.3396 | L18 | 3200 BLK TOWNE WAY DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.34 | 211.5104 | [18 empty] | 0
| 538 | 5 | B | SSMHT0002724 | SS.MH.T0002724 | 32.3152 | -95.3394 | M18 | 3211 TOWNE WAY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.62 | 89.4272 | [18 empty] | 0
| 539 | 5 | D | SSMHT0003335 | SS.MH.T0003335 | 32.3461 | -95.3389 | K15 | 3501 CHANDLER HWY | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 5.66 | 77.3696 | 2 | [6 empty] | 650 |  |  |  | 2321.088 |  |  | 280 |  |  |  | 3251.088 | Rehabilitate
| 540 | 5 | C | SSMHT0005668 | SS.MH.T0005668 | 32.3188 | -95.3415 | K17 | 3462 WALTON RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 8.85 | 117.436 | [18 empty] | 0
| 541 | 5 | C | SSMHT0005669 | SS.MH.T0005669 | 32.3185 | -95.3403 | K17 | 3462 WALTON RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 21 | Std 48 Round | Concrete | 10.8 | 141.928 | [18 empty] | 0
| 542 | 5 | C | SSMHT0005670 | SS.MH.T0005670 | 32.318 | -95.3394 | L18 | 3220 WALTON RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 16.46 | 213.0176 | [18 empty] | 0
| 543 | 5 | B | SSMHT0005671 | SS.MH.T0005671 | 32.3177 | -95.3386 | L18 | 3220(400) WALTON RD | Solid |  | No | Parking Lot | Unpaved | At Grade |  | Std 48 Round | Concrete | 19.1 | 246.176 | [18 empty] | 0
| 544 | 5 | D | SSMHT0005672 | SS.MH.T0005672 | 32.3183 | -95.3419 | K18 | 2850 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 9.36 | 123.8416 | 2 | [11 empty] | 3715.248 | [5 empty] | 3715.248 | Rehabilitate
| 545 | 5 | B | SSMHT0005673 | SS.MH.T0005673 | 32.3201 | -95.3419 | K17 | 2626 S.SW LP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 11.92 | 155.9952 | [18 empty] | 0
| 546 | 5 | B | SSMHT0005898 | SS.MH.T0005898 | 32.3206 | -95.3347 | L17 | 2724 TOL AVE | Solid |  | No | Road Shoulder | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.23 | 71.9688 | [18 empty] | 0
| 547 | 5 | B | SSMHT0007104 | SS.MH.T0007104 | 32.3285 | -95.3365 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Road Shoulder | Paved - Concrete | Above Grade | 10 | Std 48 Round | Concrete | 13.88 | 180.6128 | [18 empty] | 0
| 548 | 5 | C | SSMHT0007105 | SS.MH.T0007105 | 32.3298 | -95.3365 | L16 | 1700 BLKBENNETT AVE | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 8" | Other | [20 empty] | 0
| 549 | 5 | B | SSMHT0007119 | SS.MH.T0007119 | 32.3143 | -95.3533 | K18 | NONE NATURE TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.02 | 81.8912 | [18 empty] | 0
| 550 | 5 | X-Access | SSMHT0007122 | SS.MH.T0007122 |  |  | K18 | 3809 PUTTING LN | Solid |  |  | Yard | Unpaved | [24 empty] | 0
| 551 | 5 | B | SSMHT0007123 | SS.MH.T0007123 | 32.3175 | -95.3533 | K18 | 3849 PUTTING LN | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.44 | 112.2864 | [18 empty] | 0
| 552 | 5 | B | SSMHT0007129 | SS.MH.T0007129 | 32.3198 | -95.362 | J17 | 2811 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.28 | 97.7168 | [18 empty] | 0
| 553 | 5 | B | SSMHT0007130 | SS.MH.T0007130 | 32.3196 | -95.3621 | J17 | 2818 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.94 | 106.0064 | [18 empty] | 0
| 554 | 5 | B | SSMHT0007131 | SS.MH.T0007131 | 32.3193 | -95.3622 | J17 | 2824 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.26 | 110.0256 | [18 empty] | 0
| 555 | 5 | C | SSMHT0007132 | SS.MH.T0007132 | 32.3192 | -95.3623 | J17 | 2824 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 556 | 5 | B | SSMHT0007133 | SS.MH.T0007133 | 32.319 | -95.3628 | J17 | 2848 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.98 | 106.5088 | [18 empty] | 0
| 557 | 5 | B | SSMHT0007134 | SS.MH.T0007134 | 32.3187 | -95.3631 | J17 | 2848 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.44 | 99.7264 | [18 empty] | 0
| 558 | 5 | B | SSMHT0007135 | SS.MH.T0007135 | 32.3185 | -95.3634 | J18 | 2848 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.3 | 123.088 | [18 empty] | 0
| 559 | 5 | C | SSMHT0007136 | SS.MH.T0007136 | 32.3185 | -95.3636 | J18 | 2848 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.6 | 101.736 | [18 empty] | 0
| 560 | 5 | C | SSMHT0007137 | SS.MH.T0007137 | 32.3187 | -95.3638 | J17 | 2872 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.01 | 94.3256 | [18 empty] | 0
| 561 | 5 | C | SSMHT0007138 | SS.MH.T0007138 | 32.3189 | -95.364 | J17 | 2878STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.48 | 100.2288 | [18 empty] | 0
| 562 | 5 | B | SSMHT0007139 | SS.MH.T0007139 | 32.3197 | -95.3635 | J17 | 2907 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.94 | 118.5664 | [18 empty] | 0
| 563 | 5 | B | SSMHT0007140 | SS.MH.T0007140 | 32.3199 | -95.3631 | J17 | 2913 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 564 | 5 | C | SSMHT0007141 | SS.MH.T0007141 | 32.3203 | -95.3628 | J17 | 2931 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.96 | 131.3776 | [18 empty] | 0
| 565 | 5 | C | SSMHT0007142 | SS.MH.T0007142 | 32.3204 | -95.3617 | J17 | 4500 BLK CASCADES BLVD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 14.66 | 190.4096 | [18 empty] | 0
| 566 | 5 | B | SSMHT0007143 | SS.MH.T0007143 | 32.3205 | -95.3618 | J17 | 4500 BLK CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 15.76 | 204.2256 | [18 empty] | 0
| 567 | 5 | B | SSMHT0007144 | SS.MH.T0007144 | 32.3208 | -95.3624 | J17 | 4537 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.43 | 149.8408 | [18 empty] | 0
| 568 | 5 | C | SSMHT0007145 | SS.MH.T0007145 | 32.3211 | -95.3632 | J17 | 4545 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.5 | 150.72 | [18 empty] | 0
| 569 | 5 | B | SSMHT0007146 | SS.MH.T0007146 | 32.3209 | -95.3648 | J17 | 2849 J. CUPIT CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 17.88 | 230.8528 | [18 empty] | 0
| 570 | 5 | B | SSMHT0007147 | SS.MH.T0007147 | 32.3211 | -95.3648 | J17 | 2861 J. CUPIT CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.88 | 155.4928 | [18 empty] | 0
| 571 | 5 | B | SSMHT0007156 | SS.MH.T0007156 | 32.321 | -95.3612 | J17 | 4454 TRIGGS TRACE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.02 | 132.1312 | [18 empty] | 0
| 572 | 5 | B | SSMHT0007157 | SS.MH.T0007157 | 32.3217 | -95.3614 | J17 | 4506 TRIGGS TRACE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.78 | 154.2368 | [18 empty] | 0
| 573 | 5 | C | SSMHT0007169 | SS.MH.T0007169 | 32.3211 | -95.3595 | J17 | 4463 COUPLES CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.02 | 157.2512 | [18 empty] | 0
| 574 | 5 | C | SSMHT0007170 | SS.MH.T0007170 | 32.3213 | -95.3598 | J17 | 4463 COUPLES CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 17.53 | 226.4568 | [18 empty] | 0
| 575 | 5 | C | SSMHT0007171 | SS.MH.T0007171 | 32.3213 | -95.3602 | J17 | 4463 COUPLES CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 19.4 | 249.944 | [18 empty] | 0
| 576 | 5 | C | SSMHT0007172 | SS.MH.T0007172 | 32.3214 | -95.3605 | J17 | 4463 COUPLES CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.68 | 152.9808 | [18 empty] | 0
| 577 | 5 | C | SSMHT0007173 | SS.MH.T0007173 | 32.3216 | -95.3606 | J17 | 4463 COUPLES CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.54 | 176.3424 | [18 empty] | 0
| 578 | 5 | B | SSMHT0007225 | SS.MH.T0007225 | 32.3173 | -95.3572 | K18 | 4210 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.7 | 178.352 | [18 empty] | 0
| 579 | 5 | B | SSMHT0007226 | SS.MH.T0007226 | 32.316 | -95.3582 | K18 | 3682 FORREST CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.74 | 141.1744 | [18 empty] | 0
| 580 | 5 | B | SSMHT0007227 | SS.MH.T0007227 | 32.3146 | -95.3581 | K18 | 3800 BLK HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.6 | 151.976 | [18 empty] | 0
| 581 | 5 | B | SSMHT0007233 | SS.MH.T0007233 | 32.3135 | -95.3581 | K18 | 3934 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.66 | 127.6096 | [18 empty] | 0
| 582 | 5 | B | SSMHT0007234 | SS.MH.T0007234 | 32.3131 | -95.358 | K18 | 3922 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.24 | 109.7744 | [18 empty] | 0
| 583 | 5 | B | SSMHT0007235 | SS.MH.T0007235 | 32.3127 | -95.3577 | K18 | 3854 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.1 | 133.136 | [18 empty] | 0
| 584 | 5 | B | SSMHT0007236 | SS.MH.T0007236 | 32.3125 | -95.3572 | K18 | 3842 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.7 | 153.232 | [18 empty] | 0
| 585 | 5 | B | SSMHT0007237 | SS.MH.T0007237 | 32.3125 | -95.3567 | K18 | 3830 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.7 | 140.672 | [18 empty] | 0
| 586 | 5 | B | SSMHT0007238 | SS.MH.T0007238 | 32.3125 | -95.3564 | K18 | 3824 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.38 | 98.9728 | [18 empty] | 0
| 587 | 5 | B | SSMHT0007239 | SS.MH.T0007239 | 32.3123 | -95.3562 | K18 | 3811 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | [20 empty] | 0
| 588 | 5 | B | SSMHT0007240 | SS.MH.T0007240 | 32.3118 | -95.3567 | K18 | 3611 RED LEAF DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.76 | 141.4256 | [18 empty] | 0
| 589 | 5 | C | SSMHT0007247 | SS.MH.T0007247 | 32.3121 | -95.3558 | K18 | 3782 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 16.8 | 217.288 | [18 empty] | 0
| 590 | 5 | C | SSMHT0007248 | SS.MH.T0007248 | 32.312 | -95.3554 | K18 | 3770 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.08 | 145.4448 | [18 empty] | 0
| 591 | 5 | B | SSMHT0007249 | SS.MH.T0007249 | 32.312 | -95.3542 | K18 | 3734 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.8 | 141.928 | [18 empty] | 0
| 592 | 5 | B | SSMHT0007250 | SS.MH.T0007250 | 32.3122 | -95.3538 | K18 | 3722 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.82 | 154.7392 | [18 empty] | 0
| 593 | 5 | C | SSMHT0007251 | SS.MH.T0007251 | 32.3123 | -95.3536 | K18 | 3729 HOGAN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.24 | 147.4544 | [18 empty] | 0
| 594 | 5 | B | SSMHT0007269 | SS.MH.T0007269 | 32.3144 | -95.355 | K18 | 3883 LOUISE CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.82 | 117.0592 | [18 empty] | 0
| 595 | 5 | B | SSMHT0007325 | SS.MH.T0007325 | 32.3144 | -95.3521 | K18 | 3868 LAMB DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.4 | 111.784 | [18 empty] | 0
| 596 | 5 | X-CNL | SSMHT0007326 | SS.MH.T0007326 |  |  | K18 | 3850 LAMB DR |  |  |  | Yard | Unpaved | [24 empty] | 0
| 597 | 5 | X-CNL | SSMHT0007327 | SS.MH.T0007327 |  |  | K18 | 3808 LAMB DR |  |  |  | Yard | Unpaved | [24 empty] | 0
| 598 | 5 | B | SSMHT0007328 | SS.MH.T0007328 | 32.3154 | -95.3533 | K18 | 3850 SCENIC DR | Solid |  | Yes | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 6.87 | 92.5672 | [18 empty] | 0
| 599 | 5 | X-CNO | SSMHT0007329 | SS.MH.T0007329 | 32.3153 | -95.3544 | K18 | 3851 SCENIC DR | Solid |  |  | Yard | Unpaved | Below Grade | 1 | [22 empty] | 0
| 600 | 5 | B | SSMHT0007330 | SS.MH.T0007330 | 32.3121 | -95.3531 | K18 | 4133 SCENIC DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.12 | 145.9472 | [18 empty] | 0
| 601 | 5 | X-CNL | SSMHT0007331 | SS.MH.T0007331 |  |  | K18 | 4133 SCENIC DR |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 602 | 5 | B | SSMHT0007332 | SS.MH.T0007332 | 32.3121 | -95.3519 | K18 | 4145 SCENIC DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.34 | 123.5904 | [18 empty] | 0
| 603 | 5 | C | SSMHT0007333 | SS.MH.T0007333 | 32.3176 | -95.352 | K18 | BLDG 29 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.15 | 108.644 | [18 empty] | 0
| 604 | 5 | B | SSMHT0007613 | SS.MH.T0007613 | 32.3176 | -95.3569 | K18 | 4055 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.56 | 151.4736 | [18 empty] | 0
| 605 | 5 | B | SSMHT0007614 | SS.MH.T0007614 | 32.317 | -95.3574 | K18 | 4141 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.27 | 160.3912 | [18 empty] | 0
| 606 | 5 | C | SSMHT0007626 | SS.MH.T0007626 | 32.3202 | -95.3609 | J17 | 4468 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 15.72 | 203.7232 | [18 empty] | 0
| 607 | 5 | B | SSMHT0007627 | SS.MH.T0007627 | 32.3179 | -95.3631 | J18 | 2847 STEWART WAY | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.94 | 80.8864 | [18 empty] | 0
| 608 | 5 | X-CNL | SSMHT0007628 | SS.MH.T0007628 |  |  | J18 | 2847 STEWART WAY |  |  |  | Field | Unpaved | [24 empty] | 0
| 609 | 5 | X-CNL | SSMHT0007629 | SS.MH.T0007629 |  |  | J17 | 2890 STEWART WAY |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 610 | 5 | C | SSMHT0007631 | SS.MH.T0007631 | 32.3202 | -95.3592 | J17 | 4398 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.04 | 132.3824 | [18 empty] | 0
| 611 | 5 | C | SSMHT0007632 | SS.MH.T0007632 | 32.3203 | -95.3587 | K17 | 4387 HOGAN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.68 | 140.4208 | [18 empty] | 0
| 612 | 5 | B | SSMHT0007633 | SS.MH.T0007633 | 32.3202 | -95.3584 | K17 | 4390 HOGAN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.68 | 102.7408 | [18 empty] | 0
| 613 | 5 | X-CNL | SSMHT0007639 | SS.MH.T0007639 |  |  | K17 | 2819 HOGAN CT |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 614 | 5 | X-CNO | SSMHT0007679 | SS.MH.T0007679 | 32.3207 | -95.3654 | J17 | 2849 J. CUPIT CT | Solid |  |  | Road Shoulder | Unpaved | Below Grade | 13 | [22 empty] | 0
| 615 | 5 | B | SSMHT0007795 | SS.MH.T0007795 | 32.3149 | -95.3413 | K18 | 3120 S. SW LP 323 | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 0 | 6.28 | [18 empty] | 0
| 616 | 5 | B | SSMHT0007796 | SS.MH.T0007796 | 32.3143 | -95.3388 | L18 | 3142 PARK CENTER DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.22 | 71.8432 | [18 empty] | 0
| 617 | 5 | C | SSMHT0007797 | SS.MH.T0007797 | 32.3143 | -95.3389 | L18 | 3120 S. SW LP 323 | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.16 | 196.6896 | [18 empty] | 0
| 618 | 5 | B | SSMHT0007798 | SS.MH.T0007798 | 32.3277 | -95.3321 | L17 | 2469 EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.12 | 108.2672 | [18 empty] | 0
| 619 | 5 | B | SSMHT0007799 | SS.MH.T0007799 | 32.3278 | -95.3309 | L17 | 2469 EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.68 | 152.9808 | [18 empty] | 0
| 620 | 5 | B | SSMHT0007800 | SS.MH.T0007800 | 32.3278 | -95.3297 | L17 | 2461 EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 60 Round | Concrete | 13.31 | 173.4536 | [18 empty] | 0
| 621 | 5 | B | SSMHT0007801 | SS.MH.T0007801 | 32.3278 | -95.3285 | L17 | 2467 EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 14.23 | 185.0088 | [18 empty] | 0
| 622 | 5 | B | SSMHT0007802 | SS.MH.T0007802 | 32.3278 | -95.3272 | L17 | NONE EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.82 | 154.7392 | [18 empty] | 0
| 623 | 5 | B | SSMHT0007803 | SS.MH.T0007803 | 32.3278 | -95.3261 | L17 | 800 BLK EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.9 | 130.624 | [18 empty] | 0
| 624 | 5 | B | SSMHT0007804 | SS.MH.T0007804 | 32.3277 | -95.3255 | L17 | 800 BLK EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.02 | 157.2512 | [18 empty] | 0
| 625 | 5 | B | SSMHT0007805 | SS.MH.T0007805 | 32.3275 | -95.3249 | L17 | 800 BLK EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.42 | 174.8352 | [18 empty] | 0
| 626 | 5 | B | SSMHT0007806 | SS.MH.T0007806 | 32.3271 | -95.3237 | L17 | 800 BLK EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.5 | 163.28 | [18 empty] | 0
| 627 | 5 | B | SSMHT0007807 | SS.MH.T0007807 | 32.3266 | -95.3226 | L17 | 800 BLK EARL CAMPBELL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.14 | 146.1984 | [18 empty] | 0
| 628 | 5 | C | SSMHT0007826 | SS.MH.T0007826 | 32.3179 | -95.3563 | K18 | 4224 HOGAN DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 629 | 5 | C | SSMHT0007827 | SS.MH.T0007827 | 32.321 | -95.3593 | J17 | 4402 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.38 | 124.0928 | [18 empty] | 0
| 630 | 5 | C | SSMHT0007828 | SS.MH.T0007828 | 32.3208 | -95.3594 | J17 | 4402 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.92 | 130.8752 | [18 empty] | 0
| 631 | 5 | C | SSMHT0007832 | SS.MH.T0007832 | 32.3238 | -95.3619 | J17 | 4498 CASCADES SHORELINE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.13 | 146.0728 | [18 empty] | 0
| 632 | 5 | B | SSMHT0007833 | SS.MH.T0007833 | 32.3238 | -95.3622 | J17 | 4498 CASCADES SHORELINE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.94 | 118.5664 | [18 empty] | 0
| 633 | 5 | X-CNO | SSMHT0007834 | SS.MH.T0007834 | 32.3232 | -95.3609 | J17 | 4550 CASCADES SHORELINE DR | Solid |  |  | Street | Paved - Concrete | At Grade | [23 empty] | 0
| 634 | 5 | B | SSMHT0007835 | SS.MH.T0007835 | 32.3234 | -95.3614 | J17 | 4486 CASCADES SHORELINE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.08 | 70.0848 | [18 empty] | 0
| 635 | 5 | B | SSMHT0007836 | SS.MH.T0007836 | 32.3231 | -95.3601 | J17 | 4550 CASCADES SHORELINE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.24 | 147.4544 | [18 empty] | 0
| 636 | 5 | B | SSMHT0007837 | SS.MH.T0007837 | 32.3227 | -95.3593 | J17 | 4550 CASCADES SHORELINE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.62 | 152.2272 | [18 empty] | 0
| 637 | 5 | X-CNO | SSMHT0007838 | SS.MH.T0007838 | 32.3225 | -95.359 | J17 | 4550 CASCADES SHORELINE DR | Solid |  |  | Street | Paved - Concrete | At Grade | [23 empty] | 0
| 638 | 5 | B | SSMHT0009059 | SS.MH.T0009059 | 32.321 | -95.3497 | K17 | 4110 BRIARWOOD RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.46 | 125.0976 | [18 empty] | 0
| 639 | 5 | B | SSMHT0009069 | SS.MH.T0009069 | 32.3221 | -95.3524 | K17 | 4134 BRIARWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.18 | 171.8208 | [18 empty] | 0
| 640 | 5 | B | SSMHT0009073 | SS.MH.T0009073 | 32.3223 | -95.3531 | K17 | 3363 CASCADE BLVD | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.26 | 147.7056 | [18 empty] | 0
| 641 | 5 | B | SSMHT0009084 | SS.MH.T0009084 | 32.3221 | -95.3562 | K17 | 4331 MARK HAYES CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.2 | 121.832 | [18 empty] | 0
| 642 | 5 | B | SSMHT0009085 | SS.MH.T0009085 | 32.322 | -95.3559 | K17 | 4331 MARK HAYES CT | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.08 | 132.8848 | [18 empty] | 0
| 643 | 5 | B | SSMHT0009086 | SS.MH.T0009086 | 32.3218 | -95.3558 | K17 | 4334 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.82 | 117.0592 | [18 empty] | 0
| 644 | 5 | B | SSMHT0009087 | SS.MH.T0009087 | 32.3218 | -95.355 | K17 | 4318 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.52 | 176.0912 | [18 empty] | 0
| 645 | 5 | B | SSMHT0009088 | SS.MH.T0009088 | 32.3217 | -95.3547 | K17 | 4312 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.7 | 140.672 | [18 empty] | 0
| 646 | 5 | B | SSMHT0009089 | SS.MH.T0009089 | 32.322 | -95.3564 | K17 | 4353 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.47 | 150.3432 | [18 empty] | 0
| 647 | 5 | C | SSMHT0009090 | SS.MH.T0009090 | 32.3218 | -95.3566 | K17 | 4350 CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.38 | 149.2128 | [18 empty] | 0
| 648 | 5 | C | SSMHT0009094 | SS.MH.T0009094 | 32.3214 | -95.3583 | K17 | 4400 BLK CASCADES BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.58 | 101.4848 | [18 empty] | 0
| 649 | 5 | B | SSMHT0009095 | SS.MH.T0009095 | 32.3221 | -95.3588 | K17 | 4405 CASCADES SHORELINE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.12 | 95.7072 | [18 empty] | 0
| 650 | 5 | X-CNL | SSMHT0009401 | SS.MH.T0009401 |  |  | L18 | 3110 TOWNE PARK DR |  |  |  | Parking Lot | Paved - Asphalt | [24 empty] | 0
| 651 | 5 | B | SSMHT0009402 | SS.MH.T0009402 | 32.3123 | -95.3375 | L18 | 3110 (36) TOWNE PARK DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 14.6 | 189.656 | [18 empty] | 0
| 652 | 5 | D | SSMHT0009403 | SS.MH.T0009403 | 32.316 | -95.3287 | L18 | 3020 RHINEHART ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.25 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 653 | 5 | X-CNL | SSMHT0009404 | SS.MH.T0009404 |  |  | L19 | 3915 W. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 654 | 5 | X-CNL | SSMHT0009405 | SS.MH.T0009405 |  |  | L19 | 3920 S. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 655 | 5 | X-Buried | SSMHT0009406 | SS.MH.T0009406 | 32.3084 | -95.3375 | L18 | 3024 MC CORMICK LN |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 656 | 5 | D | SSMHT0009407 | SS.MH.T0009407 | 32.3421 | -95.339 | L15 | 3400 BLK BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 657 | 5 | X-Buried | SSMHT0009408 | SS.MH.T0009408 | 32.3421 | -95.3363 | L15 | 701 DUCKENFIELD AVE |  |  |  | Yard | Unpaved | Below Grade | 12 | [22 empty] | 0
| 658 | 5 | X-Buried | SSMHT0009409 | SS.MH.T0009409 | 32.3409 | -95.3337 | L15 | 800 BRITTON AVE |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 659 | 5 | X-Buried | SSMHT0009410 | SS.MH.T0009410 | 32.341 | -95.3337 | L15 | 800 BRITTON AVE |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 660 | 5 | X-CNL | SSMHT0009411 | SS.MH.T0009411 |  |  | L15 | 815 S. BUCKLEY ST |  |  |  | Yard | Unpaved | [24 empty] | 0
| 661 | 5 | D | SSMHT0009483 | SS.MH.T0009483 | 32.3213 | -95.3417 | K17 | 2700 S.SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 4.52 | 63.0512 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
| 662 | 5 | D | SSMHT0009484 | SS.MH.T0009484 | 32.342 | -95.3526 | K15 | 4550 ST HWY 31 W. | None |  | No | Trees/Woods | Unpaved | Above Grade | 7 | CO 6" | Other | 3 |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
| 663 | 5 | C | SSMHT0009485 | SS.MH.T0009485 | 32.3227 | -95.3421 | K17 | 2603 S. SW LP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.96 | 143.9376 | [18 empty] | 0
| 664 | 5 | X-CNL | SSMHT0009486 | SS.MH.T0009486 |  |  | K16 | 1000 S. SW LP 323 |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 665 | 5 | X-Buried | SSMHT0009487 | SS.MH.T0009487 | 32.3197 | -95.3332 | L17 | 2734 RACHEL AVE |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 666 | 5 | X-CNL | SSMHT0009488 | SS.MH.T0009488 |  |  | L17 | 2738 DEPRIEST AVE |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 667 | 5 | X-CNL | SSMHT0009489 | SS.MH.T0009489 |  |  | L15 | 819 S. BUCKLEY ST |  |  |  | Yard | Unpaved | [24 empty] | 0
| 668 | 5 | D | SSMHT0009490 | SS.MH.T0009490 | 32.3406 | -95.3267 | L15 | 2310 BELLWOOD RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
Upated | 669 | 5 | X-CNL | SSMHT0009491 | SS.MH.T0009491 |  |  | L16 | 847 CLARK ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 670 | 5 | X-Buried | SSMHT0009492 | SS.MH.T0009492 | 32.3378 | -95.3283 | L16 | 2431 W. JACKSON ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 671 | 5 | D | SSMHT0009493 | SS.MH.T0009493 | 32.3366 | -95.329 | L16 | 2515 W. SHAW ST | Vented |  | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 4.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 672 | 5 | D | SSMHT0009494 | SS.MH.T0009494 | 32.339 | -95.3319 | L16 | 902 S. TURNER ST | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 6.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 673 | 5 | D | SSMHT0009495 | SS.MH.T0009495 | 32.3389 | -95.3319 | L16 | 902 S. TURNER ST | Vented |  | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 13 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 674 | 5 | D | SSMHT0009496 | SS.MH.T0009496 | 32.3389 | -95.336 | L16 | 930 DUCKENFIELD AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 675 | 5 | D | SSMHT0009497 | SS.MH.T0009497 | 32.3388 | -95.336 | L16 | 936 DUCKENFIELD AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 676 | 5 | B | SSMHT0009498 | SS.MH.T0009498 | 32.3383 | -95.3349 | L16 | 3116 CARDEN LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.9 | [19 empty] | 0
| 677 | 5 | X-Buried | SSMHT0009499 | SS.MH.T0009499 | 32.3375 | -95.334 | L16 | 3014 W. JACKSON ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 678 | 5 | X-CNL | SSMHT0009629 | SS.MH.T0009629 |  |  | L16 | 909 S. LYONS AVE |  |  |  | Yard | Unpaved | [24 empty] | 0
| 679 | 5 | X-CNL | SSMHT0009630 | SS.MH.T0009630 |  |  | L16 | 2305 W. ROBBINS ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 680 | 5 | C | SSMHT0009631 | SS.MH.T0009631 | 32.3433 | -95.347 | K15 | 4136 CHANDLER HWY | Vented | 2 | No | Parking Lot | Unpaved | Above Grade | 1 | CO 6" | Other | [20 empty] | 0
| 681 | 5 | X-CNL | SSMHT0009634 | SS.MH.T0009634 |  |  | K16 | 1029 WHITESIDE RD |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 682 | 5 | D | SSMHT0009635 | SS.MH.T0009635 | 32.3184 | -95.3332 | L17 | 2902 MOOREHEAD ST | Vented | 2 | No | Gutter | Paved - Concrete | At Grade |  | CO 6" | Other | 9.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 683 | 5 | D | SSMHT0009636 | SS.MH.T0009636 | 32.3133 | -95.3362 | L18 | 3110 TOWNE PARK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.8 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 684 | 5 | D | SSMHT0009637 | SS.MH.T0009637 | 32.315 | -95.3406 | K18 | 3120 S. SW LP 323 | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 685 | 5 | D | SSMHT0009695 | SS.MH.T0009695 | 32.3133 | -95.3553 | K18 | 3468 PINE TERRACE DR | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 8" | Other | 8.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 686 | 5 | X-CNL | SSMHT0009696 | SS.MH.T0009696 |  |  | K18 | 4087 HOGAN DR |  |  |  | Yard | Unpaved | [24 empty] | 0
| 687 | 5 | X-CNL | SSMHT0009697 | SS.MH.T0009697 |  |  | K18 | 4087 HOGAN DR |  |  |  | Yard | Unpaved | [24 empty] | 0
| 688 | 5 | D | SSMHT0009719 | SS.MH.T0009719 | 32.3301 | -95.3367 | L16 | 1553 BENNETTE AVE | Vented | 2 |  | Street | Paved - Asphalt | At Grade | [11 empty] | 3000 | [11 empty] | 3000 | Repair
| 689 | 5 | D | SSMHT0009720 | SS.MH.T0009720 | 32.3175 | -95.3528 | K18 | 3837 PUTTING LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 690 | 5 | X-CNL | SSMHT0009721 | SS.MH.T0009721 |  |  | K18 | 3849 PUTTING LN |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 691 | 5 | B | SSMHT0009722 | SS.MH.T0009722 | 32.32 | -95.3617 | J17 | 285 STEWART WAY | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 9 | [19 empty] | 0
| 692 | 5 | C | SSMHT0009723 | SS.MH.T0009723 | 32.3205 | -95.3627 | J17 | 2931 STEWART WAY | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 11.2 | [19 empty] | 0
| 693 | 5 | C | SSMHT0009724 | SS.MH.T0009724 | 32.3214 | -95.3637 | J17 | 4555 CASCADES BLVD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 8.9 | [19 empty] | 0
| 694 | 5 | C | SSMHT0009725 | SS.MH.T0009725 | 32.3212 | -95.3649 | J17 | 2861 J. CUPIT CT | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 9.9 | [19 empty] | 0
| 695 | 5 | C | SSMHT0009727 | SS.MH.T0009727 | 32.3217 | -95.3619 | J17 | 4516 TRIGGS TRACE | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | [20 empty] | 0
| 696 | 5 | D | SSMHT0009729 | SS.MH.T0009729 | 32.322 | -95.3607 | J17 | 4463 COUPLES CT | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 14 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 697 | 5 | D | SSMHT0009737 | SS.MH.T0009737 | 32.3133 | -95.3532 | K18 | 3958 SCENIC DR | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 7.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 698 | 5 | X-CNL | SSMHT0009738 | SS.MH.T0009738 |  |  | K18 | 3949 SCENIC DR |  |  |  | Yard | Unpaved | [24 empty] | 0
| 699 | 5 | B | SSMHT0009739 | SS.MH.T0009739 | 32.3134 | -95.3546 | K18 | 3444 PINE TERRACE DR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.33 | 110.9048 | [18 empty] | 0
| 700 | 5 | C | SSMHT0009856 | SS.MH.T0009856 | 32.3213 | -95.3505 | K17 | 4122 BRIARWOOD RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Other | 8 | [19 empty] | 0
| 701 | 5 | X-CNL | SSMHT0009976 | SS.MH.T0009976 |  |  | K18 | 3831 LAMB DR |  |  |  | Yard | Unpaved | [24 empty] | 0
| 702 | 5 | X-CNL | SSMHT0009994 | SS.MH.T0009994 |  |  | L17 | 2815 FRANKSTON HWY |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 703 | 5 | D | SSMHT0009995 | SS.MH.T0009995 | 32.3201 | -95.3249 | L17 | 2721 MONROE ST | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 704 | 5 | D | SSMHT0009996 | SS.MH.T0009996 | 32.3185 | -95.3258 | L17 | 2214 DAVIS AVE | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 705 | 5 | D | SSMHT0009997 | SS.MH.T0009997 | 32.3184 | -95.3271 | L17 | 2300 BLK HALL ST | Vented | 2 | No | Gutter | Paved - Concrete | Above Grade | 1 | CO 6" | Other | 5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 706 | 5 | X-Buried | SSMHT0009998 | SS.MH.T0009998 | 32.3183 | -95.3266 | L17 | 2901 GARDNER AVE |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 707 | 5 | D | SSMHT0009999 | SS.MH.T0009999 | 32.3463 | -95.3461 | K15 | 406 MORGAN AVE | Vented | 2 | No | Road Shoulder | Paved - Concrete | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 708 | 5 | D | SSMHT0010000 | SS.MH.T0010000 | 32.3457 | -95.3512 | K15 | NONE OLD CHANDLER RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 709 | 5 | X-CNL | SSMHT0010001 | SS.MH.T0010001 |  |  | K15 | 4209 OLD CHANDLER RD |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 710 | 5 | D | SSMHT0010002 | SS.MH.T0010002 | 32.3143 | -95.3329 | L18 | 3117 SEATON ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.52 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 711 | 5 | X-Buried | SSMHT0010003 | SS.MH.T0010003 | 32.3415 | -95.3436 | K15 | 709 WHITESIDE RD |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 712 | 5 | D | SSMHT0010004 | SS.MH.T0010004 | 32.3418 | -95.3436 | K15 | 703 WHITESIDE RD | Vented | 2 | No | Street | Paved - Asphalt | Above Grade | 1 | CO 6" | Other |  |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
| 713 | 5 | D | SSMHT0010005 | SS.MH.T0010005 | 32.3437 | -95.3436 | K15 | 603 WHITESIDE RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 714 | 5 | X-CNL | SSMHT0010006 | SS.MH.T0010006 |  |  | K15 | 4285 CHANDLER HWY |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 715 | 5 | D | SSMHT0010090 | SS.MH.T0010090 | 32.3198 | -95.3346 | L17 | 2736 TOL AVE | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 9.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 716 | 5 | B | SSMHT0010091 | SS.MH.T0010091 | 32.3193 | -95.333 | L17 | 2902 WALTON RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4 | [19 empty] | 0
| 717 | 5 | X-CNL | SSMHT0010092 | SS.MH.T0010092 |  |  | L17 | 2902 WALTON RD |  |  |  | Street | Paved - Concrete | [24 empty] | 0
| 718 | 5 | X-Buried | SSMHT0010093 | SS.MH.T0010093 | 32.3189 | -95.3343 | L17 | 2806 PEARL ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 719 | 5 | X-CNL | SSMHT0010094 | SS.MH.T0010094 |  |  | L18 | 2615 MADISON ST |  |  |  | Yard | Unpaved | [24 empty] | 0
| 720 | 5 | X-Buried | SSMHT0010095 | SS.MH.T0010095 | 32.3182 | -95.3295 | L17 | 2500 BLKPATRICK DR |  |  |  | Road Shoulder | Unpaved |  | 12 | [22 empty] | 0
| 721 | 5 | X-Buried | SSMHT0010096 | SS.MH.T0010096 | 32.3173 | -95.3279 | L18 | 2922 MEYER AVE |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 722 | 5 | B | SSMHT0010097 | SS.MH.T0010097 | 32.3172 | -95.3282 | L18 | 2400 BLK MADISON ST | Vented | 2 | No | Gutter | Paved - Concrete | At Grade |  | CO 6" | Other | 7.4 | [19 empty] | 0
| 723 | 5 | X-Buried | SSMHT0010098 | SS.MH.T0010098 | 32.3173 | -95.33 | L18 | 2603 MADISON ST |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 724 | 5 | D | SSMHT0010099 | SS.MH.T0010099 | 32.3152 | -95.331 | L18 | 3000 BLK BUDDIE ST | Vented | 2 | No | Gutter | Paved - Concrete | At Grade |  | CO 6" | Other | 3.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 725 | 5 | D | SSMHT0010100 | SS.MH.T0010100 | 32.3144 | -95.3298 | L18 | 2706 LUTHER ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 2.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 726 | 5 | D | SSMHT0010101 | SS.MH.T0010101 | 32.3143 | -95.3305 | L18 | 2708 SARA ST | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 7.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 727 | 5 | D | SSMHT0010268 | SS.MH.T0010268 | 32.3151 | -95.3399 | K18 | 3211 TOWN WAY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 728 | 5 | X-Buried | SSMHT0010330 | SS.MH.T0010330 | 32.316 | -95.3337 | L18 | 3111 SEATON ST |  |  |  | Trees/Woods | Unpaved | Below Grade | 9 | [22 empty] | 0
| 729 | 5 | B | SSMHT0010340 | SS.MH.T0010340 | 32.3464 | -95.3427 | K15 | 3904 OLD CHANDLER RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 5.64 | 77.1184 | [18 empty] | 0
| 730 | 5 | D | SSMHT0010380 | SS.MH.T0010380 | 32.3134 | -95.354 | K18 | 3438 PINE TERRACE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 731 | 5 | D | SSMHT0010404 | SS.MH.T0010404 | 32.3201 | -95.3598 | J17 | 4418 CASCADES BLVD | None |  | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 732 | 5 | C | SSMHT0010405 | SS.MH.T0010405 | 32.3198 | -95.3559 | K17 | 2810 HOGAN CT | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.9 | [19 empty] | 0
| 733 | 5 | D | SSMHT0010423 | SS.MH.T0010423 | 32.3137 | -95.3384 | L18 | 3208 PARK CENTER DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 734 | 5 | X-CNL | SSMHT0010425 | SS.MH.T0010425 |  |  | M18 | 3142 PARK CENTER DR |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 735 | 5 | D | SSMHT0010518 | SS.MH.T0010518 | 32.3215 | -95.3543 | K17 | 4306 CASCADES BLVD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 8.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 736 | 5 | D | SSMHT0010519 | SS.MH.T0010519 | 32.3218 | -95.3562 | K17 | 4350 CASCADES BLVD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 737 | 5 | B | SSMHT0010725 | SS.MH.T0010725 | 32.3154 | -95.3394 | L18 | 3211 TOWNE WAY DR | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.06 | 82.3936 | [18 empty] | 0
| 738 | 5 | B | SSMHT0010734 | SS.MH.T0010734 | 32.3391 | -95.3337 | L16 | 956 BRITTON AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13 | [19 empty] | 0
| 739 | 5 | D | SSMHT0010903 | SS.MH.T0010903 | 32.3386 | -95.3372 | L16 | 1019 BOYD AVE | Solid |  | No | Street | Unpaved | Above Grade | 21 | Std 48 Round | Concrete | 4.74 | 65.8144 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 740 | 5 | C | SSMHT0011488 | SS.MH.T0011488 | 32.3471 | -95.342 | K15 | 430 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 8.06 | 107.5136 | [18 empty] | 0
| 741 | 5 | X-CNL | SSMHT0011541 | SS.MH.T0011541 |  |  | K15 | 4010 SUEL DR |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 742 | 5 | B | SSMHT0011698 | SS.MH.T0011698 | 32.315 | -95.3323 | L18 | 2824 LUTHER ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.4 | 99.224 | [18 empty] | 0
| 743 | 5 | B | SSMHT0011760 | SS.MH.T0011760 | 32.3389 | -95.3337 | L16 | 1007 BRITTON AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | [20 empty] | 0
| 744 | 5 | C | SSMHT0011761 | SS.MH.T0011761 | 32.348 | -95.3435 | K15 | 300 BLK WHITESIDE RD | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 9.88 | 130.3728 | [18 empty] | 0
| 745 | 5 | D | SSMHT0011874 | SS.MH.T0011874 | 32.3461 | -95.338 | L15 | 3450 CHANDLER HWY | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Other | 5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 746 | 5 | D | SSMHT0012271 | SS.MH.T0012271 | 32.3359 | -95.3286 | L16 | 2510 HABITAT CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 747 | 5 | D | SSMHT0012405 | SS.MH.T0012405 | 32.3183 | -95.3358 | L17 | 3106 MOOREHEAD ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 748 | 5 | D | SSMHT0012410 | SS.MH.T0012410 | 32.3422 | -95.3497 | K15 | 4420 ST HWY 31 W. | None |  | No | Yard | Paved - Concrete | Above Grade | 4 | CO 8" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 749 | 5 | D | SSMHT0012411 | SS.MH.T0012411 | 32.3365 | -95.3318 | L16 | 2850 W. SHAW ST | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | 42 | Brick | 4.64 | 64.5584 | 2 | [6 empty] | 650 |  |  |  | 1936.752 | [6 empty] | 2586.752 | Rehabilitate
| 750 | 5 | C | SSMHT0012796 | SS.MH.T0012796 | 32.3367 | -95.34 | K16 | 1000 S.SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.46 | 74.8576 | [18 empty] | 0
| 751 | 5 | B | SSMHT0013059 | SS.MH.T0013059 | 32.3433 | -95.347 | K15 | 4136 CHANDLER HWY | Solid |  | No | Parking Lot | Unpaved | Above Grade | 6 | Std 60 Round | Concrete | 8.04 | 107.2624 | [18 empty] | 0
| 752 | 5 | D | SSMHT0013060 | SS.MH.T0013060 | 32.3421 | -95.3508 | K15 | 4420 ST HWY 31 W. | Solid |  | No | Yard | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 6.93 | 93.3208 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 753 | 5 | D | SSMHT0013061 | SS.MH.T0013061 | 32.342 | -95.3518 | K15 | 4550 ST HWY 31 W. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 11.66 | 152.7296 | 2 | [11 empty] | 4581.888 | [5 empty] | 4581.888 | Rehabilitate
| 754 | 5 | B | SSMHT0013467 | SS.MH.T0013467 | 32.3056 | -95.338 | L19 | 3915 W. SW LP 323 | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 4.96 | 68.5776 | [18 empty] | 0
| 755 | 5 | B | SSMHT0013533 | SS.MH.T0013533 | 32.3162 | -95.3539 | K18 | 3827 SCENIC DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.82 | 104.4992 | [18 empty] | 0
| 756 | 5 | B | SSMHT0013548 | SS.MH.T0013548 | 32.3281 | -95.3352 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 15.38 | 199.4528 | [18 empty] | 0
| 757 | 5 | X-CNO | SSMHT0013829 | SS.MH.T0013829 | 32.342 | -95.3413 | K15 | 3600 BLK BELLWOOD RD | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 758 | 5 | A | SSMHT0013925 | SS.MH.T0013925 | 32.3238 | -95.3624 | J17 | 4510 CASCADES SHORELINE DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.06 | 82.3936 | [18 empty] | 0
| 759 | 5 | B | SSMHT0013953 | SS.MH.T0013953 | 32.3208 | -95.3612 | J17 | 4454 TRIGGS TRACE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | [18 empty] | 0
| 760 | 5 | D | SSMHT0014475 | SS.MH.T0014475 | 32.3219 | -95.3422 | K17 | 2609 S. SW LP 323 | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 9.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 761 | 5 | X-Buried | SSMHT0014534 | SS.MH.T0014534 | 32.3198 | -95.3654 | J17 | 2831 J. CUPIT CT |  |  |  | Trees/Woods | Unpaved | Below Grade | 14 | [22 empty] | 0
| 762 | 5 | B | SSMHT0014535 | SS.MH.T0014535 | 32.32 | -95.3646 | J17 | 2831 J. CUPIT CT | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 7.08 | 95.2048 | [18 empty] | 0
| 763 | 5 | X-CNL | SSMHT0014536 | SS.MH.T0014536 |  |  | J17 | 2813 J. CUPIT CT |  |  |  | Drainage Ditch | Unpaved | [24 empty] | 0
| 764 | 5 | C | SSMHT0014537 | SS.MH.T0014537 | 32.3205 | -95.3637 | J17 | 2813 J. CUPIT CT | Solid |  | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.6 | 101.736 | [18 empty] | 0
| 765 | 5 | X-CNL | SSMHT0014538 | SS.MH.T0014538 |  |  | J17 | 2813 J. CUPIT CT |  |  |  | Drainage Ditch | Unpaved | [24 empty] | 0
| 766 | 5 | X-CNL | SSMHT0014543 | SS.MH.T0014543 |  |  | K15 | 3904 OLD CHANDLER RD |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 767 | 5 | X-CNL | SSMHT0014847 | SS.MH.T0014847 |  |  | K17 | 2025 S SOUTHWEST LOOP 323 |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 768 | 5 | C | SSMHT0014848 | SS.MH.T0014848 | 32.3262 | -95.3373 | L17 | 3258 EARL CAMPBELL PKWY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 7.44 | 99.7264 | [18 empty] | 0
| 769 | 5 | C | SSMHT0015472 | SS.MH.T0015472 | 32.3459 | -95.3389 | K15 | 3510 CHANDLER HWY | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Brick | 6.3 | 85.408 | [18 empty] | 0
| 770 | 5 | B | SSMHT0015515 | SS.MH.T0015515 | 32.3182 | -95.3302 | L17 | 2520 PATRICK ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.14 | 95.9584 | [18 empty] | 0
Holly need location update | 771 | 5 | C | SSMHT0015516 | SS.MH.T0015516 | 32.316 | -95.333 | L18 | 3111 SEATON ST | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 6.8 | 91.688 | [18 empty] | 0
| 772 | 5 | B | SSMHT0015517 | SS.MH.T0015517 | 32.3202 | -95.3616 | J17 | 2805 STEWART WAY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.74 | 153.7344 | [18 empty] | 0
| 773 | 5 | B | SSMHT0015523 | SS.MH.T0015523 | 32.315 | -95.3313 | L18 | 2812 LUTHER ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.78 | 91.4368 | [18 empty] | 0
| 774 | 5 | B | SSMHT0015537 | SS.MH.T0015537 | 32.3224 | -95.3332 | L17 | NONE TOL AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 6.74 | 90.9344 | [18 empty] | 0
| 775 | 5 | B | SSMHT0015538 | SS.MH.T0015538 | 32.3367 | -95.3337 | L16 | 1131 BRITTON AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 42 | Concrete | 3.66 | 52.2496 | [18 empty] | 0
| 776 | 5 | B | SSMHT0015539 | SS.MH.T0015539 | 32.3365 | -95.336 | L16 | 3209 W. SHAW ST | Solid |  | Yes | Road Shoulder | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.74 | 90.9344 | [18 empty] | 0
| 777 | 5 | D | SSMHT0015540 | SS.MH.T0015540 | 32.3221 | -95.3304 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 20 | Std 48 Round | Concrete | 12.9 | 168.304 | 2 | [11 empty] | 5049.12 | [5 empty] | 5049.12 | Rehabilitate
| 778 | 5 | B | SSMHT0015542 | SS.MH.T0015542 | 32.3332 | -95.3332 | L16 | 3201 ROBERTSON RD | Solid |  | Yes | Parking Lot | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.57 | 76.2392 | [18 empty] | 0
| 779 | 5 | C | SSMHT0015543 | SS.MH.T0015543 | 32.3339 | -95.3312 | L16 | 2821 ROBERTSON RD | Solid |  | No | Parking Lot | Unpaved | At Grade |  | Std 48 Round | Concrete | [20 empty] | 0
| 780 | 5 | B | SSMHT0015544 | SS.MH.T0015544 | 32.3331 | -95.3303 | L16 | 2821 ROBERTSON RD | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.41 | 124.4696 | [18 empty] | 0
| 781 | 5 | B | SSMHT0015545 | SS.MH.T0015545 | 32.3331 | -95.3329 | L16 | 3001 ROBERTSON RD | Vented | 1 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.61 | 114.4216 | [18 empty] | 0
| 782 | 5 | B | SSMHT0015546 | SS.MH.T0015546 | 32.3156 | -95.3392 | L18 | 3211 TOWNE WAY DR | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.83 | 79.5048 | [18 empty] | 0
| 783 | 5 | B | SSMHT0015547 | SS.MH.T0015547 | 32.3164 | -95.3393 | L18 | 3211 TOWNE WAY DR | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 4.8 | 66.568 | [18 empty] | 0
| 784 | 5 | D | SSMHT0015548 | SS.MH.T0015548 | 32.3164 | -95.3398 | L18 | 3211 TOWNE WAY DR | Solid |  | No | Parking Lot | Unpaved | Above Grade | 5 | CO 4" | Other | 3.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 785 | 5 | B | SSMHT0015581 | SS.MH.T0015581 | 32.3286 | -95.3352 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.72 | 178.6032 | [18 empty] | 0
| 786 | 5 | C | SSMHT0015582 | SS.MH.T0015582 | 32.3288 | -95.3356 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 6.9 | 92.944 | [18 empty] | 0
| 787 | 5 | B | SSMHT0015583 | SS.MH.T0015583 | 32.3286 | -95.3342 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.71 | 140.7976 | [18 empty] | 0
| 788 | 5 | B | SSMHT0015584 | SS.MH.T0015584 | 32.3294 | -95.3342 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.96 | 118.8176 | [18 empty] | 0
| 789 | 5 | C | SSMHT0015585 | SS.MH.T0015585 | 32.3294 | -95.3337 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 6.28 | 85.1568 | [18 empty] | 0
| 790 | 5 | C | SSMHT0015586 | SS.MH.T0015586 | 32.3299 | -95.3337 | L17 | 3013 EARL CAMPBELL PKWY | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 4.34 | 60.7904 | [18 empty] | 0
| 791 | 5 | B | SSMHT0015587 | SS.MH.T0015587 | 32.317 | -95.3539 | K18 | 3815 SCENIC DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.63 | 114.6728 | [18 empty] | 0
| 792 | 5 | D | SSMHT0015590 | SS.MH.T0015590 | 32.3468 | -95.3451 | K15 | 1419 OLD CHANDLER RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.22 | 84.4032 | 2 | [11 empty] | 2532.096 | [5 empty] | 2532.096 | Rehabilitate
| 793 | 5 | B | SSMHT0015594 | SS.MH.T0015594 | 32.3099 | -95.3374 | L18 | 3422 S. SE LP 323 | Solid |  | No | Drainage Ditch | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.58 | 101.4848 | [18 empty] | 0
| 794 | 5 | X-CNO | SSMHT0015595 | SS.MH.T0015595 | 32.3098 | -95.3376 | L18 | 3422 S. SE LP 323 | Solid |  |  | Parking Lot | Paved - Concrete | At Grade | [23 empty] | 0
| 795 | 5 | B | SSMHT0015596 | SS.MH.T0015596 | 32.3099 | -95.3377 | L18 | 3422 S. SE LP 323 | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.55 | 88.548 | [18 empty] | 0
| 796 | 5 | B | SSMHT0015597 | SS.MH.T0015597 | 32.3099 | -95.3382 | L18 | 3374 S. SE LP 323 | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 797 | 5 | B | SSMHT0015598 | SS.MH.T0015598 | 32.3099 | -95.3387 | L18 | 3350 S. SW LP 323 | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.22 | 96.9632 | [18 empty] | 0
| 798 | 5 | B | SSMHT0015599 | SS.MH.T0015599 | 32.3099 | -95.3393 | L18 | 3350 S. SW LP 323 | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.6 | 76.616 | [18 empty] | 0
| 799 | 5 | B | SSMHT0015602 | SS.MH.T0015602 | 32.3206 | -95.3418 | K17 | 2626 S. SW LP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.8 | 179.608 | [18 empty] | 0
| 800 | 5 | B | SSMHT0015603 | SS.MH.T0015603 | 32.3184 | -95.3634 | J18 | 2847 STEWART WAY | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.02 | 119.5712 | [18 empty] | 0
| 801 | 5 | D | SSMHT0015604 | SS.MH.T0015604 | 32.3112 | -95.3405 | K18 | 3210 S. SW LP 323 | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 9.46 | 125.0976 | 2 | [11 empty] | 3752.928 | [5 empty] | 3752.928 | Rehabilitate
| 802 | 5 | C | SSMHT0015605 | SS.MH.T0015605 | 32.3125 | -95.3378 | L18 | 3110 (3) TOWNE PARK DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 17.92 | 231.3552 | [18 empty] | 0
| 803 | 5 | X-Buried | SSMHT0015606 | SS.MH.T0015606 | 32.3116 | -95.3376 | L18 | 3110 TOWNE PARK DR |  |  |  | Parking Lot | Paved - Asphalt | [24 empty] | 0
| 804 | 5 | B | SSMHT0015607 | SS.MH.T0015607 | 32.3117 | -95.3363 | L18 | 3110 (22) TOWNE PARK DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.38 | 149.2128 | [18 empty] | 0
| 805 | 5 | D | SSMHT0015608 | SS.MH.T0015608 | 32.3123 | -95.3362 | L18 | 3110 (16) TOWNE PARK DR | Vented | 2 | No | Parking Lot | Paved - Asphalt | At Grade |  | CO 6" | Other | 12 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 806 | 5 | B | SSMHT0015609 | SS.MH.T0015609 | 32.3113 | -95.3361 | L18 | 3110 (18) TOWNE PARK DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.24 | 84.6544 | [18 empty] | 0
| 807 | 5 | B | SSMHT0015610 | SS.MH.T0015610 | 32.3108 | -95.3362 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 5.52 | 75.6112 | [18 empty] | 0
| 808 | 5 | X-CNO | SSMHT0015614 | SS.MH.T0015614 | 32.3154 | -95.3404 | K18 | 3010 S. SW LP 323 | Solid |  |  | Parking Lot | Paved - Concrete | At Grade | [23 empty] | 0
| 809 | 5 | X-CNO | SSMHT0015615 | SS.MH.T0015615 | 32.3183 | -95.3386 | L18 | 3220(100) WALTON RD | Solid |  |  | Sidewalk | Paved - Concrete | At Grade | [23 empty] | 0
| 810 | 5 | C | SSMHT0015616 | SS.MH.T0015616 | 32.3171 | -95.3387 | L18 | 3220(700) WALTON RD | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.02 | 69.3312 | [18 empty] | 0
| 811 | 5 | C | SSMHT0015617 | SS.MH.T0015617 | 32.3168 | -95.3376 | L18 | 3220(900) WALTON RD | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 4.04 | 57.0224 | [18 empty] | 0
| 812 | 5 | C | SSMHT0015618 | SS.MH.T0015618 | 32.3181 | -95.3379 | L18 | 3220(100) WALTON RD | Solid |  | No | Parking Lot | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.5 | 100.48 | [18 empty] | 0
| 813 | 5 | C | SSMHT0015619 | SS.MH.T0015619 | 32.3487 | -95.3427 | K15 | 400 S. SW LP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 5.48 | 75.1088 | [18 empty] | 0
| 814 | 5 | B | SSMHT0015669 | SS.MH.T0015669 | 32.3439 | -95.3404 | K15 | 530 S. SW LP 323 | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.64 | 139.9184 | [18 empty] | 0
| 815 | 5 | B | SSMHT0015670 | SS.MH.T0015670 | 32.3439 | -95.3394 | K15 | 503 S. SW LP 323 | Solid |  | No | Parking Lot | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 9.2 | 121.832 | [18 empty] | 0
| 816 | 5 | X-CNO | SSMHT0015671 | SS.MH.T0015671 | 32.3439 | -95.3392 | K15 | 3450 CHANDLER HWY | Solid |  |  | Parking Lot | Unpaved | Below Grade | 2 | [22 empty] | 0
| 817 | 5 | C | SSMHT0015678 | SS.MH.T0015678 | 32.3447 | -95.3395 | K15 | 530 S.SW LP 323 | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.42 | 74.3552 | [18 empty] | 0
| 818 | 5 | A | SSMHT0015683 | SS.MH.T0015683 | 32.329 | -95.3401 | K17 | 1822 S SOUTHWEST LOOP 323 | Vented | 2 | No | Sidewalk | Paved - Concrete | At Grade |  | CO 4" | Other | 7.92 | [19 empty] | 0
| 819 | 6 | A | SSMHT0009420 | SS.MH.T0009420 | 32.3495 | -95.3669 | J15 | 5706 WILLINGHAM DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.3 | [19 empty] | 0
| 820 | 8 | B | SSMHT0009980 | SS.MH.T0009980 | 32.3435 | -95.3205 | L15 | 1718 W HOUSTON ST | Solid |  | No | Driveway | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 10 | 131.88 | [18 empty] | 0
| 821 | 10 | A | SSMHT0000866 | SS.MH.T0000866 | 32.3881 | -95.3104 | M11 | NONE N NW LOOP 323 | Bolted |  | No | Trees/Woods | Unpaved | Above Grade | 19 | Std 48 Round | Concrete | 5.86 | 79.8816 | [18 empty] | 0
| 822 | 10 | A | SSMHT0010120 | SS.MH.T0010120 | 32.3664 | -95.3082 | M13 | 1605 N TENNEHA AVE | Vented | IRON |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.25 | [19 empty] | 0
| 823 | 13 | D | SSMHT0000783 | SS.MH.T0000783 | 32.3463 | -95.2917 | N15 | 903 E. FRONT ST. | Vented | 4 | No | Creek | Unpaved | Above Grade | 5 | 36 | Brick | 3.56 | 50.9936 | 2 |  | 1000 | [8 empty] | 1529.808 |  |  | 280 |  |  |  | 2809.808 | Rehabilitate
| 824 | 13 | C | SSMHT0004812 | SS.MH.T0004812 | 32.3294 | -95.2887 | N16 | 1821 S. FLEISHEL AVE. | Vented | 2 | No | Yard | Unpaved | Below Grade | 1 | Std 48 Round | Brick | 3.98 | 56.2688 | [18 empty] | 0
| 825 | 13 | B | SSMHT0011445 | SS.MH.T0011445 | 32.3383 | -95.2952 | N16 | 516 E. DODGE ST. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 36 | Concrete | 3.74 | 53.2544 | [18 empty] | 0
| 826 | 13 | C | SSMHT0014037 | SS.MH.T0014037 | 32.3456 | -95.2893 | N15 | 415 S FLEISHEL AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.18 | 71.3408 | [18 empty] | 0
| 827 | 14 | D | SSMHT0004659 | SS.MH.T0004659 | 32.3419 | -95.2769 | O15 | 800 BLK. S. PORTER ST. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | 32 | Brick | 3.78 | 53.7568 | 2 | [10 empty] | 1612.704 | [6 empty] | 1612.704 | Rehabilitate
| 828 | 14 | A | SSMHT0005869 | SS.MH.T0005869 | 32.3409 | -95.2771 | O15 | 800 BLK. S. PORTER ST. | Solid |  | No | Field | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 829 | 14 | X-Buried | SSMHT0005895 | SS.MH.T0005895 | 32.3452 | -95.2722 | O15 | 2314 OLD HENDERSON HWY |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 830 | 14 | A | SSMHT0010024 | SS.MH.T0010024 | 32.3356 | -95.2718 | O16 | 2312 SPARROW CIR | Vented | 0 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13.89 | [19 empty] | 0
| 831 | 14 | C | SSMHT0015211 | SS.MH.T0015211 | 32.3088 | -95.2717 | O18 | 3824 TROUP HWY | Solid |  | No | Yard | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 7.5 | 100.48 | [18 empty] | 0
| 832 | 14 | A | SSMHT0015213 | SS.MH.T0015213 | 32.3409 | -95.2772 | O15 | 800 BLK. S. PORTER ST. | Solid |  | No | Field | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 6.2 | 84.152 | [18 empty] | 0
| 833 | 15 | B | SSMHT0002951 | SS.MH.T0002951 | 32.3528 | -95.3028 | M14 | 303 N. BOIS D ARC AVE. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.7 | 65.312 | [18 empty] | 0
| 834 | 15 | B | SSMHT0011043 | SS.MH.T0011043 | 32.3489 | -95.3062 | M15 | 215 S. BONNER AVE. | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 5.7 | 77.872 | [18 empty] | 0
| 835 | 15 | X-CNO | SSMHT0015513 | SS.MH.T0015513 | 32.3489 | -95.3061 | M15 | 215 S. BONNER AVE. | Solid |  |  | Parking Lot | Paved - Concrete | Above Grade | 12 | [22 empty] | 0
| 836 | 16 | X-Buried | SSMHT0001480 | SS.MH.T0001480 | 32.2682 | -95.3305 | L22 | 2010 HOLLY CREEK DR. |  |  |  | Sidewalk | Paved - Concrete | [24 empty] | 0
| 837 | 17 | C | SSMHT0001709 | SS.MH.T0001709 | 32.3007 | -95.3144 | M19 | 1010 CHARLESTON DR | Vented | 2 | No | Yard | Unpaved | Below Grade |  | CO 6" | Other | 6.4 | [19 empty] | 0
| 838 | 17 | A | SSMHT0010194 | SS.MH.T0010194 | 32.2785 | -95.3222 | L21 | 1507 ROYAL OAK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.35 | [19 empty] | 0
| 839 | 17 | B | SSMHT0010887 | SS.MH.T0010887 | 32.2734 | -95.3024 | M22 | 8166 KEVIN DR. | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 9.4 | [19 empty] | 0
| 840 | 17 | X-CNO | SSMHT0013793 | SS.MH.T0013793 | 32.2878 | -95.3081 | M20 | 5621 OLD BULLARD RD |  |  |  | Yard | Unpaved | Below Grade | 5 | [22 empty] | 0
| 841 | 17 | B | SSMHT0014272 | SS.MH.T0014272 | 32.3029 | -95.3103 | M19 | 724 W. SW LOOP 323 | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.5 | 125.6 | [18 empty] | 0
| 842 | 17 | D | SSMHT0014669 | SS.MH.T0014669 | 32.2893 | -95.3223 | L20 | 1600 RICE RD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 3.89 | 55.1384 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair
| 843 | 17 | C | SSMHT0014683 | SS.MH.T0014683 | 32.3075 | -95.3354 | L18 | 3913 FRANKSTON HWY. | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.6 | 101.736 | [18 empty] | 0
| 844 | 18 | C | SSMHT0000320 | SS.MH.T0000320 | 32.2952 | -95.2808 | O19 | 1800 SHILOH RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Concrete | 5.68 | 77.6208 | [18 empty] | 0
| 845 | 18 | X-Buried | SSMHT0000528 | SS.MH.T0000528 | 32.2949 | -95.244 | P19 | 4414 CRESTIGE CT. |  |  |  | Yard | Unpaved | [24 empty] | 0
| 846 | 18 | B | SSMHT0001694 | SS.MH.T0001694 | 32.2931 | -95.2921 | N20 | 5100 SWEETBRIAR LN. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Concrete | 5.54 | 75.8624 | [18 empty] | 0
| 847 | 18 | B | SSMHT0003500 | SS.MH.T0003500 | 32.2936 | -95.3052 | M20 | 5215 BULLARD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Concrete | 6.01 | 81.7656 | [18 empty] | 0
| 848 | 18 | D | SSMHT0005213 | SS.MH.T0005213 | 32.2948 | -95.301 | N20 | 200 BLK SHILOH RD. | Vented | 2 | Yes | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Brick | 11.1 | 145.696 | 2 | [11 empty] | 4370.88 | [5 empty] | 4370.88 | Rehabilitate
| 849 | 18 | C | SSMHT0005215 | SS.MH.T0005215 | 32.2948 | -95.2998 | N20 | 300 BLK SHILOH RD. | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 14.38 | 186.8928 | [18 empty] | 0
| 850 | 18 | C | SSMHT0006242 | SS.MH.T0006242 | 32.3018 | -95.2754 | O19 | 4400 PALUXY DR | Solid |  | No | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 11.34 | 148.7104 | [18 empty] | 0
| 851 | 18 | D | SSMHT0009296 | SS.MH.T0009296 | 32.2869 | -95.3008 | N20 | 5610 S BROADWAY AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.24 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 852 | 18 | D | SSMHT0009311 | SS.MH.T0009311 | 32.2869 | -95.2855 | N20 | 1129 GARDEN PARK CIR. | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 3 | CO 6" | Other | 9.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 853 | 18 | D | SSMHT0009543 | SS.MH.T0009543 | 32.308 | -95.272 | N20 | 5400 CARMEL CT | Solid |  |  | Yard | Unpaved | Below Grade | 2 | CO 6" | Other | 1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 854 | 18 | A | SSMHT0010076 | SS.MH.T0010076 | 32.298 | -95.2722 | O19 | 4817 PRESTWICK LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.78 | [19 empty] | 0
| 855 | 18 | A | SSMHT0010162 | SS.MH.T0010162 | 32.2925 | -95.2808 | O20 | 1713 TIMBER CREEK DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.25 | [19 empty] | 0
| 856 | 18 | A | SSMHT0010265 | SS.MH.T0010265 | 32.32 | -95.322 | L17 | 2726 WALKER ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.3 | [19 empty] | 0
| 857 | 18 | C | SSMHT0013509 | SS.MH.T0013509 | 32.3056 | -95.2807 | O19 | 1726 SYBIL LN. | Solid |  | No | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 10.84 | 142.4304 | [18 empty] | 0
| 858 | 18 | B | SSMHT0014972 | SS.MH.T0014972 | 32.297 | -95.2759 | O19 | 2060 SHILOH RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 8.63 | 114.6728 | [18 empty] | 0
| 859 | 18 | B | SSMHT0015005 | SS.MH.T0015005 | 32.2866 | -95.2655 | O20 | 5731 ANDOVER DR | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 8.28 | 110.2768 | [18 empty] | 0
| 860 | 18 | A | SSMHT0015038 | SS.MH.T0015038 | 32.2863 | -95.293 | N20 | 5704 FOXCROFT RD. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10 | [19 empty] | 0
| 861 | 18 | A | SSMHT0015039 | SS.MH.T0015039 | 32.2862 | -95.293 | N20 | 5706 FOXCROFT RD. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.2 | [19 empty] | 0
| 862 | 18 | A | SSMHT0015214 | SS.MH.T0015214 | 32.291 | -95.2799 | O20 | 1708 TIMBER VIEW | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 22 | Std 48 Round | Concrete | 10.3 | 135.648 | [18 empty] | 0
| 863 | 18 | B | SSMHT0015215 | SS.MH.T0015215 | 32.2911 | -95.2801 | O20 | 1708 TIMBER VIEW | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 36 | Std 48 Round | Concrete | 11.16 | 146.4496 | [18 empty] | 0
| 864 | 18 | X-CNO | SSMHT0015514 | SS.MH.T0015514 | 32.3055 | -95.28 | O19 | 1800 SYBIL LN | Solid |  |  | Yard | Unpaved | At Grade | [23 empty] | 0
| 865 | 18 | D | SSMHT0015549 | SS.MH.T0015549 | 32.3054 | -95.2793 | O19 | 1826 SYBIL LN | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 12.64 | 165.0384 | 2 | [6 empty] | 650 |  |  |  |  | 4951.152 |  | 280 |  |  |  | 5881.152 | Rehabilitate
| 866 | 18 | C | SSMHT0015578 | SS.MH.T0015578 | 32.305 | -95.2794 | O19 | 1817 SYBIL LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.56 | 126.3536 | [18 empty] | 0
| 867 | 19 | X-CNL | SSMHT0003991 | SS.MH.T0003991 | 32.3187 | -95.3008 | M17 | 2737 S BROADWAY AVE |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 868 | 20 | B | SSMHT0000248 | SS.MH.T0000248 | 32.2494 | -95.2787 | N21 | 9127 PALUXY DR | Solid |  | Yes | Yard | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 8.72 | 115.8032 | [18 empty] | 0
| 869 | 20 | C | SSMHT0000249 | SS.MH.T0000249 | 32.2494 | -95.279 | O24 | 9127 PALUXY DR | Solid |  | Yes | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.76 | 103.7456 | [18 empty] | 0
| 870 | 20 | B | SSMHT0000250 | SS.MH.T0000250 | 32.2494 | -95.2793 | O24 | 1750 CENTENNIAL PKWY | Solid |  | Yes | Yard | Unpaved | Above Grade | 7 | Std 60 Round | Concrete | 6.85 | 92.316 | [18 empty] | 0
| 871 | 20 | B | SSMHT0000251 | SS.MH.T0000251 | 32.2484 | -95.279 | O24 | 1750 CENTENNIAL PKWY | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.98 | 93.9488 | [18 empty] | 0
| 872 | 20 | B | SSMHT0000311 | SS.MH.T0000311 | 32.2743 | -95.2897 | N21 | 8156 GREER DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.81 | 91.8136 | [18 empty] | 0
| 873 | 20 | C | SSMHT0000319 | SS.MH.T0000319 | 32.2661 | -95.2976 | N22 | 731 PURDUE DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.48 | 163.0288 | [18 empty] | 0
| 874 | 20 | X-CNL | SSMHT0000353 | SS.MH.T0000353 |  |  | M23 | 8208 CROOKED TRL |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 875 | 20 | X-CNL | SSMHT0000433 | SS.MH.T0000433 |  |  | M23 | 620 W CUMBERAND RD |  |  |  | Street | Paved - Concrete | [24 empty] | 0
| 876 | 20 | B | SSMHT0000533 | SS.MH.T0000533 | 32.2377 | -95.2977 | N25 | 9247 STONEBANK CROSSING | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.24 | 134.8944 | [18 empty] | 0
| 877 | 20 | B | SSMHT0000534 | SS.MH.T0000534 | 32.2375 | -95.2978 | N25 | 9246 STONEBANK CROSSING | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.16 | 133.8896 | [18 empty] | 0
| 878 | 20 | B | SSMHT0000535 | SS.MH.T0000535 | 32.2373 | -95.2977 | N25 | 9234 QUIET WATER | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.2 | 134.392 | [18 empty] | 0
| 879 | 20 | D | SSMHT0000536 | SS.MH.T0000536 | 32.237 | -95.2977 | N25 | 9245 QUIET WATER | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.3 | 135.648 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 880 | 20 | B | SSMHT0000537 | SS.MH.T0000537 | 32.2366 | -95.2983 | N25 | 9344 STONEBANK CROSSING | Solid |  | No | Yard | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.86 | 117.5616 | [18 empty] | 0
| 881 | 20 | C | SSMHT0000538 | SS.MH.T0000538 | 32.2367 | -95.2985 | N25 | 9344 STONEBANK CROSSING | Solid |  | No | Yard | Unpaved | Above Grade | 21 | Std 48 Round | Concrete | 18.9 | 243.664 | [18 empty] | 0
| 882 | 20 | C | SSMHT0000544 | SS.MH.T0000544 | 32.267 | -95.2912 | N22 | 8393 GARRETT RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 3.14 | 45.7184 | [18 empty] | 0
| 883 | 20 | B | SSMHT0000545 | SS.MH.T0000545 | 32.267 | -95.2925 | N22 | 8355 GARRETT RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.86 | 105.0016 | [18 empty] | 0
| 884 | 20 | B | SSMHT0000584 | SS.MH.T0000584 | 32.2587 | -95.3187 | M23 | 1301 W CUMBERLAND RD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.43 | 112.1608 | [18 empty] | 0
| 885 | 20 | X-CNL | SSMHT0000586 | SS.MH.T0000586 |  |  | M23 | 413 W CUMBERLAND RD |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 886 | 20 | C | SSMHT0000587 | SS.MH.T0000587 | 32.2587 | -95.3177 | M23 | 1501 W CUMBERLAND RD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 887 | 20 | C | SSMHT0000588 | SS.MH.T0000588 | 32.259 | -95.3175 | M23 | 413 W CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 7.77 | 103.8712 | [18 empty] | 0
| 888 | 20 | B | SSMHT0000589 | SS.MH.T0000589 | 32.2587 | -95.317 | M23 | 413 CUMBERLAND DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.64 | 127.3584 | [18 empty] | 0
| 889 | 20 | B | SSMHT0000590 | SS.MH.T0000590 | 32.2588 | -95.3162 | M23 | 413 CUMBERLAND RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 890 | 20 | D | SSMHT0000591 | SS.MH.T0000591 | 32.259 | -95.316 | M23 | 2401 W CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 7.76 | 103.7456 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 891 | 20 | C | SSMHT0000592 | SS.MH.T0000592 | 32.259 | -95.3153 | M23 | 8402 LAKEWAY DR | Solid |  | No | Yard | Unpaved | Above Grade | 29 | Std 60 Round | Concrete | 19.67 | 253.3352 | [18 empty] | 0
| 892 | 20 | B | SSMHT0001348 | SS.MH.T0001348 | 32.2464 | -95.2937 | N24 | 9441 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.76 | 128.8656 | [18 empty] | 0
| 893 | 20 | B | SSMHT0001349 | SS.MH.T0001349 | 32.2461 | -95.2938 | N24 | 9445 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.75 | 116.18 | [18 empty] | 0
| 894 | 20 | B | SSMHT0001350 | SS.MH.T0001350 | 32.2457 | -95.2938 | N24 | 9453 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.16 | 121.3296 | [18 empty] | 0
| 895 | 20 | B | SSMHT0001351 | SS.MH.T0001351 | 32.2457 | -95.2926 | N24 | 1226 RAINMAKER | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.31 | 98.0936 | [18 empty] | 0
| 896 | 20 | A | SSMHT0001352 | SS.MH.T0001352 | 32.2447 | -95.2938 | N24 | 9465 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.11 | 120.7016 | [18 empty] | 0
| 897 | 20 | B | SSMHT0001353 | SS.MH.T0001353 | 32.2442 | -95.2938 | N24 | 9465 CHEROKEE TRL. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.54 | 113.5424 | [18 empty] | 0
| 898 | 20 | D | SSMHT0001354 | SS.MH.T0001354 | 32.2441 | -95.2948 | N24 | NONE COVENTRY RD | Solid |  | No | Creek | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 6.64 | 89.6784 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 899 | 20 | B | SSMHT0001370 | SS.MH.T0001370 | 32.2609 | -95.3086 | M23 | 7925 S BROADWAY AVE | Solid |  | No | Yard | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 7.76 | 103.7456 | [18 empty] | 0
| 900 | 20 | C | SSMHT0001371 | SS.MH.T0001371 | 32.2609 | -95.3095 | M23 | 7925 S BROADWAY AVE | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 12.3 | 160.768 | [18 empty] | 0
| 901 | 20 | A | SSMHT0001372 | SS.MH.T0001372 | 32.2614 | -95.3095 | M23 | 7925 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.02 | 81.8912 | [18 empty] | 0
| 902 | 20 | C | SSMHT0001373 | SS.MH.T0001373 | 32.2614 | -95.3086 | M23 | 7925 S BROADWAY AVE | Solid |  | No | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 8.42 | 112.0352 | [18 empty] | 0
| 903 | 20 | B | SSMHT0001374 | SS.MH.T0001374 | 32.2606 | -95.3095 | M23 | 7925 S BROADWAY AVE | Solid |  | No | Yard | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 12.34 | 161.2704 | [18 empty] | 0
| 904 | 20 | C | SSMHT0001375 | SS.MH.T0001375 | 32.26 | -95.3095 | M23 | 8101 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 13.3 | 173.328 | [18 empty] | 0
| 905 | 20 | X-CNL | SSMHT0001376 | SS.MH.T0001376 |  |  | M23 | 8225 S BROADWAY AVE |  |  |  | Trees/Woods | Unpaved | Below Grade | [23 empty] | 0
| 906 | 20 | B | SSMHT0001413 | SS.MH.T0001413 | 32.2468 | -95.2933 | N24 | 9437 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.14 | 146.1984 | [18 empty] | 0
| 907 | 20 | B | SSMHT0001414 | SS.MH.T0001414 | 32.2571 | -95.3178 | M23 | 421W CUMBERLAND RD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 908 | 20 | C | SSMHT0001415 | SS.MH.T0001415 | 32.2572 | -95.3187 | M23 | 202 W CUMBERLAND RD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.17 | 108.8952 | [18 empty] | 0
| 909 | 20 | X-CNL | SSMHT0001416 | SS.MH.T0001416 |  |  | M23 | 202 W CUMBERLAND RD |  |  |  | Street | Unpaved | Below Grade |  | Std 48 Round | [21 empty] | 0
| 910 | 20 | A | SSMHT0001426 | SS.MH.T0001426 | 32.2448 | -95.2922 | N24 | 1235 COLT LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.14 | 121.0784 | [18 empty] | 0
| 911 | 20 | D | SSMHT0001427 | SS.MH.T0001427 | 32.2448 | -95.2915 | N24 | 1242 COLT LN | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 20 | Std 48 Round | Concrete | 16.24 | 210.2544 | 2 | [6 empty] | 650 |  |  |  |  | 6307.632 | [5 empty] | 6957.632 | Rehabilitate
| 912 | 20 | B | SSMHT0001428 | SS.MH.T0001428 | 32.2443 | -95.2914 | N24 | NONE COVENTRY PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.14 | 133.6384 | [18 empty] | 0
| 913 | 20 | B | SSMHT0001429 | SS.MH.T0001429 | 32.2446 | -95.2908 | N24 | 1236 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.18 | 58.7808 | [18 empty] | 0
| 914 | 20 | B | SSMHT0001430 | SS.MH.T0001430 | 32.2449 | -95.2901 | N24 | 1228 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.51 | 113.1656 | [18 empty] | 0
No change until CCTV | 915 | 20 | X-CNL | SSMHT0001431 | SS.MH.T0001431 |  |  | N24 | 1236 CENTENNIAL PKWY |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 916 | 20 | B | SSMHT0001432 | SS.MH.T0001432 | 32.2449 | -95.2893 | N24 | 1436 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.09 | 120.4504 | [18 empty] | 0
| 917 | 20 | C | SSMHT0001433 | SS.MH.T0001433 | 32.245 | -95.2887 | N24 | NONE CONVENTRY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 21.38 | 274.8128 | [18 empty] | 0
| 918 | 20 | C | SSMHT0001434 | SS.MH.T0001434 | 32.245 | -95.2872 | N24 | NONE COVENTRY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.06 | 107.5136 | [18 empty] | 0
| 919 | 20 | C | SSMHT0001435 | SS.MH.T0001435 | 32.245 | -95.2869 | N24 | NONE COVENTRY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 18.22 | 235.1232 | [18 empty] | 0
| 920 | 20 | X-CNL | SSMHT0001436 | SS.MH.T0001436 |  |  | N24 | NONE COVERNTRY RD |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 921 | 20 | C | SSMHT0001437 | SS.MH.T0001437 | 32.245 | -95.2845 | N24 | NONE CONVENTRY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 27.34 | 349.6704 | [18 empty] | 0
| 922 | 20 | B | SSMHT0001438 | SS.MH.T0001438 | 32.245 | -95.2844 | N24 | NONE COVENTRY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 60 Round | Concrete | 27.69 | 354.0664 | [18 empty] | 0
| 923 | 20 | C | SSMHT0001439 | SS.MH.T0001439 | 32.2453 | -95.2836 | N24 | 1527 SKIDMORE LN | Solid |  | No | Field | Unpaved | Above Grade | 29 | Std 48 Round | Concrete | 16.16 | 209.2496 | [18 empty] | 0
| 924 | 20 | B | SSMHT0001466 | SS.MH.T0001466 | 32.2572 | -95.3151 | M23 | 8436 LAKE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9 | 119.32 | [18 empty] | 0
| 925 | 20 | B | SSMHT0001467 | SS.MH.T0001467 | 32.2579 | -95.3152 | M23 | 8424 LAKE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.86 | 130.1216 | [18 empty] | 0
| 926 | 20 | B | SSMHT0001468 | SS.MH.T0001468 | 32.2585 | -95.3152 | M23 | 8402 LAKEWAY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.01 | 132.0056 | [18 empty] | 0
| 927 | 20 | B | SSMHT0001469 | SS.MH.T0001469 | 32.2588 | -95.3148 | M23 | 8402 LAKE WAY DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 9.8 | 129.368 | [18 empty] | 0
| 928 | 20 | C | SSMHT0001470 | SS.MH.T0001470 | 32.2591 | -95.3148 | M23 | 8402 LAKEWAY DR | Solid |  | No | Street | Unpaved | Below Grade | 12 | Std 48 Round | Concrete | 9.88 | 130.3728 | [18 empty] | 0
| 929 | 20 | C | SSMHT0002449 | SS.MH.T0002449 | 32.2602 | -95.3104 | M23 | 8106 CROOKED TRL | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.42 | 112.0352 | [18 empty] | 0
| 930 | 20 | B | SSMHT0002450 | SS.MH.T0002450 | 32.2598 | -95.3101 | M23 | 8105 CROOKED TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.04 | 157.5024 | [18 empty] | 0
| 931 | 20 | C | SSMHT0002451 | SS.MH.T0002451 | 32.2591 | -95.3104 | M23 | 8311 CROOKED TRL | Solid |  | No | Yard | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 24.34 | 311.9904 | [18 empty] | 0
| 932 | 20 | D | SSMHT0002452 | SS.MH.T0002452 | 32.2591 | -95.3102 | M23 | 8310 CROOKED TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 21.57 | 277.1992 | 2 | [11 empty] | 8315.976 | [5 empty] | 8315.976 | Rehabilitate
| 933 | 20 | X-CNO | SSMHT0002453 | SS.MH.T0002453 | 32.2591 | -95.3101 | M23 | 8310 CROOKED TRL | Solid |  |  | Yard | Unpaved | At Grade | [23 empty] | 0
| 934 | 20 | D | SSMHT0002454 | SS.MH.T0002454 | 32.2591 | -95.3096 | M23 | 8225 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 13.54 | 176.3424 | 2 | [11 empty] | 5290.272 | [5 empty] | 5290.272 | Rehabilitate
| 935 | 20 | C | SSMHT0002455 | SS.MH.T0002455 | 32.2586 | -95.3103 | M23 | 8404 CROOKED TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 22.64 | 290.6384 | [18 empty] | 0
| 936 | 20 | D | SSMHT0002456 | SS.MH.T0002456 | 32.2585 | -95.3097 | M23 | 8205 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 19.4 | 249.944 | 2 | [6 empty] | 650 |  | 1000 |  |  | 7498.32 |  | 280 |  |  |  | 9428.32 | Rehabilitate
| 937 | 20 | B | SSMHT0002457 | SS.MH.T0002457 | 32.2584 | -95.3097 | M23 | 8389 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 19.02 | 245.1712 | [18 empty] | 0
| 938 | 20 | B | SSMHT0002458 | SS.MH.T0002458 | 32.2584 | -95.3104 | M23 | 8407 CROOKED TRL | Solid |  | No | Yard | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 4.5 | 62.8 | [18 empty] | 0
| 939 | 20 | B | SSMHT0002459 | SS.MH.T0002459 | 32.2583 | -95.3103 | M23 | 8408 CROOKED TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.4 | 187.144 | [18 empty] | 0
| 940 | 20 | D | SSMHT0002460 | SS.MH.T0002460 | 32.2572 | -95.3094 | M23 | 8389 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 10.83 | 142.3048 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 941 | 20 | A | SSMHT0002461 | SS.MH.T0002461 | 32.257 | -95.3101 | M23 | 8505 CROOKED TRAIL | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.98 | 131.6288 | [18 empty] | 0
| 942 | 20 | A | SSMHT0002462 | SS.MH.T0002462 | 32.257 | -95.31 | M23 | 8502 CROOKED TRAIL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.64 | 127.3584 | [18 empty] | 0
| 943 | 20 | D | SSMHT0002463 | SS.MH.T0002463 | 32.2591 | -95.3118 | M23 | 8402 LAKEWAY DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 21 | Std 48 Round | Concrete | 13.67 | 177.9752 | 2 | [6 empty] | 650 |  |  |  |  | 5339.256 | [5 empty] | 5989.256 | Rehabilitate
| 944 | 20 | D | SSMHT0002467 | SS.MH.T0002467 | 32.2591 | -95.3132 | M23 | 8402 LAKEWAY DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 7.9 | 105.504 | 2 | [6 empty] | 650 |  |  |  |  | 3165.12 | [5 empty] | 3815.12 | Rehabilitate
| 945 | 20 | C | SSMHT0003870 | SS.MH.T0003870 | 32.268 | -95.302 | M22 | 400BLK HARVARD DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.22 | 184.8832 | [18 empty] | 0
| 946 | 20 | C | SSMHT0003871 | SS.MH.T0003871 | 32.2685 | -95.302 | M22 | 8238 BAYLOR DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 11.2 | 146.952 | [18 empty] | 0
| 947 | 20 | C | SSMHT0003872 | SS.MH.T0003872 | 32.2697 | -95.3022 | M22 | 8226 BAYLOR DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.44 | 74.6064 | [18 empty] | 0
| 948 | 20 | B | SSMHT0005448 | SS.MH.T0005448 | 32.2728 | -95.2898 | N22 | 1025 JEFFERY DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.1 | 120.576 | [18 empty] | 0
| 949 | 20 | B | SSMHT0005459 | SS.MH.T0005459 | 32.2765 | -95.2897 | N21 | 1105 ELAINE DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.36 | 61.0416 | [18 empty] | 0
| 950 | 20 | C | SSMHT0005500 | SS.MH.T0005500 | 32.2696 | -95.3002 | N22 | 8229 CLEMSON DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.07 | 82.5192 | [18 empty] | 0
| 951 | 20 | C | SSMHT0005501 | SS.MH.T0005501 | 32.2696 | -95.2995 | N22 | 513 OXFORD DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.56 | 88.6736 | [18 empty] | 0
| 952 | 20 | D | SSMHT0005502 | SS.MH.T0005502 | 32.2699 | -95.2994 | N22 | 600 OXFORD DR | Vented | 2 | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Brick | 6.7 | 90.432 | 2 | [11 empty] | 2712.96 | [5 empty] | 2712.96 | Rehabilitate
| 953 | 20 | B | SSMHT0005503 | SS.MH.T0005503 | 32.2691 | -95.2981 | N22 | 715 OXFORD DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6 | 81.64 | [18 empty] | 0
| 954 | 20 | D | SSMHT0005504 | SS.MH.T0005504 | 32.2687 | -95.2999 | N22 | 8237 CLEMSON DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.4 | 86.664 | 2 | [11 empty] | 2599.92 | [5 empty] | 2599.92 | Rehabilitate
| 955 | 20 | B | SSMHT0005505 | SS.MH.T0005505 | 32.2691 | -95.2971 | N22 | 8300 CAMBRIDGE RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 17.66 | 228.0896 | [18 empty] | 0
| 956 | 20 | C | SSMHT0005506 | SS.MH.T0005506 | 32.2691 | -95.2952 | N22 | 817 MCCLENNY DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.52 | 75.6112 | [18 empty] | 0
| 957 | 20 | B | SSMHT0005507 | SS.MH.T0005507 | 32.2685 | -95.2971 | N22 | NONE CAMBRIDGE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.04 | 170.0624 | [18 empty] | 0
| 958 | 20 | B | SSMHT0005508 | SS.MH.T0005508 | 32.2677 | -95.297 | N22 | 1917 CAMBRIDGE RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [18 empty] | 0
| 959 | 20 | B | SSMHT0005509 | SS.MH.T0005509 | 32.267 | -95.297 | N22 | 8420 CAMBRIDGE RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 36 | Concrete | 3.76 | 53.5056 | [18 empty] | 0
| 960 | 20 | C | SSMHT0005510 | SS.MH.T0005510 | 32.267 | -95.2976 | N22 | 700 HARVARD DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.04 | 94.7024 | [18 empty] | 0
| 961 | 20 | B | SSMHT0005511 | SS.MH.T0005511 | 32.2684 | -95.2976 | N22 | 8304 OXFORD DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.7 | 77.872 | [18 empty] | 0
| 962 | 20 | C | SSMHT0005512 | SS.MH.T0005512 | 32.2661 | -95.2984 | N22 | 707 PURDUE DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.08 | 107.7648 | [18 empty] | 0
| 963 | 20 | X-CNL | SSMHT0005513 | SS.MH.T0005513 |  |  | N22 | 609 PURDUE DR. |  |  |  | Yard | Unpaved | [24 empty] | 0
| 964 | 20 | B | SSMHT0005514 | SS.MH.T0005514 | 32.2671 | -95.2998 | N22 | 600 PURDUE DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.66 | 77.3696 | [18 empty] | 0
| 965 | 20 | C | SSMHT0005515 | SS.MH.T0005515 | 32.2675 | -95.2985 | N22 | 701 HARVARD DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.8 | 79.128 | [18 empty] | 0
| 966 | 20 | D | SSMHT0005516 | SS.MH.T0005516 | 32.268 | -95.2998 | N22 | 513 HARVARD DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 11.56 | 151.4736 | 2 | [11 empty] | 4544.208 | [5 empty] | 4544.208 | Rehabilitate
| 967 | 20 | C | SSMHT0005517 | SS.MH.T0005517 | 32.268 | -95.3008 | N22 | 500 HARVARD DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.62 | 114.5472 | [18 empty] | 0
| 968 | 20 | D | SSMHT0005519 | SS.MH.T0005519 | 32.2669 | -95.3011 | N22 | 520 PRINCETON DR | Solid |  | No | Creek | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.44 | 74.6064 |  |  |  |  | 500 |  |  | 650 | [10 empty] | 1150 | Repair
| 969 | 20 | B | SSMHT0005520 | SS.MH.T0005520 | 32.2664 | -95.3008 | N22 | 520 PRINCETON DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.99 | 68.9544 | [18 empty] | 0
| 970 | 20 | C | SSMHT0005521 | SS.MH.T0005521 | 32.2655 | -95.3011 | N22 | 505 PRINCETON DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.91 | 105.6296 | [18 empty] | 0
| 971 | 20 | B | SSMHT0005606 | SS.MH.T0005606 | 32.2677 | -95.296 | N22 | 1917 CAMBRIDGE RD. | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.9 | 80.384 | [18 empty] | 0
| 972 | 20 | D | SSMHT0005607 | SS.MH.T0005607 | 32.2677 | -95.2951 | N22 | 1917 CAMBRIDGE RD. | Solid |  | No | Road Shoulder | Paved - Asphalt | Above Grade | 5 | Std 48 Round | Concrete | 10.36 | 136.4016 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
| 973 | 20 | B | SSMHT0006180 | SS.MH.T0006180 | 32.2758 | -95.2897 | N21 | 6700 GREER DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.58 | 76.3648 | [18 empty] | 0
| 974 | 20 | B | SSMHT0006181 | SS.MH.T0006181 | 32.2754 | -95.2897 | N21 | 8146 GREER DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.38 | 124.0928 | [18 empty] | 0
| 975 | 20 | B | SSMHT0006182 | SS.MH.T0006182 | 32.2735 | -95.2897 | N21 | 8164 GREER DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.02 | 107.0112 | [18 empty] | 0
| 976 | 20 | C | SSMHT0006183 | SS.MH.T0006183 | 32.2646 | -95.3011 | N22 | NONE CAMBRIDGE RD | Vented | 2 | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 4.32 | 60.5392 | [18 empty] | 0
| 977 | 20 | C | SSMHT0006196 | SS.MH.T0006196 | 32.268 | -95.3018 | N22 | 400BLK HARVARD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.74 | 116.0544 | [18 empty] | 0
| 978 | 20 | C | SSMHT0006197 | SS.MH.T0006197 | 32.268 | -95.3008 | N22 | 500 HARVARD DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.28 | 122.8368 | [18 empty] | 0
| 979 | 20 | C | SSMHT0006198 | SS.MH.T0006198 | 32.268 | -95.3013 | N22 | NONE HARVARD DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.67 | 127.7352 | [18 empty] | 0
| 980 | 20 | C | SSMHT0006199 | SS.MH.T0006199 | 32.268 | -95.3019 | M22 | 400BLK HARVARD DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.74 | 166.2944 | [18 empty] | 0
| 981 | 20 | X-CNL | SSMHT0006269 | SS.MH.T0006269 |  |  | N22 | 8300 EL CERRITO PL. |  |  |  | Street | Paved - Asphalt |  |  | Std 48 Round | [21 empty] | 0
| 982 | 20 | D | SSMHT0006270 | SS.MH.T0006270 | 32.2691 | -95.2961 | N22 | 720 MCCLENNY DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.82 | 154.7392 | [15 empty] | 900 |  |  | 900 | Repair
| 983 | 20 | B | SSMHT0007035 | SS.MH.T0007035 | 32.2732 | -95.2672 | O21 | 5829 THOMPSON PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.94 | 156.2464 | [18 empty] | 0
| 984 | 20 | B | SSMHT0007036 | SS.MH.T0007036 | 32.273 | -95.2674 | O21 | 5833 THOMPSON PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.14 | 171.3184 | [18 empty] | 0
| 985 | 20 | C | SSMHT0007042 | SS.MH.T0007042 | 32.2717 | -95.2669 | O22 | 2539 GUINN FARM RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.57 | 176.7192 | [18 empty] | 0
| 986 | 20 | D | SSMHT0007045 | SS.MH.T0007045 | 32.2694 | -95.2634 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 16.96 | 219.2976 | 2 | [6 empty] | 650 |  |  |  |  | 6578.928 |  | 280 |  |  |  | 7508.928 | Rehabilitate
| 987 | 20 | C | SSMHT0007052 | SS.MH.T0007052 | 32.2715 | -95.2663 | O22 | 2548 GUINN FARMS RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 17 | 219.8 | [18 empty] | 0
| 988 | 20 | C | SSMHT0007053 | SS.MH.T0007053 | 32.2711 | -95.2665 | O22 | 6025 MORNING MIST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.02 | 182.3712 | [18 empty] | 0
| 989 | 20 | D | SSMHT0007054 | SS.MH.T0007054 | 32.2708 | -95.2667 | O22 | 6033 MORNING MIST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.03 | 157.3768 | 2 | [11 empty] | 4721.304 | [5 empty] | 4721.304 | Rehabilitate
| 990 | 20 | D | SSMHT0007055 | SS.MH.T0007055 | 32.2704 | -95.2668 | O22 | 6041 MORNING MIST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.04 | 144.9424 | 2 | [11 empty] | 4348.272 | [5 empty] | 4348.272 | Rehabilitate
| 991 | 20 | B | SSMHT0007056 | SS.MH.T0007056 | 32.27 | -95.2668 | O22 | 6049 MORNING MIST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.74 | 128.6144 | [18 empty] | 0
| 992 | 20 | B | SSMHT0007057 | SS.MH.T0007057 | 32.2698 | -95.2668 | O22 | 6053 MORNING MIST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.43 | 112.1608 | [18 empty] | 0
| 993 | 20 | B | SSMHT0007058 | SS.MH.T0007058 | 32.2709 | -95.2671 | O22 | 2523 MEADOWGLEN CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.45 | 137.532 | [18 empty] | 0
| 994 | 20 | B | SSMHT0007059 | SS.MH.T0007059 | 32.2703 | -95.2679 | O22 | 2548 MEADOWLAND CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.48 | 100.2288 | [18 empty] | 0
| 995 | 20 | B | SSMHT0007060 | SS.MH.T0007060 | 32.2699 | -95.2681 | O22 | 2533 MEADOWLAND CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.96 | 106.2576 | [18 empty] | 0
| 996 | 20 | B | SSMHT0007063 | SS.MH.T0007063 | 32.2718 | -95.2692 | O22 | 5930 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.77 | 103.8712 | [18 empty] | 0
| 997 | 20 | C | SSMHT0007082 | SS.MH.T0007082 | 32.2727 | -95.2681 | O22 | 5834 THOMPSON PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.29 | 148.0824 | [18 empty] | 0
| 998 | 20 | B | SSMHT0007083 | SS.MH.T0007083 | 32.2726 | -95.2686 | O22 | 5845 THOMPSON PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.52 | 138.4112 | [18 empty] | 0
| 999 | 20 | C | SSMHT0007084 | SS.MH.T0007084 | 32.2725 | -95.2692 | O22 | 5859 THOMPSON PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.7 | 102.992 | [18 empty] | 0
| 1000 | 20 | B | SSMHT0007085 | SS.MH.T0007085 | 32.2702 | -95.2693 | O22 | 6043 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.2 | 109.272 | [18 empty] | 0
| 1001 | 20 | B | SSMHT0007086 | SS.MH.T0007086 | 32.2703 | -95.2692 | O22 | 6039 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.49 | 112.9144 | [18 empty] | 0
| 1002 | 20 | B | SSMHT0007087 | SS.MH.T0007087 | 32.2714 | -95.2692 | O22 | 6016 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.18 | 121.5808 | [18 empty] | 0
| 1003 | 20 | B | SSMHT0007088 | SS.MH.T0007088 | 32.2732 | -95.2692 | O21 | 5875 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.07 | 95.0792 | [18 empty] | 0
| 1004 | 20 | C | SSMHT0007089 | SS.MH.T0007089 | 32.2733 | -95.2692 | O21 | 5875 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0
| 1005 | 20 | C | SSMHT0007090 | SS.MH.T0007090 | 32.2734 | -95.2688 | O21 | 5856 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.88 | 92.6928 | [18 empty] | 0
| 1006 | 20 | B | SSMHT0007091 | SS.MH.T0007091 | 32.2715 | -95.269 | O22 | 6015 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.37 | 111.4072 | [18 empty] | 0
| 1007 | 20 | C | SSMHT0007092 | SS.MH.T0007092 | 32.272 | -95.2674 | O22 | 2523 GUINN FARMS RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.71 | 140.7976 | [18 empty] | 0
| 1008 | 20 | X-CNL | SSMHT0007101 | SS.MH.T0007101 |  |  | N24 | 1236 CENTENNIAL PKWY |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1009 | 20 | A | SSMHT0007257 | SS.MH.T0007257 | 32.2755 | -95.27 | O21 | 2448 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.26 | 172.8256 | [18 empty] | 0
| 1010 | 20 | A | SSMHT0007258 | SS.MH.T0007258 | 32.2748 | -95.27 | O21 | 2448 ROY RD | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.96 | 181.6176 | [18 empty] | 0
| 1011 | 20 | C | SSMHT0007287 | SS.MH.T0007287 | 32.245 | -95.2854 | N24 | NONE CONVENTRY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.22 | 197.4432 | [18 empty] | 0
| 1012 | 20 | C | SSMHT0007361 | SS.MH.T0007361 | 32.2604 | -95.2993 | N23 | 8620 RADCLIFFE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.6 | 139.416 | [18 empty] | 0
| 1013 | 20 | C | SSMHT0007362 | SS.MH.T0007362 | 32.2605 | -95.2995 | N23 | 8620 RACLIFFE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.42 | 137.1552 | [18 empty] | 0
| 1014 | 20 | C | SSMHT0007363 | SS.MH.T0007363 | 32.2605 | -95.2984 | N23 | 8643 RADCLIFFE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.04 | 107.2624 | [18 empty] | 0
| 1015 | 20 | B | SSMHT0007364 | SS.MH.T0007364 | 32.2604 | -95.2977 | N23 | 8705 RADCLIFFE DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 7.34 | 98.4704 | [18 empty] | 0
| 1016 | 20 | B | SSMHT0007365 | SS.MH.T0007365 | 32.2607 | -95.2996 | N23 | 8612 RADCLIFFE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0
| 1017 | 20 | C | SSMHT0007366 | SS.MH.T0007366 | 32.2627 | -95.3001 | N22 | 8515 RADCLIFFE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.69 | 102.8664 | [18 empty] | 0
| 1018 | 20 | B | SSMHT0007367 | SS.MH.T0007367 | 32.2646 | -95.3005 | N22 | 311 CAMBRIDGE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.08 | 145.4448 | [18 empty] | 0
| 1019 | 20 | C | SSMHT0007368 | SS.MH.T0007368 | 32.2646 | -95.2993 | N22 | 1034 CAMBRIDGE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.18 | 159.2608 | [18 empty] | 0
| 1020 | 20 | C | SSMHT0007369 | SS.MH.T0007369 | 32.2628 | -95.299 | N22 | 8515 AUBURN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.89 | 80.2584 | [18 empty] | 0
| 1021 | 20 | B | SSMHT0007370 | SS.MH.T0007370 | 32.2627 | -95.2989 | N22 | 8515 AUBURN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.49 | 87.7944 | [18 empty] | 0
| 1022 | 20 | C | SSMHT0007371 | SS.MH.T0007371 | 32.2615 | -95.2986 | N23 | 8527 AUBURN DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.74 | 103.4944 | [18 empty] | 0
| 1023 | 20 | D | SSMHT0007372 | SS.MH.T0007372 | 32.2586 | -95.3077 | M23 | 8288 S BROADWAY AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 9.44 | 124.8464 | [7 empty] | 650 |  |  | 725 |  |  |  |  | 900 |  |  | 2275 | Repair | 6867 changed to 13058
| 1024 | 20 | C | SSMHT0007373 | SS.MH.T0007373 | 32.2586 | -95.3063 | M23 | 8310 S BROADWAY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.54 | 163.7824 | [18 empty] | 0
| 1025 | 20 | B | SSMHT0007374 | SS.MH.T0007374 | 32.2588 | -95.3077 | M23 | 8288 S BROADWAY AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 10.02 | 132.1312 | [18 empty] | 0
| 1026 | 20 | B | SSMHT0007375 | SS.MH.T0007375 | 32.2619 | -95.3038 | M23 | 8421 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.4 | 86.664 | [18 empty] | 0
| 1027 | 20 | B | SSMHT0007376 | SS.MH.T0007376 | 32.2621 | -95.304 | M23 | 8421 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 6.28 | 85.1568 | [18 empty] | 0
| 1028 | 20 | B | SSMHT0007377 | SS.MH.T0007377 | 32.2619 | -95.3033 | M23 | 8425 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 7.38 | 98.9728 | [18 empty] | 0
| 1029 | 20 | B | SSMHT0007378 | SS.MH.T0007378 | 32.2619 | -95.302 | M23 | 8444 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.86 | 92.4416 | [18 empty] | 0
| 1030 | 20 | C | SSMHT0007379 | SS.MH.T0007379 | 32.262 | -95.3016 | N23 | 8450 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.99 | 131.7544 | [18 empty] | 0
| 1031 | 20 | D | SSMHT0007380 | SS.MH.T0007380 | 32.2623 | -95.3015 | N23 | 8450 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.3 | 173.328 | 2 | [11 empty] | 5199.84 | [5 empty] | 5199.84 | Rehabilitate
| 1032 | 20 | B | SSMHT0007381 | SS.MH.T0007381 | 32.2646 | -95.3021 | M22 | 414 CAMBRIDGE RD | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.18 | 121.5808 | [18 empty] | 0
| 1033 | 20 | C | SSMHT0007382 | SS.MH.T0007382 | 32.2627 | -95.2973 | N22 | 8470 WILKEN PLAZA | Solid |  | No | Yard | Unpaved | Above Grade | 37 | Std 48 Round | Concrete | 9.94 | 131.1264 | [18 empty] | 0
| 1034 | 20 | C | SSMHT0007383 | SS.MH.T0007383 | 32.2646 | -95.2974 | N22 | 8424 CAMBRIDGE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.96 | 131.3776 | [18 empty] | 0
| 1035 | 20 | B | SSMHT0007384 | SS.MH.T0007384 | 32.2646 | -95.2971 | N22 | 8424 AMBRIDGE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.48 | 150.4688 | [18 empty] | 0
| 1036 | 20 | X-CNL | SSMHT0007385 | SS.MH.T0007385 |  |  | N22 | 718 CAMBRIDGE RD |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1037 | 20 | B | SSMHT0007386 | SS.MH.T0007386 | 32.2646 | -95.2987 | N22 | 718 CAMBRIDGE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.56 | 164.0336 | [18 empty] | 0
| 1038 | 20 | B | SSMHT0007387 | SS.MH.T0007387 | 32.2642 | -95.2983 | N22 | 719 CAMBRIDGE RD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 4 | Std 48 Round | Concrete | 13.16 | 171.5696 | [18 empty] | 0
| 1039 | 20 | B | SSMHT0007388 | SS.MH.T0007388 | 32.2636 | -95.2979 | N22 | 8470 WILKEN PLAZA | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 9.96 | 131.3776 | [18 empty] | 0
| 1040 | 20 | C | SSMHT0007389 | SS.MH.T0007389 | 32.2622 | -95.2964 | N23 | 8429 CASTLETON WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 27 | Std 48 Round | Concrete | 9.43 | 124.7208 | [18 empty] | 0
| 1041 | 20 | D | SSMHT0007390 | SS.MH.T0007390 | 32.262 | -95.2955 | N23 | 8429 CASTLETON WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 8.34 | 111.0304 | 2 | [6 empty] | 650 |  |  |  |  | 3330.912 | [5 empty] | 3980.912 | Rehabilitate
| 1042 | 20 | C | SSMHT0007391 | SS.MH.T0007391 | 32.2606 | -95.2952 | N23 | 6523 ROCHESTER WAY | Solid |  | No | Yard | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 9.89 | 130.4984 | [18 empty] | 0
| 1043 | 20 | B | SSMHT0007392 | SS.MH.T0007392 | 32.26 | -95.2947 | N23 | 816 WILDER WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 9.98 | 131.6288 | [18 empty] | 0
| 1044 | 20 | C | SSMHT0007393 | SS.MH.T0007393 | 32.2604 | -95.2938 | N23 | 6526 ROCHESTER WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 11 | 144.44 | [18 empty] | 0
| 1045 | 20 | C | SSMHT0007394 | SS.MH.T0007394 | 32.2608 | -95.2938 | N23 | 6526 ROCHESTER WAY | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 6.41 | 86.7896 | [18 empty] | 0
| 1046 | 20 | B | SSMHT0007395 | SS.MH.T0007395 | 32.2614 | -95.2928 | N23 | 1008 WILDER WOODS | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 14.7 | 190.912 | [18 empty] | 0
| 1047 | 20 | B | SSMHT0007396 | SS.MH.T0007396 | 32.2588 | -95.2945 | N23 | 1015 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 9.56 | 126.3536 | [18 empty] | 0
| 1048 | 20 | D | SSMHT0007403 | SS.MH.T0007403 | 32.26 | -95.295 | N23 | 816 WILDER WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 8.38 | 111.5328 | 2 | [6 empty] | 650 |  |  |  |  | 3345.984 | [5 empty] | 3995.984 | Rehabilitate
| 1049 | 20 | C | SSMHT0007409 | SS.MH.T0007409 | 32.2561 | -95.2958 | N23 | 816 CUMBERLAND RD | Solid |  | No | Driveway | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.26 | 122.5856 | [18 empty] | 0
| 1050 | 20 | B | SSMHT0007410 | SS.MH.T0007410 | 32.2562 | -95.2973 | N23 | 732 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.48 | 137.9088 | [18 empty] | 0
| 1051 | 20 | B | SSMHT0007411 | SS.MH.T0007411 | 32.2562 | -95.2988 | N23 | 610 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 17.58 | 227.0848 | [18 empty] | 0
| 1052 | 20 | B | SSMHT0007412 | SS.MH.T0007412 | 32.2562 | -95.3001 | N23 | 606 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 18.54 | 239.1424 | [18 empty] | 0
| 1053 | 20 | B | SSMHT0007413 | SS.MH.T0007413 | 32.2562 | -95.3014 | N23 | 514 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 17.7 | 228.592 | [18 empty] | 0
| 1054 | 20 | X-CNL | SSMHT0007414 | SS.MH.T0007414 |  |  | N23 | 422 CUMBERLAND RD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1055 | 20 | B | SSMHT0007415 | SS.MH.T0007415 | 32.2566 | -95.3038 | M23 | 501 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 17.8 | 229.848 | [18 empty] | 0
| 1056 | 20 | C | SSMHT0007421 | SS.MH.T0007421 | 32.2563 | -95.3187 | M23 | 574 W CUMBERLAND RD | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Sealed Concrete | 13.94 | 181.3664 | [18 empty] | 0
| 1057 | 20 | C | SSMHT0007422 | SS.MH.T0007422 | 32.2589 | -95.295 | N23 | 901 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 9.49 | 125.4744 | [18 empty] | 0
| 1058 | 20 | B | SSMHT0007423 | SS.MH.T0007423 | 32.259 | -95.2957 | N23 | 901 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 11.46 | 150.2176 | [18 empty] | 0
| 1059 | 20 | B | SSMHT0007424 | SS.MH.T0007424 | 32.259 | -95.2973 | N23 | 775 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 6.28 | 85.1568 | [18 empty] | 0
| 1060 | 20 | B | SSMHT0007425 | SS.MH.T0007425 | 32.259 | -95.297 | N23 | 775 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.58 | 88.9248 | [18 empty] | 0
| 1061 | 20 | B | SSMHT0007426 | SS.MH.T0007426 | 32.2579 | -95.291 | N23 | 1217 WILDER WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.48 | 112.7888 | [18 empty] | 0
| 1062 | 20 | C | SSMHT0007427 | SS.MH.T0007427 | 32.258 | -95.2912 | N23 | 1217 WILDER WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.88 | 105.2528 | [18 empty] | 0
| 1063 | 20 | C | SSMHT0007429 | SS.MH.T0007429 | 32.2585 | -95.2935 | N23 | 1021 WILDER WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.66 | 102.4896 | [18 empty] | 0
| 1064 | 20 | C | SSMHT0007430 | SS.MH.T0007430 | 32.259 | -95.2999 | N23 | 533 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | [18 empty] | 0
| 1065 | 20 | D | SSMHT0007431 | SS.MH.T0007431 | 32.259 | -95.2986 | N23 | 683 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | 2 | [11 empty] | 3240.48 | [5 empty] | 3240.48 | Rehabilitate
| 1066 | 20 | C | SSMHT0007432 | SS.MH.T0007432 | 32.2589 | -95.3024 | M23 | 418 WIDER WAY | Solid |  | No | Street | Unpaved | At Grade |  | Std 48 Round | Concrete | 12.7 | 165.792 | [18 empty] | 0
| 1067 | 20 | C | SSMHT0007433 | SS.MH.T0007433 | 32.2589 | -95.3012 | N23 | 507 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 8.78 | 116.5568 | [18 empty] | 0
| 1068 | 20 | D | SSMHT0007434 | SS.MH.T0007434 | 32.2597 | -95.3076 | M23 | 7934 S BROADWAY AVE | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.4 | 124.344 | 2 | [6 empty] | 650 |  |  |  |  | 3730.32 | [5 empty] | 4380.32 | Rehabilitate
| 1069 | 20 | B | SSMHT0007435 | SS.MH.T0007435 | 32.2593 | -95.2973 | N23 | 8643 RADCLIFFE DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 6.4 | 86.664 | [18 empty] | 0
| 1070 | 20 | D | SSMHT0007436 | SS.MH.T0007436 | 32.2595 | -95.2973 | N23 | 8643 RADCLIFFE DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 9.34 | 123.5904 | 2 | [11 empty] | 3707.712 | [5 empty] | 3707.712 | Rehabilitate
| 1071 | 20 | C | SSMHT0007437 | SS.MH.T0007437 | 32.26 | -95.2973 | N23 | 8643 RADCLIFFE DR | Solid |  | No | Trees/Woods | Paved - Concrete | Above Grade | 15 | Std 48 Round | Concrete | 8.24 | 109.7744 | [18 empty] | 0
| 1072 | 20 | A | SSMHT0007438 | SS.MH.T0007438 | 32.2605 | -95.2972 | O18 | 8705 RADCLIFFE DR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.54 | 75.8624 | [18 empty] | 0
| 1073 | 20 | A | SSMHT0007439 | SS.MH.T0007439 | 32.2604 | -95.295 | N23 | 6527 ROCHESTER WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 7.96 | 106.2576 | [18 empty] | 0
| 1074 | 20 | X-Buried | SSMHT0007440 | SS.MH.T0007440 | 32.2649 | -95.2969 | N22 | 8424 CAMBRIDGE RD |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1075 | 20 | C | SSMHT0007441 | SS.MH.T0007441 | 32.2634 | -95.3018 | N22 | 8464 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.92 | 143.4352 | [18 empty] | 0
| 1076 | 20 | C | SSMHT0007448 | SS.MH.T0007448 | 32.2594 | -95.2897 | N23 | 1217 WILDER WAY | Bolted | 4 | No | Trees/Woods | Unpaved | Above Grade | 16 | Std 48 Round | Concrete | 7.32 | 98.2192 | [18 empty] | 0
| 1077 | 20 | B | SSMHT0007561 | SS.MH.T0007561 | 32.2716 | -95.2652 | O22 | 7283 ROLLING ACRES PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.77 | 103.8712 | [18 empty] | 0
| 1078 | 20 | B | SSMHT0007562 | SS.MH.T0007562 | 32.2714 | -95.2659 | O22 | 2552 GUINN FARMS RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.33 | 110.9048 | [18 empty] | 0
| 1079 | 20 | B | SSMHT0007563 | SS.MH.T0007563 | 32.2712 | -95.2655 | O22 | 7304 ROLLING ACRES PLACE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.48 | 125.3488 | [18 empty] | 0
| 1080 | 20 | C | SSMHT0007564 | SS.MH.T0007564 | 32.2708 | -95.2657 | O22 | 7316 ROLLING ACRES PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0
| 1081 | 20 | B | SSMHT0007565 | SS.MH.T0007565 | 32.2705 | -95.2658 | O22 | 7328 ROLLING ACRESS PLACE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.72 | 115.8032 | [18 empty] | 0
| 1082 | 20 | C | SSMHT0007566 | SS.MH.T0007566 | 32.2701 | -95.2658 | O22 | 7340 ROLLING ACRES PLACE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.3 | 110.528 | [18 empty] | 0
| 1083 | 20 | B | SSMHT0007567 | SS.MH.T0007567 | 32.2698 | -95.2658 | O22 | 7352 ROLLING ACRES PLACE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.75 | 103.62 | [18 empty] | 0
| 1084 | 20 | C | SSMHT0007568 | SS.MH.T0007568 | 32.2698 | -95.2649 | O22 | 7340 HARVEST HILL DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.15 | 108.644 | [18 empty] | 0
| 1085 | 20 | B | SSMHT0007569 | SS.MH.T0007569 | 32.2702 | -95.2649 | O22 | 7316 HARVEST HILL DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.36 | 111.2816 | [18 empty] | 0
| 1086 | 20 | B | SSMHT0007570 | SS.MH.T0007570 | 32.2705 | -95.2648 | O22 | 7311 HARVEST HILL DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.59 | 114.1704 | [18 empty] | 0
| 1087 | 20 | B | SSMHT0007571 | SS.MH.T0007571 | 32.2708 | -95.2647 | O22 | 7305 HARVEST HILL DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.79 | 104.1224 | [18 empty] | 0
| 1088 | 20 | C | SSMHT0007572 | SS.MH.T0007572 | 32.2728 | -95.2664 | O21 | 7234 MORNING MIST DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.46 | 125.0976 | [18 empty] | 0
| 1089 | 20 | B | SSMHT0007573 | SS.MH.T0007573 | 32.2728 | -95.2665 | O21 | 7234 MORNING MIST DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.1 | 120.576 | [18 empty] | 0
| 1090 | 20 | B | SSMHT0007574 | SS.MH.T0007574 | 32.2723 | -95.267 | O22 | 7210 MORNING MIST CT | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.05 | 132.508 | [18 empty] | 0
| 1091 | 20 | B | SSMHT0007575 | SS.MH.T0007575 | 32.2726 | -95.2667 | O22 | 7312 MORNING MIST | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.34 | 111.0304 | [18 empty] | 0
| 1092 | 20 | B | SSMHT0007576 | SS.MH.T0007576 | 32.2724 | -95.2664 | O22 | 7300 MORNING MIST CT | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.83 | 104.6248 | [18 empty] | 0
| 1093 | 20 | B | SSMHT0007577 | SS.MH.T0007577 | 32.2723 | -95.266 | O22 | 7276 MORNING MIST CT | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.12 | 108.2672 | [18 empty] | 0
| 1094 | 20 | D | SSMHT0007621 | SS.MH.T0007621 | 32.2543 | -95.2911 | N23 | 1111 CUMBERLNAD RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 7.24 | 97.2144 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 1095 | 20 | B | SSMHT0007682 | SS.MH.T0007682 | 32.2541 | -95.2913 | N23 | 1111 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 8.32 | 110.7792 | [18 empty] | 0
| 1096 | 20 | C | SSMHT0007683 | SS.MH.T0007683 | 32.2537 | -95.2927 | N23 | 9116 CHEROKEE TRL | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.46 | 87.4176 | [18 empty] | 0
| 1097 | 20 | D | SSMHT0007684 | SS.MH.T0007684 | 32.2535 | -95.2929 | N23 | 9116 CHEROKEE TRL | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 6.94 | 93.4464 | 2 | [6 empty] | 650 |  |  |  |  | 2803.392 | [5 empty] | 3453.392 | Rehabilitate
| 1098 | 20 | D | SSMHT0007713 | SS.MH.T0007713 | 32.2405 | -95.2984 | N24 | 602 WINDING BROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.91 | 118.1896 | 2 | [11 empty] | 3545.688 | [5 empty] | 3545.688 | Rehabilitate
| 1099 | 20 | C | SSMHT0007714 | SS.MH.T0007714 | 32.2407 | -95.2987 | N24 | 506 SKIPPING STONE LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.59 | 101.6104 | [18 empty] | 0
| 1100 | 20 | B | SSMHT0007715 | SS.MH.T0007715 | 32.2407 | -95.299 | N24 | 513 SKIPPING STONE LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.08 | 95.2048 | [18 empty] | 0
| 1101 | 20 | B | SSMHT0007716 | SS.MH.T0007716 | 32.2406 | -95.2992 | N24 | 513 SKIPPING STONE LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.29 | 97.8424 | [18 empty] | 0
| 1102 | 20 | D | SSMHT0007717 | SS.MH.T0007717 | 32.2407 | -95.2982 | N24 | 605 WINDING BROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.08 | 120.3248 | 2 | [11 empty] | 3609.744 | [5 empty] | 3609.744 | Rehabilitate
| 1103 | 20 | C | SSMHT0007718 | SS.MH.T0007718 | 32.2407 | -95.2978 | N24 | 610 WINDING BROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.91 | 118.1896 | [18 empty] | 0
| 1104 | 20 | B | SSMHT0007719 | SS.MH.T0007719 | 32.2406 | -95.2973 | N24 | 618 WINDING BROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.68 | 115.3008 | [18 empty] | 0
| 1105 | 20 | B | SSMHT0007720 | SS.MH.T0007720 | 32.2407 | -95.2967 | N24 | 637 WINDING BROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.09 | 120.4504 | [18 empty] | 0
| 1106 | 20 | B | SSMHT0007721 | SS.MH.T0007721 | 32.2491 | -95.2931 | N24 | 9415 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.44 | 149.9664 | [18 empty] | 0
| 1107 | 20 | B | SSMHT0007722 | SS.MH.T0007722 | 32.248 | -95.2931 | N24 | 9433 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.45 | 175.212 | [18 empty] | 0
| 1108 | 20 | B | SSMHT0007723 | SS.MH.T0007723 | 32.2472 | -95.2931 | N24 | 9437 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.03 | 94.5768 | [18 empty] | 0
| 1109 | 20 | B | SSMHT0007724 | SS.MH.T0007724 | 32.2467 | -95.2931 | N24 | 1202 DREAM CATCHER | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.37 | 86.2872 | [18 empty] | 0
| 1110 | 20 | B | SSMHT0007725 | SS.MH.T0007725 | 32.2502 | -95.2931 | N24 | 9311 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.92 | 181.1152 | [18 empty] | 0
| 1111 | 20 | B | SSMHT0007726 | SS.MH.T0007726 | 32.2513 | -95.2932 | N24 | 9205 CHEROKEE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.27 | 135.2712 | [18 empty] | 0
| 1112 | 20 | B | SSMHT0007729 | SS.MH.T0007729 | 32.2387 | -95.2976 | N25 | 9226 STONEBANK CROSSING | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.74 | 103.4944 | [18 empty] | 0
| 1113 | 20 | B | SSMHT0007730 | SS.MH.T0007730 | 32.239 | -95.2977 | N25 | 9222 STONEBROOK CROSSING | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.7 | 102.992 | [18 empty] | 0
| 1114 | 20 | B | SSMHT0007731 | SS.MH.T0007731 | 32.2392 | -95.2978 | N25 | 9214 STONE BANK CROSSING | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.86 | 117.5616 | [18 empty] | 0
| 1115 | 20 | B | SSMHT0007732 | SS.MH.T0007732 | 32.2392 | -95.2988 | N25 | 9195 TEAL FLIGHT WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1116 | 20 | B | SSMHT0007733 | SS.MH.T0007733 | 32.2392 | -95.2991 | N25 | 9189 TEAL FLIGHT WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.37 | 123.9672 | [18 empty] | 0
| 1117 | 20 | B | SSMHT0007734 | SS.MH.T0007734 | 32.2392 | -95.2998 | N25 | 9174 TEAL FLIGHT WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.74 | 103.4944 | [18 empty] | 0
| 1118 | 20 | C | SSMHT0007735 | SS.MH.T0007735 | 32.2549 | -95.2908 | N23 | 1111 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.96 | 118.8176 | [18 empty] | 0
| 1119 | 20 | D | SSMHT0007736 | SS.MH.T0007736 | 32.2546 | -95.2897 | N23 | 1223 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.22 | 84.4032 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
| 1120 | 20 | B | SSMHT0007737 | SS.MH.T0007737 | 32.2542 | -95.2885 | N23 | 1315 CUMBERLAND RD | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 6.4 | 86.664 | [18 empty] | 0
| 1121 | 20 | B | SSMHT0007738 | SS.MH.T0007738 | 32.2551 | -95.2909 | N23 | 1111 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 10.22 | 134.6432 | [18 empty] | 0
| 1122 | 20 | C | SSMHT0007739 | SS.MH.T0007739 | 32.2538 | -95.2873 | N23 | 1401 CUMBERLAND RD | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 6.04 | 82.1424 | [18 empty] | 0
| 1123 | 20 | X-Buried | SSMHT0007864 | SS.MH.T0007864 | 32.2588 | -95.3188 | M23 | 1301 W CUMBERLAND RD |  |  |  | Yard | Unpaved | Below Grade | 14 | [22 empty] | 0
| 1124 | 20 | B | SSMHT0008035 | SS.MH.T0008035 | 32.2774 | -95.2782 | O21 | 1913 DEERBROOK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.52 | 100.7312 | [18 empty] | 0
| 1125 | 20 | A | SSMHT0008036 | SS.MH.T0008036 | 32.2774 | -95.2771 | O21 | 1937 DEERBROOK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.36 | 111.2816 | [18 empty] | 0
| 1126 | 20 | B | SSMHT0008047 | SS.MH.T0008047 | 32.2781 | -95.2789 | O21 | NONE GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.34 | 161.2704 | [18 empty] | 0
| 1127 | 20 | B | SSMHT0008048 | SS.MH.T0008048 | 32.2781 | -95.2779 | O21 | NONE GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.72 | 166.0432 | [18 empty] | 0
| 1128 | 20 | C | SSMHT0008049 | SS.MH.T0008049 | 32.2782 | -95.2769 | O21 | NONE GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 19.89 | 256.0984 | [18 empty] | 0
| 1129 | 20 | A | SSMHT0008050 | SS.MH.T0008050 | 32.2784 | -95.2757 | O21 | NONE E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.31 | 98.0936 | [18 empty] | 0
| 1130 | 20 | B | SSMHT0008051 | SS.MH.T0008051 | 32.2774 | -95.2762 | O21 | 2037 DEERBROOK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.06 | 94.9536 | [18 empty] | 0
| 1131 | 20 | B | SSMHT0008052 | SS.MH.T0008052 | 32.2774 | -95.2744 | O21 | 2159 DEERBROOK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [18 empty] | 0
| 1132 | 20 | B | SSMHT0008053 | SS.MH.T0008053 | 32.2774 | -95.2735 | O21 | 2233 DEERBROOK DR | Solid |  | No | Driveway | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.24 | 84.6544 | [18 empty] | 0
| 1133 | 20 | B | SSMHT0008054 | SS.MH.T0008054 | 32.277 | -95.2735 | O21 | 2233 DEERBROOK DR | Solid |  | No | Alley | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.36 | 98.7216 | [18 empty] | 0
| 1134 | 20 | B | SSMHT0008055 | SS.MH.T0008055 | 32.2768 | -95.2735 | O21 | 2233 DEERBROOK DR | Solid |  | No | Driveway | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.28 | 135.3968 | [18 empty] | 0
| 1135 | 20 | D | SSMHT0008056 | SS.MH.T0008056 | 32.2782 | -95.2838 | N21 | 1502 E GRANDE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.07 | 120.1992 | 2 | [11 empty] | 3605.976 | [5 empty] | 3605.976 | Rehabilitate
| 1136 | 20 | C | SSMHT0008057 | SS.MH.T0008057 | 32.2781 | -95.2843 | N21 | 1502 E GRANDE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.78 | 179.3568 | [18 empty] | 0
| 1137 | 20 | B | SSMHT0008058 | SS.MH.T0008058 | 32.2781 | -95.2852 | N21 | 1343 E GRANDE BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.98 | 156.7488 | [18 empty] | 0
| 1138 | 20 | C | SSMHT0008059 | SS.MH.T0008059 | 32.2782 | -95.2863 | N21 | 1343 E GRANDE BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.8 | 167.048 | [18 empty] | 0
| 1139 | 20 | B | SSMHT0008060 | SS.MH.T0008060 | 32.2783 | -95.2873 | N21 | 1136 E GRANDE BLVD | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.86 | 180.3616 | [18 empty] | 0
| 1140 | 20 | B | SSMHT0008061 | SS.MH.T0008061 | 32.2781 | -95.2873 | N21 | 1136 E GRANDE BLVD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 21.04 | 270.5424 | [18 empty] | 0
| 1141 | 20 | B | SSMHT0008062 | SS.MH.T0008062 | 32.2778 | -95.2804 | O21 | 6435 PALUXY DR | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 7.66 | 102.4896 | [18 empty] | 0
| 1142 | 20 | B | SSMHT0008063 | SS.MH.T0008063 | 32.2773 | -95.2797 | O21 | 6435 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 7.22 | 96.9632 | [18 empty] | 0
| 1143 | 20 | C | SSMHT0008064 | SS.MH.T0008064 | 32.2771 | -95.2798 | O21 | 6435 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 11.14 | 146.1984 | [18 empty] | 0
| 1144 | 20 | B | SSMHT0008065 | SS.MH.T0008065 | 32.2768 | -95.2797 | O21 | 6435 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.88 | 117.8128 | [18 empty] | 0
| 1145 | 20 | B | SSMHT0008066 | SS.MH.T0008066 | 32.2762 | -95.2797 | O21 | 1838 SUSAN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.92 | 93.1952 | [18 empty] | 0
| 1146 | 20 | B | SSMHT0008067 | SS.MH.T0008067 | 32.2762 | -95.2802 | O21 | 1824 SUSAN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.28 | 97.7168 | [18 empty] | 0
| 1147 | 20 | C | SSMHT0008068 | SS.MH.T0008068 | 32.2762 | -95.2815 | O21 | 1731 SUSAN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.58 | 101.4848 | [18 empty] | 0
| 1148 | 20 | A | SSMHT0008069 | SS.MH.T0008069 | 32.2762 | -95.2827 | N21 | 1710 SUSAN DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.7 | 115.552 | [18 empty] | 0
| 1149 | 20 | A | SSMHT0008070 | SS.MH.T0008070 | 32.2772 | -95.2838 | N21 | 6425 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0
| 1150 | 20 | D | SSMHT0008071 | SS.MH.T0008071 | 32.2767 | -95.2827 | N21 | 1525 E GRANDE BLVD | Solid |  | No | Parking Lot | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 9.56 | 126.3536 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
| 1151 | 20 | D | SSMHT0008072 | SS.MH.T0008072 | 32.2771 | -95.2873 | N21 | 1343 E GRANDE BLVD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 13.36 | 174.0816 | 2 | [11 empty] | 5222.448 |  | 280 |  |  |  | 5502.448 | Rehabilitate
| 1152 | 20 | C | SSMHT0008073 | SS.MH.T0008073 | 32.276 | -95.2873 | N21 | 1343 E GRANDE BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 12.9 | 168.304 | [18 empty] | 0
| 1153 | 20 | C | SSMHT0008075 | SS.MH.T0008075 | 32.2749 | -95.2873 | N21 | 1343 E GRANDE BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 12.4 | 162.024 | [18 empty] | 0
| 1154 | 20 | B | SSMHT0008100 | SS.MH.T0008100 | 32.2751 | -95.261 | P21 | 2924 ROY RD | Solid |  | No | Driveway | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 13.76 | 179.1056 | [18 empty] | 0
| 1155 | 20 | C | SSMHT0008101 | SS.MH.T0008101 | 32.275 | -95.261 | P21 | 2924 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 13.46 | 175.3376 | [18 empty] | 0
| 1156 | 20 | C | SSMHT0008102 | SS.MH.T0008102 | 32.2749 | -95.2609 | P21 | 2924 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 11.28 | 147.9568 | [18 empty] | 0
| 1157 | 20 | C | SSMHT0008103 | SS.MH.T0008103 | 32.2741 | -95.2606 | P21 | 14152 FM2964 | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 9 | Std 48 Round | Concrete | 7.32 | 98.2192 | [18 empty] | 0
| 1158 | 20 | C | SSMHT0008104 | SS.MH.T0008104 | 32.273 | -95.2602 | P21 | 14228 FM 2964 | Solid |  | No | Yard | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 6.46 | 87.4176 | [18 empty] | 0
| 1159 | 20 | C | SSMHT0008105 | SS.MH.T0008105 | 32.272 | -95.2598 | P22 | 14228 FM2964 | Solid |  | No | Yard | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 5.48 | 75.1088 | [18 empty] | 0
| 1160 | 20 | A | SSMHT0008167 | SS.MH.T0008167 | 32.2762 | -95.2838 | N21 | 6629 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.52 | 113.2912 | [18 empty] | 0
| 1161 | 20 | B | SSMHT0008168 | SS.MH.T0008168 | 32.2753 | -95.2838 | N21 | 6713 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9 | 119.32 | [18 empty] | 0
| 1162 | 20 | B | SSMHT0008169 | SS.MH.T0008169 | 32.2753 | -95.2825 | N21 | 1711 ANGY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [18 empty] | 0
| 1163 | 20 | B | SSMHT0008170 | SS.MH.T0008170 | 32.2753 | -95.2812 | O21 | 1726 ANGY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.68 | 165.5408 | [18 empty] | 0
| 1164 | 20 | B | SSMHT0008171 | SS.MH.T0008171 | 32.2753 | -95.2803 | O21 | 1818 ANGY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.38 | 124.0928 | [18 empty] | 0
| 1165 | 20 | B | SSMHT0008172 | SS.MH.T0008172 | 32.2746 | -95.2838 | N21 | 6807 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.54 | 138.6624 | [18 empty] | 0
| 1166 | 20 | B | SSMHT0008173 | SS.MH.T0008173 | 32.2744 | -95.2837 | N21 | 1625 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.16 | 159.0096 | [18 empty] | 0
| 1167 | 20 | A | SSMHT0008174 | SS.MH.T0008174 | 32.2737 | -95.284 | N21 | 6827 CIRCLE DR | Solid |  | No | Yard | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 13.3 | 173.328 | [18 empty] | 0
| 1168 | 20 | B | SSMHT0008175 | SS.MH.T0008175 | 32.2743 | -95.2835 | N21 | 1625 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.54 | 126.1024 | [18 empty] | 0
| 1169 | 20 | B | SSMHT0008176 | SS.MH.T0008176 | 32.2743 | -95.2822 | O21 | 1714 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0
| 1170 | 20 | C | SSMHT0008177 | SS.MH.T0008177 | 32.2744 | -95.2809 | O21 | 8081 CIRCLE DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.84 | 192.6704 | [18 empty] | 0
| 1171 | 20 | X-CNL | SSMHT0008178 | SS.MH.T0008178 |  |  | O21 | 1925 NORTH DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1172 | 20 | B | SSMHT0008179 | SS.MH.T0008179 | 32.275 | -95.2779 | O21 | 1925 NORTH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.24 | 109.7744 | [18 empty] | 0
| 1173 | 20 | A | SSMHT0008180 | SS.MH.T0008180 | 32.2757 | -95.2781 | O21 | 1906 NORTH DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 10.35 | 136.276 | [18 empty] | 0
| 1174 | 20 | B | SSMHT0008181 | SS.MH.T0008181 | 32.2757 | -95.2787 | O21 | 1906 NORTH DR | Vented | 2 | No | Trees/Woods | Unpaved | Below Grade | 1 | CO 6" | Other | 8.17 | [19 empty] | 0
| 1175 | 20 | A | SSMHT0008182 | SS.MH.T0008182 | 32.2751 | -95.2772 | O21 | 1937 NORTH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.93 | 93.3208 | [18 empty] | 0
| 1176 | 20 | A | SSMHT0008183 | SS.MH.T0008183 | 32.275 | -95.2752 | O21 | 2123 NORTH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.16 | 96.2096 | [18 empty] | 0
| 1177 | 20 | A | SSMHT0008184 | SS.MH.T0008184 | 32.275 | -95.2742 | O21 | 2159 NORTH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.48 | 100.2288 | [18 empty] | 0
| 1178 | 20 | B | SSMHT0008185 | SS.MH.T0008185 | 32.2711 | -95.2956 | N22 | 811 JEFF DAVIS DR | Solid |  | No | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 10.7 | 140.672 | [18 empty] | 0
| 1179 | 20 | B | SSMHT0008186 | SS.MH.T0008186 | 32.2711 | -95.2947 | N22 | 819 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 14.22 | 184.8832 | [18 empty] | 0
| 1180 | 20 | B | SSMHT0008187 | SS.MH.T0008187 | 32.2711 | -95.2933 | N22 | 921 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 14.68 | 190.6608 | [18 empty] | 0
| 1181 | 20 | C | SSMHT0008188 | SS.MH.T0008188 | 32.2711 | -95.2907 | N22 | 1115 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 12.96 | 169.0576 | [18 empty] | 0
| 1182 | 20 | A | SSMHT0008189 | SS.MH.T0008189 | 32.2711 | -95.2892 | N22 | 1211 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 10.02 | 132.1312 | [18 empty] | 0
| 1183 | 20 | C | SSMHT0008190 | SS.MH.T0008190 | 32.2711 | -95.2886 | N22 | 1211 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 11 | 144.44 | [18 empty] | 0
| 1184 | 20 | B | SSMHT0008191 | SS.MH.T0008191 | 32.2711 | -95.2858 | N22 | 1409 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.62 | 101.9872 | [18 empty] | 0
| 1185 | 20 | B | SSMHT0008192 | SS.MH.T0008192 | 32.2712 | -95.2839 | N22 | 1515 JEFFDAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 7.28 | 97.7168 | [18 empty] | 0
| 1186 | 20 | A | SSMHT0008193 | SS.MH.T0008193 | 32.2714 | -95.2827 | N22 | 1617 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 6.87 | 92.5672 | [18 empty] | 0
| 1187 | 20 | B | SSMHT0008197 | SS.MH.T0008197 | 32.2715 | -95.2817 | O22 | 1703 JEFFDAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 9.3 | 123.088 | [18 empty] | 0
| 1188 | 20 | A | SSMHT0008198 | SS.MH.T0008198 | 32.2714 | -95.2809 | O22 | 1717 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 7.89 | 105.3784 | [18 empty] | 0
| 1189 | 20 | B | SSMHT0008199 | SS.MH.T0008199 | 32.2724 | -95.2796 | O22 | 7015 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.26 | 72.3456 | [18 empty] | 0
| 1190 | 20 | A | SSMHT0008200 | SS.MH.T0008200 | 32.2716 | -95.2796 | O22 | 1816 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 5.95 | 81.012 | [18 empty] | 0
| 1191 | 20 | C | SSMHT0008201 | SS.MH.T0008201 | 32.2713 | -95.2797 | O22 | 1819 JEFF DAVIS DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.36 | 86.1616 | [18 empty] | 0
| 1192 | 20 | A | SSMHT0008202 | SS.MH.T0008202 | 32.2721 | -95.2817 | O22 | 1630 JEB STUART DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 8.07 | 107.6392 | [18 empty] | 0
| 1193 | 20 | B | SSMHT0008203 | SS.MH.T0008203 | 32.2731 | -95.282 | O22 | 1616JEB STUART DR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.26 | 84.9056 | [18 empty] | 0
| 1194 | 20 | B | SSMHT0008204 | SS.MH.T0008204 | 32.2731 | -95.2828 | N22 | 1610 JEB STUART DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 6.88 | 92.6928 | [18 empty] | 0
| 1195 | 20 | D | SSMHT0008210 | SS.MH.T0008210 | 32.2731 | -95.2879 | N22 | 1306 JEB STUART DR | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Other | 6.17 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1196 | 20 | D | SSMHT0008211 | SS.MH.T0008211 | 32.2738 | -95.2728 | O21 | 2211 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.92 | 130.8752 | [15 empty] | 900 |  |  | 900 | Repair
| 1197 | 20 | B | SSMHT0008212 | SS.MH.T0008212 | 32.2756 | -95.2734 | O21 | 6704 MANDY LN | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 6.34 | 85.9104 | [18 empty] | 0
| 1198 | 20 | X-CNL | SSMHT0008213 | SS.MH.T0008213 |  |  | O21 | 6724 MANDY LN |  |  |  | Trees/Woods | Unpaved | Below Grade | [23 empty] | 0
| 1199 | 20 | C | SSMHT0008214 | SS.MH.T0008214 | 32.2744 | -95.2734 | O21 | 2202 ROY RD | Solid |  | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.24 | 134.8944 | [18 empty] | 0
| 1200 | 20 | B | SSMHT0008215 | SS.MH.T0008215 | 32.2744 | -95.2728 | O21 | 2208 ROY RD | Solid |  | No | Field | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 8.38 | 111.5328 | [18 empty] | 0
| 1201 | 20 | B | SSMHT0008216 | SS.MH.T0008216 | 32.2738 | -95.2719 | O21 | 2211 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 5.34 | 73.3504 | [18 empty] | 0
| 1202 | 20 | B | SSMHT0008217 | SS.MH.T0008217 | 32.2738 | -95.2708 | O21 | 2335 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 10.98 | 144.1888 | [18 empty] | 0
| 1203 | 20 | D | SSMHT0008218 | SS.MH.T0008218 | 32.2738 | -95.2699 | O21 | 2448 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 14.38 | 186.8928 | [15 empty] | 900 |  |  | 900 | Repair
| 1204 | 20 | B | SSMHT0008224 | SS.MH.T0008224 | 32.2739 | -95.2692 | O21 | 2448 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 9.2 | 121.832 | [18 empty] | 0
| 1205 | 20 | B | SSMHT0008225 | SS.MH.T0008225 | 32.2739 | -95.2688 | O21 | 2448 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 11.32 | 148.4592 | [18 empty] | 0
| 1206 | 20 | A | SSMHT0008226 | SS.MH.T0008226 | 32.2744 | -95.2678 | O21 | 2502 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 8.12 | 108.2672 | [18 empty] | 0
| 1207 | 20 | B | SSMHT0008227 | SS.MH.T0008227 | 32.2748 | -95.2669 | O21 | 2624 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 9.42 | 124.5952 | [18 empty] | 0
| 1208 | 20 | X-CNL | SSMHT0008228 | SS.MH.T0008228 |  |  | O21 | 2615 ROY RD |  |  |  | Road Shoulder | Unpaved | Below Grade |  | Std 48 Round | [21 empty] | 0
| 1209 | 20 | A | SSMHT0008229 | SS.MH.T0008229 | 32.2749 | -95.2651 | O21 | 2687 ROY RD | Solid |  | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.92 | 93.1952 | [18 empty] | 0
| 1210 | 20 | C | SSMHT0008230 | SS.MH.T0008230 | 32.275 | -95.2625 | P21 | 2902 ROY RD | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.66 | 89.9296 | [18 empty] | 0
| 1211 | 20 | B | SSMHT0008231 | SS.MH.T0008231 | 32.275 | -95.2615 | P21 | 2912 ROY RD | Solid |  | Yes | Gutter | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.14 | 83.3984 | [18 empty] | 0
| 1212 | 20 | A | SSMHT0008344 | SS.MH.T0008344 | 32.2739 | -95.2758 | O21 | 2038 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.25 | 84.78 | [18 empty] | 0
| 1213 | 20 | B | SSMHT0008345 | SS.MH.T0008345 | 32.2739 | -95.2768 | O21 | ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.76 | 91.1856 | [18 empty] | 0
| 1214 | 20 | B | SSMHT0008346 | SS.MH.T0008346 | 32.2739 | -95.2778 | O21 | 1926 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.22 | 84.4032 | [18 empty] | 0
| 1215 | 20 | C | SSMHT0008347 | SS.MH.T0008347 | 32.2739 | -95.2779 | O21 | 1926 ROY RD | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 6.98 | 93.9488 | [18 empty] | 0
| 1216 | 20 | B | SSMHT0008348 | SS.MH.T0008348 | 32.2739 | -95.278 | O21 | 1926 ROY RD | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.36 | 98.7216 | [18 empty] | 0
| 1217 | 20 | A | SSMHT0008349 | SS.MH.T0008349 | 32.2738 | -95.278 | O21 | 1926 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 7.23 | 97.0888 | [18 empty] | 0
| 1218 | 20 | B | SSMHT0008350 | SS.MH.T0008350 | 32.2738 | -95.2792 | O21 | 6818 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.32 | 173.5792 | [18 empty] | 0
| 1219 | 20 | B | SSMHT0008351 | SS.MH.T0008351 | 32.273 | -95.2792 | O22 | 6928 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 7.71 | 103.1176 | [18 empty] | 0
| 1220 | 20 | B | SSMHT0008352 | SS.MH.T0008352 | 32.2724 | -95.2792 | O22 | 6928 PULUXY DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 9.82 | 129.6192 | [18 empty] | 0
| 1221 | 20 | D | SSMHT0008353 | SS.MH.T0008353 | 32.2723 | -95.2787 | O22 | 6928 PALUXY DR | Solid |  | No | Creek | Unpaved | Above Grade | 38 | Std 48 Round | Concrete | 8.9 | 118.064 | 2 | [6 empty] | 650 |  |  |  |  | 3541.92 | [5 empty] | 4191.92 | Rehabilitate
| 1222 | 20 | C | SSMHT0008358 | SS.MH.T0008358 | 32.272 | -95.2892 | N22 | 1204 JEFF DAVIS DR | Solid |  | No | Field | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.92 | 118.3152 | [18 empty] | 0
| 1223 | 20 | B | SSMHT0008359 | SS.MH.T0008359 | 32.2739 | -95.2897 | N21 | 8158 GREER DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.14 | 108.5184 | [18 empty] | 0
| 1224 | 20 | B | SSMHT0008360 | SS.MH.T0008360 | 32.2739 | -95.2896 | N21 | 8160 GREER DR. | Solid |  | No | Yard | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 9.32 | 123.3392 | [18 empty] | 0
| 1225 | 20 | C | SSMHT0008361 | SS.MH.T0008361 | 32.2739 | -95.2893 | N21 | 8160 GREER DR. | Solid |  | No | Trees/Woods | Unpaved | At Grade | 18 | Std 48 Round | Concrete | 8.52 | 113.2912 | [18 empty] | 0
| 1226 | 20 | X-CNL | SSMHT0008362 | SS.MH.T0008362 |  |  | N22 | 1302 JEB STUART DR |  |  |  | Trees/Woods | Unpaved | Below Grade | [23 empty] | 0
| 1227 | 20 | C | SSMHT0008363 | SS.MH.T0008363 | 32.27 | -95.2949 | N22 | 902 MCCLENNY DR. | Solid |  | No | Yard | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 7 | 94.2 | [18 empty] | 0
| 1228 | 20 | B | SSMHT0008364 | SS.MH.T0008364 | 32.27 | -95.2943 | N22 | 902 MCCLENNY DR. | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 10.72 | 140.9232 | [18 empty] | 0
| 1229 | 20 | B | SSMHT0008365 | SS.MH.T0008365 | 32.2702 | -95.2956 | N22 | 715 JEFFDAVIS DR | Solid |  | No | Field | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.98 | 119.0688 | [18 empty] | 0
| 1230 | 20 | C | SSMHT0008366 | SS.MH.T0008366 | 32.2691 | -95.2942 | N22 | 800 MCCLENNY DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.02 | 144.6912 | [18 empty] | 0
| 1231 | 20 | B | SSMHT0008367 | SS.MH.T0008367 | 32.2691 | -95.2945 | N22 | 8300 EL CERRITO PL. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 1232 | 20 | B | SSMHT0008368 | SS.MH.T0008368 | 32.2691 | -95.2945 | N22 | 8300 EL CERRITO PL. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.76 | 103.7456 | [18 empty] | 0
| 1233 | 20 | B | SSMHT0008369 | SS.MH.T0008369 | 32.2684 | -95.2945 | N22 | 8313 EL CERRITO PL. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.92 | 105.7552 | [18 empty] | 0
| 1234 | 20 | C | SSMHT0008371 | SS.MH.T0008371 | 32.2691 | -95.2933 | N22 | 8300 GARRETT DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.14 | 121.0784 | [18 empty] | 0
| 1235 | 20 | C | SSMHT0008372 | SS.MH.T0008372 | 32.2683 | -95.2933 | N22 | 8313 GARRETT DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.34 | 98.4704 | [18 empty] | 0
| 1236 | 20 | B | SSMHT0008373 | SS.MH.T0008373 | 32.2691 | -95.2925 | N22 | 1017 MCCLENNY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.49 | 125.4744 | [18 empty] | 0
| 1237 | 20 | A | SSMHT0008374 | SS.MH.T0008374 | 32.269 | -95.2919 | N22 | 1017 MCCLENLY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.37 | 136.5272 | [18 empty] | 0
| 1238 | 20 | A | SSMHT0008375 | SS.MH.T0008375 | 32.2689 | -95.2909 | N22 | 1017 MCCLENNY DR | Solid |  | No | Yard | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 19.47 | 250.8232 | [18 empty] | 0
| 1239 | 20 | B | SSMHT0008379 | SS.MH.T0008379 | 32.2661 | -95.2958 | N22 | 800 MARQUETTE LANE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1240 | 20 | B | SSMHT0008380 | SS.MH.T0008380 | 32.2653 | -95.2957 | N22 | 8300 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.8 | 154.488 | [18 empty] | 0
| 1241 | 20 | B | SSMHT0008381 | SS.MH.T0008381 | 32.2648 | -95.2957 | N22 | 8379 CASTLETON WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.5 | 138.16 | [18 empty] | 0
| 1242 | 20 | C | SSMHT0008382 | SS.MH.T0008382 | 32.2644 | -95.2957 | N22 | 8387 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.64 | 127.3584 | [18 empty] | 0
| 1243 | 20 | C | SSMHT0008383 | SS.MH.T0008383 | 32.2634 | -95.2958 | N22 | 8417 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.9 | 130.624 | [18 empty] | 0
| 1244 | 20 | D | SSMHT0008384 | SS.MH.T0008384 | 32.2629 | -95.2957 | N22 | 8425 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 10.7 | 140.672 | 2 | [11 empty] | 4220.16 | [5 empty] | 4220.16 | Rehabilitate
| 1245 | 20 | C | SSMHT0008385 | SS.MH.T0008385 | 32.2628 | -95.2955 | N22 | 8422 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.86 | 180.3616 | [18 empty] | 0
| 1246 | 20 | B | SSMHT0008386 | SS.MH.T0008386 | 32.2653 | -95.2952 | N22 | 813 CAMBRIDGE BEND. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.5 | 100.48 | [18 empty] | 0
| 1247 | 20 | C | SSMHT0008387 | SS.MH.T0008387 | 32.2655 | -95.2947 | N22 | 821 CAMBRIDGE BEND. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.2 | 96.712 | [18 empty] | 0
| 1248 | 20 | B | SSMHT0008434 | SS.MH.T0008434 | 32.266 | -95.2942 | N22 | 832 CAMBRIDGE BEND. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.06 | 120.0736 | [18 empty] | 0
| 1249 | 20 | B | SSMHT0008435 | SS.MH.T0008435 | 32.2662 | -95.2935 | N22 | 908 CAMBRIDGE BEND. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.84 | 167.5504 | [18 empty] | 0
| 1250 | 20 | B | SSMHT0008436 | SS.MH.T0008436 | 32.2657 | -95.2936 | N22 | 6309 ROCHESTER WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13 | 169.56 | [18 empty] | 0
| 1251 | 20 | B | SSMHT0008437 | SS.MH.T0008437 | 32.2651 | -95.2938 | N22 | 6320 ROCHESTER WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.46 | 175.3376 | [18 empty] | 0
| 1252 | 20 | B | SSMHT0008438 | SS.MH.T0008438 | 32.2642 | -95.2943 | N22 | 6446 ROCHESTER WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 60 Round | Concrete | 16.54 | 214.0224 | [18 empty] | 0
| 1253 | 20 | C | SSMHT0008439 | SS.MH.T0008439 | 32.2635 | -95.2946 | N22 | 6459 ROCHESTER WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.6 | 202.216 | [18 empty] | 0
| 1254 | 20 | C | SSMHT0008440 | SS.MH.T0008440 | 32.2627 | -95.2948 | N22 | 8500 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.2 | 134.392 | [18 empty] | 0
| 1255 | 20 | C | SSMHT0008441 | SS.MH.T0008441 | 32.2619 | -95.2947 | N23 | 6515 ROCHESTER WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.5 | 200.96 | [18 empty] | 0
| 1256 | 20 | B | SSMHT0008442 | SS.MH.T0008442 | 32.2614 | -95.2946 | N23 | 6519 ROCHESTER WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.26 | 172.8256 | [18 empty] | 0
| 1257 | 20 | B | SSMHT0008443 | SS.MH.T0008443 | 32.2627 | -95.2937 | N22 | 8513 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.5 | 125.6 | [18 empty] | 0
| 1258 | 20 | B | SSMHT0008444 | SS.MH.T0008444 | 32.2631 | -95.2937 | N22 | 6567 WHEATON CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.82 | 104.4992 | [18 empty] | 0
| 1259 | 20 | B | SSMHT0008445 | SS.MH.T0008445 | 32.2637 | -95.2935 | N22 | 6555 WHEATON CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.98 | 106.5088 | [18 empty] | 0
| 1260 | 20 | B | SSMHT0008446 | SS.MH.T0008446 | 32.2628 | -95.2926 | N22 | 8535 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.28 | 122.8368 | [18 empty] | 0
| 1261 | 20 | B | SSMHT0008447 | SS.MH.T0008447 | 32.2631 | -95.2926 | N22 | 6557 EMORY CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.2 | 121.832 | [18 empty] | 0
| 1262 | 20 | B | SSMHT0008448 | SS.MH.T0008448 | 32.2635 | -95.2924 | N22 | 6540 EMORY CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9 | 119.32 | [18 empty] | 0
| 1263 | 20 | B | SSMHT0008449 | SS.MH.T0008449 | 32.2628 | -95.2917 | N22 | 8553 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1264 | 20 | B | SSMHT0008450 | SS.MH.T0008450 | 32.263 | -95.2915 | N22 | 8559 CAMBRIDGE BEND. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.1 | 120.576 | [18 empty] | 0
| 1265 | 20 | C | SSMHT0008451 | SS.MH.T0008451 | 32.264 | -95.291 | N22 | 1203 CAMBRIDGE BEND. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 17.06 | 220.5536 | [18 empty] | 0
| 1266 | 20 | B | SSMHT0008452 | SS.MH.T0008452 | 32.2638 | -95.2905 | N22 | 6566 FURMAN CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.98 | 181.8688 | [18 empty] | 0
| 1267 | 20 | B | SSMHT0008453 | SS.MH.T0008453 | 32.2637 | -95.2904 | N22 | 6566 FURMAN CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.54 | 176.3424 | [18 empty] | 0
| 1268 | 20 | B | SSMHT0008454 | SS.MH.T0008454 | 32.2635 | -95.2903 | N22 | 6578 FURMAN CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.2 | 146.952 | [18 empty] | 0
| 1269 | 20 | B | SSMHT0008455 | SS.MH.T0008455 | 32.2655 | -95.2905 | N22 | 1111 CAMBRIDGE BEND. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.6 | 139.416 | [18 empty] | 0
| 1270 | 20 | C | SSMHT0008457 | SS.MH.T0008457 | 32.266 | -95.2904 | N22 | 1105 CAMBRIDGE BEND. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 1271 | 20 | B | SSMHT0008458 | SS.MH.T0008458 | 32.2662 | -95.2906 | N22 | 1105 CAMBRIDGE BEND. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.56 | 126.3536 | [18 empty] | 0
| 1272 | 20 | B | SSMHT0008459 | SS.MH.T0008459 | 32.2662 | -95.2914 | N22 | 1000 CAMBRIDGE BEND. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.38 | 124.0928 | [18 empty] | 0
| 1273 | 20 | B | SSMHT0008460 | SS.MH.T0008460 | 32.2656 | -95.2915 | N22 | 6352 MANCHESTER CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.3 | 135.648 | [18 empty] | 0
| 1274 | 20 | B | SSMHT0008461 | SS.MH.T0008461 | 32.2662 | -95.2925 | N22 | 6300 OBERLIN CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.04 | 69.5824 | [18 empty] | 0
| 1275 | 20 | B | SSMHT0008462 | SS.MH.T0008462 | 32.2655 | -95.2926 | N22 | 6355 OBERLIN CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.32 | 85.6592 | [18 empty] | 0
| 1276 | 20 | D | SSMHT0008463 | SS.MH.T0008463 | 32.2533 | -95.2858 | N23 | NONE OLD HICKORY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.2 | 109.272 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair
| 1277 | 20 | B | SSMHT0008464 | SS.MH.T0008464 | 32.2532 | -95.2857 | N23 | NONE OLD HICKORY RD | Solid |  | No | Street | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.51 | 113.1656 | [18 empty] | 0
| 1278 | 20 | C | SSMHT0008465 | SS.MH.T0008465 | 32.253 | -95.2858 | N23 | NONE OLD HICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.04 | 107.2624 | [18 empty] | 0
| 1279 | 20 | C | SSMHT0008466 | SS.MH.T0008466 | 32.2525 | -95.2858 | N23 | 1467 OLD CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | [18 empty] | 0
| 1280 | 20 | C | SSMHT0008467 | SS.MH.T0008467 | 32.2517 | -95.285 | N23 | 9004 OLD HICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.58 | 63.8048 | [18 empty] | 0
| 1281 | 20 | C | SSMHT0008468 | SS.MH.T0008468 | 32.2517 | -95.285 | N23 | 9004 OLD HICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.52 | 100.7312 | [18 empty] | 0
| 1282 | 20 | C | SSMHT0008469 | SS.MH.T0008469 | 32.2515 | -95.285 | N23 | 9010 OLD HICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.54 | 88.4224 | [18 empty] | 0
| 1283 | 20 | C | SSMHT0008471 | SS.MH.T0008471 | 32.2525 | -95.2868 | N23 | 1443 OLD CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.88 | 130.3728 | [18 empty] | 0
| 1284 | 20 | B | SSMHT0008472 | SS.MH.T0008472 | 32.2525 | -95.2881 | N23 | 1395 OLD CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1285 | 20 | X-CNO | SSMHT0008473 | SS.MH.T0008473 | 32.2525 | -95.2894 | N23 | 1395 OLD CREEK DR | Solid |  |  | Street | Paved - Asphalt | At Grade | [23 empty] | 0
| 1286 | 20 | A | SSMHT0008475 | SS.MH.T0008475 | 32.2502 | -95.2849 | N24 | 9115 OLD MICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.12 | 196.1872 | [18 empty] | 0
| 1287 | 20 | B | SSMHT0008476 | SS.MH.T0008476 | 32.2486 | -95.2854 | N24 | 9202 ELM TREE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.92 | 181.1152 | [18 empty] | 0
| 1288 | 20 | C | SSMHT0008477 | SS.MH.T0008477 | 32.2481 | -95.2849 | N24 | 9229 ELM TREE RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.98 | 144.1888 | [18 empty] | 0
| 1289 | 20 | B | SSMHT0008478 | SS.MH.T0008478 | 32.2479 | -95.2845 | N24 | 9241 ELM TREE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.4 | 111.784 | [18 empty] | 0
| 1290 | 20 | C | SSMHT0008479 | SS.MH.T0008479 | 32.2479 | -95.2841 | N24 | 9241 ELM TREE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.56 | 88.6736 | [18 empty] | 0
| 1291 | 20 | B | SSMHT0008480 | SS.MH.T0008480 | 32.2496 | -95.2864 | N24 | 9132 ELM TREE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.92 | 155.9952 | [18 empty] | 0
| 1292 | 20 | B | SSMHT0008481 | SS.MH.T0008481 | 32.2498 | -95.2865 | N24 | 9108 ELM TREE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.36 | 174.0816 | [18 empty] | 0
| 1293 | 20 | B | SSMHT0008482 | SS.MH.T0008482 | 32.2506 | -95.2868 | N24 | 9062 ELM TREE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.82 | 179.8592 | [18 empty] | 0
| 1294 | 20 | A | SSMHT0008483 | SS.MH.T0008483 | 32.2509 | -95.287 | N24 | 9018 ELM TREE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.22 | 159.7632 | [18 empty] | 0
| 1295 | 20 | X-CNO | SSMHT0008484 | SS.MH.T0008484 | 32.2515 | -95.2872 | N24 | 9033 ELM TREE CIR | Solid |  |  | Yard | Unpaved | At Grade | [23 empty] | 0
| 1296 | 20 | B | SSMHT0008485 | SS.MH.T0008485 | 32.2502 | -95.2835 | N24 | 1528 CIMMARON TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.48 | 188.1488 | [18 empty] | 0
| 1297 | 20 | C | SSMHT0008486 | SS.MH.T0008486 | 32.2504 | -95.2836 | N24 | 1602 CIMMARON TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.42 | 137.1552 | [18 empty] | 0
| 1298 | 20 | B | SSMHT0008487 | SS.MH.T0008487 | 32.2505 | -95.2834 | N24 | 1602 CIMMARRON TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.58 | 101.4848 | [18 empty] | 0
| 1299 | 20 | C | SSMHT0008548 | SS.MH.T0008548 | 32.2505 | -95.2822 | O24 | 1613 CIMMARRON TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.49 | 138.0344 | [18 empty] | 0
| 1300 | 20 | C | SSMHT0008549 | SS.MH.T0008549 | 32.2505 | -95.2811 | O24 | 1621 CIMMARRON TRAIL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.74 | 141.1744 | [18 empty] | 0
| 1301 | 20 | B | SSMHT0008550 | SS.MH.T0008550 | 32.2504 | -95.281 | O24 | 1621 CIMMARON TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.56 | 151.4736 | [18 empty] | 0
| 1302 | 20 | A | SSMHT0008551 | SS.MH.T0008551 | 32.2496 | -95.281 | O24 | 9106 STONE CREEK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.54 | 100.9824 | [18 empty] | 0
| 1303 | 20 | B | SSMHT0008552 | SS.MH.T0008552 | 32.2491 | -95.281 | O24 | 1620 WILLOW BEND | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.99 | 144.3144 | [18 empty] | 0
| 1304 | 20 | B | SSMHT0008553 | SS.MH.T0008553 | 32.2496 | -95.2823 | O24 | 1613 TRAIL RIDGE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.5 | 87.92 | [18 empty] | 0
| 1305 | 20 | B | SSMHT0008554 | SS.MH.T0008554 | 32.2497 | -95.2835 | N24 | 9105 CANYON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.16 | 108.7696 | [18 empty] | 0
| 1306 | 20 | B | SSMHT0008555 | SS.MH.T0008555 | 32.2488 | -95.2835 | N24 | 9117 CANYON RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.06 | 107.5136 | [18 empty] | 0
| 1307 | 20 | C | SSMHT0008556 | SS.MH.T0008556 | 32.2488 | -95.2822 | O24 | 1613 WILLOW BEND | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.98 | 106.5088 | [18 empty] | 0
| 1308 | 20 | A | SSMHT0008714 | SS.MH.T0008714 | 32.2491 | -95.2799 | O24 | 1630 WILLOW BEND | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.72 | 115.8032 | [18 empty] | 0
| 1309 | 20 | B | SSMHT0008715 | SS.MH.T0008715 | 32.2479 | -95.2799 | O24 | 1630 SKIDMORE LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.6 | 101.736 | [18 empty] | 0
| 1310 | 20 | B | SSMHT0008716 | SS.MH.T0008716 | 32.2479 | -95.2812 | O24 | 1620 SKIDMORE LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.34 | 111.0304 | [18 empty] | 0
| 1311 | 20 | B | SSMHT0008717 | SS.MH.T0008717 | 32.2479 | -95.2823 | O24 | 1608 SKIDMORE LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.9 | 118.064 | [18 empty] | 0
| 1312 | 20 | A | SSMHT0008718 | SS.MH.T0008718 | 32.2479 | -95.2835 | N24 | 1605 SKIDMORE LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.42 | 99.4752 | [18 empty] | 0
| 1313 | 20 | B | SSMHT0008719 | SS.MH.T0008719 | 32.2495 | -95.2793 | O24 | 1750 CENTENNIAL PWK | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 6.12 | 83.1472 | [18 empty] | 0
| 1314 | 20 | A | SSMHT0008720 | SS.MH.T0008720 | 32.248 | -95.2869 | N24 | 1443 OLD HICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.12 | 145.9472 | [18 empty] | 0
| 1315 | 20 | A | SSMHT0008721 | SS.MH.T0008721 | 32.2486 | -95.2875 | N24 | 9163 COUNTY RD 1165 | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.23 | 134.7688 | [18 empty] | 0
| 1316 | 20 | B | SSMHT0008722 | SS.MH.T0008722 | 32.2491 | -95.2879 | N24 | 7183 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.22 | 109.5232 | [18 empty] | 0
| 1317 | 20 | B | SSMHT0008723 | SS.MH.T0008723 | 32.2492 | -95.288 | N24 | 9183 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.06 | 107.5136 | [18 empty] | 0
| 1318 | 20 | B | SSMHT0008724 | SS.MH.T0008724 | 32.2479 | -95.2873 | N24 | 1379 OLD HICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.32 | 98.2192 | [18 empty] | 0
| 1319 | 20 | B | SSMHT0008725 | SS.MH.T0008725 | 32.2479 | -95.2894 | N24 | 1261 OLD HICKORY RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.06 | 107.5136 | [18 empty] | 0
| 1320 | 20 | B | SSMHT0008726 | SS.MH.T0008726 | 32.2479 | -95.2907 | N24 | 9375 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.14 | 108.5184 | [18 empty] | 0
| 1321 | 20 | B | SSMHT0008727 | SS.MH.T0008727 | 32.2489 | -95.2907 | N24 | 1201 BUFFALO TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.48 | 150.4688 | [18 empty] | 0
| 1322 | 20 | A | SSMHT0008728 | SS.MH.T0008728 | 32.2489 | -95.2894 | N24 | 1215 BUFFALO TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.46 | 137.6576 | [18 empty] | 0
| 1323 | 20 | B | SSMHT0008729 | SS.MH.T0008729 | 32.2489 | -95.2884 | N24 | 1255 BUFFALO TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.82 | 104.4992 | [18 empty] | 0
| 1324 | 20 | B | SSMHT0008730 | SS.MH.T0008730 | 32.2489 | -95.2881 | N24 | 1255 BUFFALO TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.42 | 99.4752 | [18 empty] | 0
| 1325 | 20 | B | SSMHT0008731 | SS.MH.T0008731 | 32.2495 | -95.2883 | N24 | 9191 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.68 | 190.6608 | [18 empty] | 0
| 1326 | 20 | D | SSMHT0008732 | SS.MH.T0008732 | 32.25 | -95.2885 | N24 | 9218 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.44 | 187.6464 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 1327 | 20 | B | SSMHT0008733 | SS.MH.T0008733 | 32.2507 | -95.2888 | N24 | 9243 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.56 | 201.7136 | [18 empty] | 0
| 1328 | 20 | B | SSMHT0008734 | SS.MH.T0008734 | 32.2509 | -95.2892 | N24 | 9243 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.84 | 192.6704 | [18 empty] | 0
| 1329 | 20 | B | SSMHT0008735 | SS.MH.T0008735 | 32.2509 | -95.2903 | N24 | 9285 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.56 | 176.5936 | [18 empty] | 0
| 1330 | 20 | B | SSMHT0008736 | SS.MH.T0008736 | 32.251 | -95.2905 | N24 | 9285 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.68 | 140.4208 | [18 empty] | 0
| 1331 | 20 | B | SSMHT0008737 | SS.MH.T0008737 | 32.2508 | -95.2907 | N24 | 9301 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.78 | 129.1168 | [18 empty] | 0
| 1332 | 20 | B | SSMHT0008738 | SS.MH.T0008738 | 32.25 | -95.2907 | N24 | 9334 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.16 | 146.4496 | [18 empty] | 0
| 1333 | 20 | B | SSMHT0008739 | SS.MH.T0008739 | 32.2469 | -95.2907 | N24 | 9399 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.62 | 152.2272 | [18 empty] | 0
| 1334 | 20 | A | SSMHT0008740 | SS.MH.T0008740 | 32.2469 | -95.2887 | N24 | 1305 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.32 | 135.8992 | [18 empty] | 0
| 1335 | 20 | B | SSMHT0008741 | SS.MH.T0008741 | 32.2469 | -95.2874 | N24 | 1379 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.74 | 141.1744 | [18 empty] | 0
| 1336 | 20 | B | SSMHT0008742 | SS.MH.T0008742 | 32.2466 | -95.2861 | N24 | 1423 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.17 | 121.4552 | [18 empty] | 0
| 1337 | 20 | D | SSMHT0008743 | SS.MH.T0008743 | 32.2469 | -95.2861 | N24 | 1504 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.4 | 149.464 | [8 empty] | 1950 |  | 725 |  |  |  |  | 900 |  |  | 3575 | Repair
| 1338 | 20 | B | SSMHT0008744 | SS.MH.T0008744 | 32.2471 | -95.2862 | N24 | 1504 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.66 | 140.1696 | [18 empty] | 0
| 1339 | 20 | A | SSMHT0008745 | SS.MH.T0008745 | 32.2474 | -95.2863 | N24 | 9141 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.34 | 123.5904 | [18 empty] | 0
| 1340 | 20 | B | SSMHT0008746 | SS.MH.T0008746 | 32.2469 | -95.2848 | N24 | 1527 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.12 | 58.0272 | [18 empty] | 0
| 1341 | 20 | B | SSMHT0008747 | SS.MH.T0008747 | 32.2459 | -95.2854 | N24 | 1509 SANTA FE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.34 | 123.5904 | [18 empty] | 0
| 1342 | 20 | C | SSMHT0008748 | SS.MH.T0008748 | 32.2459 | -95.286 | N24 | 1423 SANTA FE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.18 | 121.5808 | [18 empty] | 0
| 1343 | 20 | B | SSMHT0008749 | SS.MH.T0008749 | 32.2459 | -95.2884 | N24 | 1305 SANTA FE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.12 | 83.1472 | [18 empty] | 0
| 1344 | 20 | B | SSMHT0008750 | SS.MH.T0008750 | 32.2459 | -95.2894 | N24 | 1266 SANTA FE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.76 | 103.7456 | [18 empty] | 0
| 1345 | 20 | X-CNL | SSMHT0008751 | SS.MH.T0008751 |  |  | N24 | 9243COUNTY RD 1165 |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1346 | 20 | B | SSMHT0008752 | SS.MH.T0008752 | 32.2457 | -95.2836 | N24 | 1533 SKIDMORE LN | Solid |  | No | Field | Unpaved | Above Grade | 22 | Std 48 Round | Concrete | 10.28 | 135.3968 | [18 empty] | 0
| 1347 | 20 | B | SSMHT0008753 | SS.MH.T0008753 | 32.2467 | -95.2836 | N24 | 1613 LEGACY DR | Solid |  | No | Field | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 11.2 | 146.952 | [18 empty] | 0
| 1348 | 20 | B | SSMHT0008754 | SS.MH.T0008754 | 32.2459 | -95.2907 | N24 | 1221 SANTE FE TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.48 | 125.3488 | [18 empty] | 0
| 1349 | 20 | D | SSMHT0008760 | SS.MH.T0008760 | 32.251 | -95.2806 | O24 | 9094 STONE CREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 7.02 | 94.4512 | 2 | [11 empty] | 2833.536 | [5 empty] | 2833.536 | Rehabilitate
| 1350 | 20 | D | SSMHT0008761 | SS.MH.T0008761 | 32.251 | -95.2804 | O24 | 9094 STONE CREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 7.1 | 95.456 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 1351 | 20 | D | SSMHT0008762 | SS.MH.T0008762 | 32.2507 | -95.2794 | O24 | 9141 PALUXY DR | Solid |  | No | Field | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 6.4 | 86.664 | [10 empty] | 725 |  |  | 700 |  |  |  |  | 1425 | Repair
| 1352 | 20 | B | SSMHT0008763 | SS.MH.T0008763 | 32.2507 | -95.2788 | O24 | 9141 PALUXY DR | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 9.84 | 129.8704 | [18 empty] | 0
| 1353 | 20 | D | SSMHT0008764 | SS.MH.T0008764 | 32.25 | -95.2804 | O24 | 1628 WILLOW BEND | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 6.9 | 92.944 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
| 1354 | 20 | B | SSMHT0008765 | SS.MH.T0008765 | 32.2495 | -95.2804 | O24 | 1628 WILLOW BEND | Solid |  | No | Yard | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 6.02 | 81.8912 | [18 empty] | 0
| 1355 | 20 | C | SSMHT0008768 | SS.MH.T0008768 | 32.2527 | -95.2826 | O23 | 1545 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 8.53 | 113.4168 | [18 empty] | 0
| 1356 | 20 | B | SSMHT0008776 | SS.MH.T0008776 | 32.2531 | -95.2847 | N23 | 1502 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 9.04 | 119.8224 | [18 empty] | 0
| 1357 | 20 | B | SSMHT0008777 | SS.MH.T0008777 | 32.2544 | -95.2857 | N23 | 1502 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 7.36 | 98.7216 | [18 empty] | 0
| 1358 | 20 | C | SSMHT0008778 | SS.MH.T0008778 | 32.2551 | -95.2857 | N23 | 1502 WILANA DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 9.44 | 124.8464 | [18 empty] | 0
| 1359 | 20 | B | SSMHT0008779 | SS.MH.T0008779 | 32.2551 | -95.2856 | N23 | 1502 WILANA DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 9.56 | 126.3536 | [18 empty] | 0
| 1360 | 20 | B | SSMHT0008780 | SS.MH.T0008780 | 32.2549 | -95.2847 | N23 | 1516 WILANA DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.02 | 144.6912 | [18 empty] | 0
| 1361 | 20 | B | SSMHT0008781 | SS.MH.T0008781 | 32.2557 | -95.2837 | N23 | 1534 WILANA DR | Solid |  | No | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 9.29 | 122.9624 | [18 empty] | 0
| 1362 | 20 | D | SSMHT0008782 | SS.MH.T0008782 | 32.2535 | -95.2857 | N23 | 1502 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 11 | Std 48 Round | Concrete | 6.88 | 92.6928 | [7 empty] | 650 |  | 1000 | 725 |  |  |  | 280 |  |  |  | 2655 | Repair
| 1363 | 20 | A | SSMHT0008783 | SS.MH.T0008783 | 32.2561 | -95.2887 | N23 | NONE WILDER TRL | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 5.84 | 79.6304 | [18 empty] | 0
| 1364 | 20 | C | SSMHT0008784 | SS.MH.T0008784 | 32.2569 | -95.2885 | N23 | NONE WILDER TRL | Solid |  | No | Yard | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 8.27 | 110.1512 | [18 empty] | 0
| 1365 | 20 | C | SSMHT0008785 | SS.MH.T0008785 | 32.2568 | -95.2879 | N23 | 1308 CUMBERLAND RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 11.8 | 154.488 | [18 empty] | 0
| 1366 | 20 | B | SSMHT0008786 | SS.MH.T0008786 | 32.2565 | -95.2878 | N23 | 1308 CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 6.46 | 87.4176 | [18 empty] | 0
| 1367 | 20 | C | SSMHT0008787 | SS.MH.T0008787 | 32.2565 | -95.2861 | N23 | 1418 CUMBERLAND RD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 7.82 | 104.4992 | [18 empty] | 0
| 1368 | 20 | B | SSMHT0008788 | SS.MH.T0008788 | 32.2566 | -95.2871 | N23 | 1418 CUMBERLAND RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 11.7 | 153.232 | [18 empty] | 0
| 1369 | 20 | B | SSMHT0008789 | SS.MH.T0008789 | 32.2569 | -95.2886 | N23 | NONE WILMER TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1370 | 20 | B | SSMHT0008790 | SS.MH.T0008790 | 32.2571 | -95.2886 | N23 | NONE WILDER TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 1371 | 20 | C | SSMHT0008791 | SS.MH.T0008791 | 32.2572 | -95.2889 | N23 | NONE WILDER TRL | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 10.04 | 132.3824 | [18 empty] | 0
| 1372 | 20 | C | SSMHT0008792 | SS.MH.T0008792 | 32.2573 | -95.289 | N23 | NONE WILDER TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.24 | 134.8944 | [18 empty] | 0
| 1373 | 20 | B | SSMHT0008793 | SS.MH.T0008793 | 32.2578 | -95.2889 | N23 | NONE WILDER TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.96 | 156.4976 | [18 empty] | 0
| 1374 | 20 | B | SSMHT0008794 | SS.MH.T0008794 | 32.258 | -95.2888 | N23 | NONE WILDER TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.18 | 134.1408 | [18 empty] | 0
| 1375 | 20 | C | SSMHT0008795 | SS.MH.T0008795 | 32.2583 | -95.2888 | N23 | NONE WILDER TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.08 | 120.3248 | [18 empty] | 0
| 1376 | 20 | D | SSMHT0008796 | SS.MH.T0008796 | 32.2587 | -95.2892 | N23 | NONE WILDER TRL | Solid |  | No | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 9.91 | 130.7496 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
| 1377 | 20 | B | SSMHT0008797 | SS.MH.T0008797 | 32.2553 | -95.2917 | N23 | 1111 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 9.28 | 122.8368 | [18 empty] | 0
| 1378 | 20 | C | SSMHT0008798 | SS.MH.T0008798 | 32.2555 | -95.2921 | N23 | 1111 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.26 | 122.5856 | [18 empty] | 0
| 1379 | 20 | C | SSMHT0008799 | SS.MH.T0008799 | 32.2566 | -95.2837 | N23 | 1516 WILANA DR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.86 | 117.5616 | [18 empty] | 0
| 1380 | 20 | B | SSMHT0008800 | SS.MH.T0008800 | 32.2566 | -95.2848 | N23 | 1516 WILANA DR | Solid |  | No | Field | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 8.6 | 114.296 | [18 empty] | 0
| 1381 | 20 | C | SSMHT0008843 | SS.MH.T0008843 | 32.2473 | -95.3075 | M24 | 107 MARKET SQUARE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.58 | 114.0448 | [18 empty] | 0
| 1382 | 20 | C | SSMHT0008844 | SS.MH.T0008844 | 32.2473 | -95.3065 | M24 | 151 MARKET SQUARE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.4 | 86.664 | [18 empty] | 0
| 1383 | 20 | B | SSMHT0008845 | SS.MH.T0008845 | 32.2473 | -95.3054 | M24 | 151 MARKET SQUARE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.07 | 107.6392 | [18 empty] | 0
| 1384 | 20 | C | SSMHT0008847 | SS.MH.T0008847 | 32.2467 | -95.3043 | M24 | NONE MARKET SQUARE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.3 | 185.888 | [18 empty] | 0
| 1385 | 20 | A | SSMHT0008848 | SS.MH.T0008848 | 32.2462 | -95.3045 | M24 | NONE MARKET SQUARE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.1 | 170.816 | [18 empty] | 0
| 1386 | 20 | B | SSMHT0008849 | SS.MH.T0008849 | 32.2458 | -95.3045 | M24 | NONE MARKET SQUARE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.21 | 172.1976 | [18 empty] | 0
| 1387 | 20 | A | SSMHT0008850 | SS.MH.T0008850 | 32.2458 | -95.3056 | M24 | 151 MARKET SQUARE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.54 | 113.5424 | [18 empty] | 0
| 1388 | 20 | B | SSMHT0008890 | SS.MH.T0008890 | 32.2478 | -95.3023 | N24 | NONE CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.16 | 146.4496 | [18 empty] | 0
| 1389 | 20 | B | SSMHT0008891 | SS.MH.T0008891 | 32.2483 | -95.3018 | N24 | NONE CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.64 | 102.2384 | [18 empty] | 0
| 1390 | 20 | B | SSMHT0008892 | SS.MH.T0008892 | 32.2527 | -95.307 | M23 | 8942 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.66 | 127.6096 | [18 empty] | 0
| 1391 | 20 | B | SSMHT0008893 | SS.MH.T0008893 | 32.2527 | -95.3046 | M23 | 172 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.88 | 80.1328 | [18 empty] | 0
| 1392 | 20 | B | SSMHT0008894 | SS.MH.T0008894 | 32.2527 | -95.3035 | M23 | 172 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.98 | 181.8688 | [18 empty] | 0
| 1393 | 20 | B | SSMHT0008895 | SS.MH.T0008895 | 32.2526 | -95.3027 | M23 | 172 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.38 | 124.0928 | [18 empty] | 0
| 1394 | 20 | B | SSMHT0008896 | SS.MH.T0008896 | 32.2522 | -95.3021 | N23 | 172 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.16 | 83.6496 | [18 empty] | 0
| 1395 | 20 | B | SSMHT0008897 | SS.MH.T0008897 | 32.2517 | -95.3017 | N23 | 172 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.64 | 77.1184 | [18 empty] | 0
| 1396 | 20 | B | SSMHT0008898 | SS.MH.T0008898 | 32.2511 | -95.3016 | N24 | NONE CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.2 | 84.152 | [18 empty] | 0
| 1397 | 20 | B | SSMHT0008899 | SS.MH.T0008899 | 32.2502 | -95.3017 | N24 | NONE CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.66 | 140.1696 | [18 empty] | 0
| 1398 | 20 | B | SSMHT0008900 | SS.MH.T0008900 | 32.2492 | -95.3017 | N24 | NONE CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.24 | 122.3344 | [18 empty] | 0
| 1399 | 20 | B | SSMHT0008901 | SS.MH.T0008901 | 32.2523 | -95.3035 | M23 | 8668 S BROADWAY AVE | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.66 | 140.1696 | [18 empty] | 0
| 1400 | 20 | B | SSMHT0008902 | SS.MH.T0008902 | 32.2524 | -95.3047 | M23 | 8668 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1401 | 20 | B | SSMHT0008903 | SS.MH.T0008903 | 32.2524 | -95.306 | M23 | 8942 S BROADWAY AVE | Solid |  | No | Parking Lot | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.5 | 87.92 | [18 empty] | 0
| 1402 | 20 | B | SSMHT0008904 | SS.MH.T0008904 | 32.2525 | -95.3066 | M23 | 8942 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.56 | 101.2336 | [18 empty] | 0
| 1403 | 20 | B | SSMHT0008905 | SS.MH.T0008905 | 32.2522 | -95.3071 | M24 | 8942 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.18 | 96.4608 | [18 empty] | 0
| 1404 | 20 | B | SSMHT0008906 | SS.MH.T0008906 | 32.2519 | -95.3071 | M23 | 8942 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.58 | 101.4848 | [18 empty] | 0
| 1405 | 20 | B | SSMHT0008907 | SS.MH.T0008907 | 32.251 | -95.3072 | M24 | 8922 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.85 | 92.316 | [18 empty] | 0
| 1406 | 20 | B | SSMHT0008908 | SS.MH.T0008908 | 32.2501 | -95.3072 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.19 | 84.0264 | [18 empty] | 0
| 1407 | 20 | B | SSMHT0008909 | SS.MH.T0008909 | 32.2495 | -95.3073 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.04 | 82.1424 | [18 empty] | 0
| 1408 | 20 | B | SSMHT0008910 | SS.MH.T0008910 | 32.2486 | -95.3074 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.48 | 87.6688 | [18 empty] | 0
| 1409 | 20 | A | SSMHT0008911 | SS.MH.T0008911 | 32.2484 | -95.3074 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.26 | 72.3456 | [18 empty] | 0
| 1410 | 20 | C | SSMHT0008912 | SS.MH.T0008912 | 32.2477 | -95.3042 | M24 | 8966 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 15.91 | 206.1096 | [18 empty] | 0
| 1411 | 20 | C | SSMHT0008913 | SS.MH.T0008913 | 32.2477 | -95.304 | M24 | 8966 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7,27 | #VALUE! | [18 empty] | 0
| 1412 | 20 | C | SSMHT0008914 | SS.MH.T0008914 | 32.2477 | -95.3055 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 60 Round | Concrete | 7.69 | 102.8664 | [18 empty] | 0
| 1413 | 20 | B | SSMHT0008915 | SS.MH.T0008915 | 32.2478 | -95.3061 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.32 | 161.0192 | [18 empty] | 0
| 1414 | 20 | C | SSMHT0008916 | SS.MH.T0008916 | 32.2478 | -95.3069 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.92 | 118.3152 | [18 empty] | 0
| 1415 | 20 | B | SSMHT0008917 | SS.MH.T0008917 | 32.2485 | -95.3054 | M24 | 8970 S BROADWAY AVE | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.49 | 125.4744 | [18 empty] | 0
| 1416 | 20 | B | SSMHT0008918 | SS.MH.T0008918 | 32.2492 | -95.3054 | M24 | 8926 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.28 | 160.5168 | [18 empty] | 0
| 1417 | 20 | B | SSMHT0008919 | SS.MH.T0008919 | 32.2492 | -95.3061 | M24 | 8926 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.73 | 115.9288 | [18 empty] | 0
| 1418 | 20 | C | SSMHT0008920 | SS.MH.T0008920 | 32.2491 | -95.3045 | M24 | 8938 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.44 | 112.2864 | [18 empty] | 0
| 1419 | 20 | B | SSMHT0008921 | SS.MH.T0008921 | 32.2509 | -95.3052 | M24 | 8926 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.01 | 157.1256 | [18 empty] | 0
| 1420 | 20 | B | SSMHT0008922 | SS.MH.T0008922 | 32.2509 | -95.3044 | M24 | 8930 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.86 | 117.5616 | [18 empty] | 0
| 1421 | 20 | C | SSMHT0008923 | SS.MH.T0008923 | 32.251 | -95.306 | M24 | 8926 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.62 | 127.1072 | [18 empty] | 0
| 1422 | 20 | B | SSMHT0008924 | SS.MH.T0008924 | 32.2499 | -95.3053 | M24 | 8934 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.64 | 127.3584 | [18 empty] | 0
| 1423 | 20 | B | SSMHT0008925 | SS.MH.T0008925 | 32.2538 | -95.307 | M23 | 172 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.12 | 145.9472 | [18 empty] | 0
| 1424 | 20 | B | SSMHT0008926 | SS.MH.T0008926 | 32.2544 | -95.307 | M23 | 172 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.86 | 92.4416 | [18 empty] | 0
| 1425 | 20 | A | SSMHT0008927 | SS.MH.T0008927 | 32.2555 | -95.307 | M23 | 8668 S BROADWAY AVE | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.62 | 76.8672 | [18 empty] | 0
| 1426 | 20 | D | SSMHT0008928 | SS.MH.T0008928 | 32.2586 | -95.3054 | M23 | 100 CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 7.36 | 98.7216 | 2 | [11 empty] | 2961.648 | [5 empty] | 2961.648 | Rehabilitate
| 1427 | 20 | C | SSMHT0008929 | SS.MH.T0008929 | 32.2586 | -95.3053 | M23 | 314 WILDERWAY | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.44 | 87.1664 | [18 empty] | 0
| 1428 | 20 | C | SSMHT0008930 | SS.MH.T0008930 | 32.2589 | -95.3051 | M23 | 314 WILDER WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.08 | 95.2048 | [18 empty] | 0
| 1429 | 20 | c | SSMHT0008931 | SS.MH.T0008931 | 32.2589 | -95.3037 | M23 | 332 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 11.03 | 144.8168 | [18 empty] | 0
| 1430 | 20 | X-CNL | SSMHT0008932 | SS.MH.T0008932 |  |  | M23 | 172 CENTENNIAL PKWY |  |  |  | Street | Paved - Concrete | Below Grade | [23 empty] | 0
| 1431 | 20 | A | SSMHT0009169 | SS.MH.T0009169 | 32.264 | -95.2899 | N23 | 6566 FURMAN CT | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 14.36 | 186.6416 | [18 empty] | 0
| 1432 | 20 | B | SSMHT0009208 | SS.MH.T0009208 | 32.2748 | -95.2665 | O21 | 2525 ROY RD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.22 | 134.6432 | [18 empty] | 0
| 1433 | 20 | B | SSMHT0009209 | SS.MH.T0009209 | 32.2749 | -95.2666 | O21 | 2525 ROY RD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.92 | 130.8752 | [18 empty] | 0
| 1434 | 20 | B | SSMHT0009250 | SS.MH.T0009250 | 32.2705 | -95.2777 | O22 | 7200 PALUXY DR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 11.87 | 155.3672 | [18 empty] | 0
| 1435 | 20 | C | SSMHT0009251 | SS.MH.T0009251 | 32.2732 | -95.2664 | O21 | 2525 ROY RD | Solid |  | Yes | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.02 | 107.0112 | [18 empty] | 0
| 1436 | 20 | B | SSMHT0009253 | SS.MH.T0009253 | 32.2729 | -95.2664 | O21 | 7234 MORNING MIST DR | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.46 | 112.5376 | [18 empty] | 0
| 1437 | 20 | B | SSMHT0009254 | SS.MH.T0009254 | 32.2705 | -95.2617 | P22 | NONE PARKHILL AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.26 | 110.0256 | [18 empty] | 0
| 1438 | 20 | B | SSMHT0009255 | SS.MH.T0009255 | 32.2702 | -95.2625 | P22 | 2959 GUINN FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.34 | 123.5904 | [18 empty] | 0
| 1439 | 20 | C | SSMHT0009256 | SS.MH.T0009256 | 32.2705 | -95.2637 | O22 | 2857 GUINN FARM RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.4 | 99.224 | [18 empty] | 0
| 1440 | 20 | X-CNL | SSMHT0009290 | SS.MH.T0009290 |  |  | M23 | 8618 S BROADWAY AVE |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1441 | 20 | X-CNL | SSMHT0009473 | SS.MH.T0009473 |  |  | N22 | 8323 EL CERRITO DR. |  |  |  | Driveway | Paved - Asphalt | [24 empty] | 0
| 1442 | 20 | D | SSMHT0009535 | SS.MH.T0009535 | 32.2728 | -95.2902 | N22 | 1009 JEFFERY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.94 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1443 | 20 | D | SSMHT0009536 | SS.MH.T0009536 | 32.2735 | -95.2903 | N21 | 1017 DAVID DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1444 | 20 | D | SSMHT0009537 | SS.MH.T0009537 | 32.2765 | -95.2905 | N21 | 1009 ELAINE DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1445 | 20 | X-CNL | SSMHT0009589 | SS.MH.T0009589 |  |  | M23 | 8204 CROOKED TRL |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1446 | 20 | X-CNL | SSMHT0009590 | SS.MH.T0009590 |  |  | M23 | 8302 CROOKED TRL |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1447 | 20 | X-CNL | SSMHT0009591 | SS.MH.T0009591 | 32.2599 | -95.3102 | M23 | 8105 CROOKED TRL |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1448 | 20 | X-CNL | SSMHT0009592 | SS.MH.T0009592 |  |  | M23 | 8311 CROOKED TRL |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1449 | 20 | B | SSMHT0009593 | SS.MH.T0009593 | 32.2593 | -95.3101 | M23 | 8306 CROOKED TRL | Vented | 2 | No | Yard | Unpaved | Above Grade | 5 | CO 6" | Other | 7.95 | [19 empty] | 0
| 1450 | 20 | D | SSMHT0009687 | SS.MH.T0009687 | 32.2458 | -95.2918 | N24 | 1227 RAINMAKER | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1451 | 20 | X-CNL | SSMHT0009693 | SS.MH.T0009693 |  |  | M23 | 413 W CUMBERLAND RD |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1452 | 20 | A | SSMHT0009694 | SS.MH.T0009694 | 32.2573 | -95.3161 | M23 | 413 CUMBERLAND DR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.82 | 91.9392 | [18 empty] | 0
| 1453 | 20 | D | SSMHT0009740 | SS.MH.T0009740 | 32.2467 | -95.292 | N24 | 1234 DREAMCATCHER | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.21 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1454 | 20 | D | SSMHT0009742 | SS.MH.T0009742 | 32.2637 | -95.299 | N22 | 615 POTOMAC DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.28 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1455 | 20 | D | SSMHT0009748 | SS.MH.T0009748 | 32.271 | -95.2651 | O22 | 2744 GUINN FARMS RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 1456 | 20 | A | SSMHT0009749 | SS.MH.T0009749 | 32.2727 | -95.266 | O22 | 7258 MORNING MIST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13.58 | [19 empty] | 0
| 1457 | 20 | D | SSMHT0009750 | SS.MH.T0009750 | 32.2728 | -95.2661 | O21 | 7252 MORNING MIST DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.24 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1458 | 20 | D | SSMHT0009760 | SS.MH.T0009760 | 32.2401 | -95.2984 | N25 | 525 WINDING BROOK LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.94 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1459 | 20 | D | SSMHT0009761 | SS.MH.T0009761 | 32.2402 | -95.2997 | N25 | 533 SKIPPING STONE LN | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.76 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1460 | 20 | B | SSMHT0009762 | SS.MH.T0009762 | 32.239 | -95.3001 | N25 | 9177 TEAL FLIGHT WAY | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.5 | [19 empty] | 0
| 1461 | 20 | A | SSMHT0009763 | SS.MH.T0009763 | 32.238 | -95.2977 | N25 | 9239 STONEBANK CROSSING | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.5 | [19 empty] | 0
| 1462 | 20 | D | SSMHT0009764 | SS.MH.T0009764 | 32.2538 | -95.2871 | N23 | 1401 CUMBERLAND RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 6.2 | 84.152 | [14 empty] | 280 |  |  |  | 280 | Repair
| 1463 | 20 | B | SSMHT0009792 | SS.MH.T0009792 | 32.2773 | -95.2787 | O21 | 1901 DEERBROOK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.18 | [19 empty] | 0
| 1464 | 20 | B | SSMHT0009793 | SS.MH.T0009793 | 32.2785 | -95.2789 | O21 | NONE E GRANDE BLVD | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 16 | [19 empty] | 0
| 1465 | 20 | X-CNL | SSMHT0009794 | SS.MH.T0009794 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1466 | 20 | D | SSMHT0009805 | SS.MH.T0009805 | 32.2753 | -95.2798 | O21 | 1821 ANGY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.46 | [15 empty] | 280 |  |  |  | 280 | Repair
| 1467 | 20 | D | SSMHT0009806 | SS.MH.T0009806 | 32.2744 | -95.2797 | O21 | 1820 CIRCLE DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.16 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1468 | 20 | C | SSMHT0009808 | SS.MH.T0009808 | 32.2739 | -95.2746 | O21 | 2136 ROY RD | Vented | 2 | No | Drainage Ditch | Unpaved | Below Grade | 1 | Std 48 Round | Other | 9.12 | 120.8272 | [18 empty] | 0
| 1469 | 20 | B | SSMHT0009809 | SS.MH.T0009809 | 32.2677 | -95.2945 | N22 | 8329 EL CERRITO PL. | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 9.34 | [19 empty] | 0
| 1470 | 20 | A | SSMHT0009810 | SS.MH.T0009810 | 32.2672 | -95.2933 | N22 | 8329 GARRETT RD. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.1 | [19 empty] | 0
| 1471 | 20 | D | SSMHT0009812 | SS.MH.T0009812 | 32.2662 | -95.2919 | N22 | 930 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.68 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1472 | 20 | A | SSMHT0009813 | SS.MH.T0009813 | 32.2662 | -95.2924 | N22 | 924 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.22 | [19 empty] | 0
| 1473 | 20 | D | SSMHT0009814 | SS.MH.T0009814 | 32.2649 | -95.2928 | N22 | 6363 OBERLIN CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.02 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1474 | 20 | D | SSMHT0009815 | SS.MH.T0009815 | 32.2661 | -95.2939 | N22 | 836 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1475 | 20 | D | SSMHT0009816 | SS.MH.T0009816 | 32.2621 | -95.2947 | N23 | 6510 ROCHESTER WAY | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1476 | 20 | A | SSMHT0009817 | SS.MH.T0009817 | 32.2628 | -95.2934 | N22 | 8517 CASTLETON WAY. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.48 | [19 empty] | 0
| 1477 | 20 | D | SSMHT0009818 | SS.MH.T0009818 | 32.2641 | -95.2932 | N22 | 6547 WHEATON CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.66 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1478 | 20 | D | SSMHT0009819 | SS.MH.T0009819 | 32.2628 | -95.2931 | N22 | 8523 CASTLETON WAY. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.28 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1479 | 20 | C | SSMHT0009833 | SS.MH.T0009833 | 32.2469 | -95.2899 | N24 | 1239 LUANN LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.78 | [19 empty] | 0
| 1480 | 20 | B | SSMHT0009834 | SS.MH.T0009834 | 32.2469 | -95.2842 | N24 | 1535 LUANN LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.38 | [19 empty] | 0
| 1481 | 20 | D | SSMHT0009835 | SS.MH.T0009835 | 32.2459 | -95.2845 | N24 | 1535 LUANN LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1482 | 20 | B | SSMHT0009836 | SS.MH.T0009836 | 32.2459 | -95.2874 | N24 | 1379 SANTA FE TRL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.62 | [19 empty] | 0
| 1483 | 20 | B | SSMHT0009837 | SS.MH.T0009837 | 32.2459 | -95.2876 | N24 | 1347 SANTA FE TRL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.62 | [19 empty] | 0
| 1484 | 20 | B | SSMHT0009838 | SS.MH.T0009838 | 32.2475 | -95.2835 | N24 | 1612 LEGACY DR | Vented | 2 | No | Field | Unpaved | At Grade |  | CO 6" | Other | 7.76 | [19 empty] | 0
| 1485 | 20 | C | SSMHT0009839 | SS.MH.T0009839 | 32.2529 | -95.2841 | N23 | 1516 CUMBERLAND RD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 3 | CO 6" | Other | 9.82 | [19 empty] | 0
| 1486 | 20 | B | SSMHT0009840 | SS.MH.T0009840 | 32.2546 | -95.2837 | N23 | 1525 WILANA DR | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 13.9 | [19 empty] | 0
| 1487 | 20 | A | SSMHT0009841 | SS.MH.T0009841 | 32.2551 | -95.2837 | N23 | 1534 WILANA DR | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 6.84 | [19 empty] | 0
| 1488 | 20 | B | SSMHT0009842 | SS.MH.T0009842 | 32.2553 | -95.2888 | N23 | NONE WILDER TRL | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 3 | CO 6" | Other | 6.67 | [19 empty] | 0
| 1489 | 20 | D | SSMHT0009843 | SS.MH.T0009843 | 32.2548 | -95.2902 | N23 | 1111 CUMBERLAND RD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other | 16.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1490 | 20 | D | SSMHT0009873 | SS.MH.T0009873 | 32.2384 | -95.2977 | N25 | 9873 STONEBANK CROSSING | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.98 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1491 | 20 | X-CNL | SSMHT0009874 | SS.MH.T0009874 |  |  | N25 | 9326 STONEBANK CROSSING |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1492 | 20 | X-CNL | SSMHT0009875 | SS.MH.T0009875 |  |  | N22 | 8339 GARRETT RD. |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 1493 | 20 | B | SSMHT0009900 | SS.MH.T0009900 | 32.277 | -95.2897 | N21 | 3203 E GRANDE BLVD | Solid |  | Yes | Yard | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 9.5 | 125.6 | [18 empty] | 0
| 1494 | 20 | D | SSMHT0009973 | SS.MH.T0009973 | 32.2583 | -95.3177 | M23 | 704 W CUMBERLAND RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1495 | 20 | X-Buried | SSMHT0010154 | SS.MH.T0010154 | 32.2758 | -95.2904 | N21 | 1012 BETH DR. |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 1496 | 20 | D | SSMHT0010336 | SS.MH.T0010336 | 32.2566 | -95.3151 | M23 | 8436 LAKEWAY DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1497 | 20 | D | SSMHT0010354 | SS.MH.T0010354 | 32.258 | -95.3104 | M23 | 8411 CROOKED TRL | Vented | 2 |  | Driveway | Paved - Concrete | At Grade |  | CO 6" | Other | 5.25 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 1498 | 20 | B | SSMHT0010355 | SS.MH.T0010355 | 32.2576 | -95.3103 | M23 | 8415 CROOKED TRL | Vented | 2 | No | Yard | Unpaved | Below Grade | 1 | CO 6" | Other | 6.1 | [19 empty] | 0
| 1499 | 20 | B | SSMHT0010356 | SS.MH.T0010356 | 32.2568 | -95.3101 | M23 | 8505 CROOKED TRL | Vented | 2 | No | Yard | Unpaved | Below Grade | 1 | CO 6" | Other | 5.84 | [19 empty] | 0
| 1500 | 20 | D | SSMHT0010357 | SS.MH.T0010357 | 32.2568 | -95.3094 | M23 | 8389 S BROADWAY AVE | Vented | 2 |  | Trees/Woods | Unpaved | Above Grade | 1 | CO 6" | Other | 5.76 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1501 | 20 | A | SSMHT0010363 | SS.MH.T0010363 | 32.2743 | -95.2673 | O21 | 5801 THOMPSON PL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.92 | [19 empty] | 0
| 1502 | 20 | D | SSMHT0010364 | SS.MH.T0010364 | 32.2736 | -95.2681 | O21 | 5847 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.22 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1503 | 20 | B | SSMHT0010365 | SS.MH.T0010365 | 32.2717 | -95.2691 | O22 | 5939 GRACE AVE | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 7.4 | [19 empty] | 0
| 1504 | 20 | A | SSMHT0010366 | SS.MH.T0010366 | 32.2725 | -95.2679 | O22 | 2512 GUINN FARMS RD | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.83 | [19 empty] | 0
| 1505 | 20 | A | SSMHT0010367 | SS.MH.T0010367 | 32.2722 | -95.2677 | O22 | 2516 GUINN FARMS RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.58 | [19 empty] | 0
| 1506 | 20 | A | SSMHT0010368 | SS.MH.T0010368 | 32.2712 | -95.2678 | O22 | 2508 MEADOWGLEN CT | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8 | [19 empty] | 0
| 1507 | 20 | A | SSMHT0010369 | SS.MH.T0010369 | 32.2702 | -95.2674 | O22 | 2563 MEADOWLAND CT | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.98 | [19 empty] | 0
| 1508 | 20 | D | SSMHT0010370 | SS.MH.T0010370 | 32.2703 | -95.2677 | O22 | 2559 MEADOWLAND CT | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.79 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1509 | 20 | D | SSMHT0010377 | SS.MH.T0010377 | 32.2755 | -95.2697 | O21 | 2448 ROY RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.72 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1510 | 20 | D | SSMHT0010394 | SS.MH.T0010394 | 32.2567 | -95.3046 | M23 | 501 CUMBERLAND RD | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 20.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1511 | 20 | D | SSMHT0010395 | SS.MH.T0010395 | 32.2582 | -95.2923 | N23 | 1127 WILDER WAY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1512 | 20 | X-CNL | SSMHT0010396 | SS.MH.T0010396 |  |  | N23 | 1127 WILDER WAY |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1513 | 20 | X-CNL | SSMHT0010397 | SS.MH.T0010397 |  |  | M23 | 7918 S BROADWAY AVE |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1514 | 20 | X-CNL | SSMHT0010398 | SS.MH.T0010398 |  |  | N23 | 8524 RADCLIFFE DR |  |  |  | Road Shoulder | Unpaved | Below Grade |  | CO 6" | [21 empty] | 0
| 1515 | 20 | D | SSMHT0010399 | SS.MH.T0010399 | 32.2618 | -95.2998 | N23 | 8524 RADCLIFFE DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other | 7.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1516 | 20 | X-CNL | SSMHT0010400 | SS.MH.T0010400 |  |  | N22 | 8502 AUBURN DR |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1517 | 20 | D | SSMHT0010442 | SS.MH.T0010442 | 32.2662 | -95.2952 | N22 | 819 MARQUETTE LANE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1518 | 20 | D | SSMHT0010443 | SS.MH.T0010443 | 32.2661 | -95.2964 | N22 | 803 MARQUETTE LANE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.98 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1519 | 20 | D | SSMHT0010444 | SS.MH.T0010444 | 32.2644 | -95.2952 | N22 | 820 NEWBURY CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.46 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1520 | 20 | D | SSMHT0010445 | SS.MH.T0010445 | 32.2609 | -95.2946 | N23 | 6527 ROCHESTER WAY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.34 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1521 | 20 | D | SSMHT0010446 | SS.MH.T0010446 | 32.2641 | -95.2921 | N22 | 6522 EMORY CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.18 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1522 | 20 | X-CNL | SSMHT0010447 | SS.MH.T0010447 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1523 | 20 | X-CNL | SSMHT0010448 | SS.MH.T0010448 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1524 | 20 | B | SSMHT0010449 | SS.MH.T0010449 | 32.2774 | -95.2755 | O21 | 2136 DEERBROOK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Concrete | 7.4 | [19 empty] | 0
| 1525 | 20 | C | SSMHT0010450 | SS.MH.T0010450 | 32.2774 | -95.2753 | O21 | 2147 DEERBROOK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.52 | [19 empty] | 0
| 1526 | 20 | A | SSMHT0010451 | SS.MH.T0010451 | 32.2781 | -95.2823 | N21 | 1510 E GRANDE BLVD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5 | [19 empty] | 0
| 1527 | 20 | X-CNL | SSMHT0010452 | SS.MH.T0010452 |  |  | O21 | 1722 SUSAN DR |  |  |  | Yard | Unpaved | Below Grade |  | Std 48 Round | [21 empty] | 0
| 1528 | 20 | D | SSMHT0010456 | SS.MH.T0010456 | 32.2764 | -95.2613 | P21 | 6525 RHONES QUARTER RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 2.86 | 42.2016 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
| 1529 | 20 | B | SSMHT0010461 | SS.MH.T0010461 | 32.275 | -95.2767 | O21 | 2025 NORTH DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 9.39 | 124.2184 | [18 empty] | 0
| 1530 | 20 | A | SSMHT0010462 | SS.MH.T0010462 | 32.275 | -95.2764 | O21 | 2037 NORTH DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.98 | [19 empty] | 0
| 1531 | 20 | B | SSMHT0010463 | SS.MH.T0010463 | 32.2743 | -95.2741 | O21 | 6811 MANDY LN | Vented | 2 | No | Drainage Ditch | Unpaved | Below Grade | 1 | CO 6" | Other | 3.78 | [19 empty] | 0
| 1532 | 20 | D | SSMHT0010464 | SS.MH.T0010464 | 32.2711 | -95.297 | N22 | 707 JEFF DAVIS DR | Vented |  | No | Road Shoulder | Unpaved | Below Grade | 4 | CO 6" | Other | 13.82 |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
| 1533 | 20 | A | SSMHT0010465 | SS.MH.T0010465 | 32.2711 | -95.2871 | N22 | 1315 JEFF DAVIS DR | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 9.16 | [19 empty] | 0
| 1534 | 20 | A | SSMHT0010466 | SS.MH.T0010466 | 32.2712 | -95.2865 | N22 | 1405 JEFF DAVIS DR | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 9.33 | [19 empty] | 0
| 1535 | 20 | D | SSMHT0010467 | SS.MH.T0010467 | 32.273 | -95.2819 | O22 | 1616 JEB STUART DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1536 | 20 | D | SSMHT0010468 | SS.MH.T0010468 | 32.2727 | -95.2817 | O22 | 1630 JEB STUART DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 5 | CO 6" | Other | 11.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1537 | 20 | B | SSMHT0010470 | SS.MH.T0010470 | 32.2732 | -95.2796 | O21 | 7015 PALUXY DR | Vented | 2 |  | Road Shoulder | Unpaved | Above Grade | 4 | CO 6" | Other | 10 | [19 empty] | 0
| 1538 | 20 | D | SSMHT0010471 | SS.MH.T0010471 | 32.2738 | -95.2736 | O21 | 2211 ROY RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Other | 7.92 | [15 empty] | 280 |  |  |  | 280 | Repair
| 1539 | 20 | C | SSMHT0010472 | SS.MH.T0010472 | 32.275 | -95.2635 | O21 | 2816 ROY RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | CO 6" | Other | 6.84 | [19 empty] | 0
| 1540 | 20 | D | SSMHT0010476 | SS.MH.T0010476 | 32.2642 | -95.2909 | N22 | 1197 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1541 | 20 | D | SSMHT0010477 | SS.MH.T0010477 | 32.2627 | -95.2903 | N22 | 6596 FURMAN CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.82 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1542 | 20 | D | SSMHT0010478 | SS.MH.T0010478 | 32.2645 | -95.2908 | N22 | 1190 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 16.96 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1543 | 20 | D | SSMHT0010479 | SS.MH.T0010479 | 32.2649 | -95.2917 | N22 | 6368 MANCHESTER CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1544 | 20 | A | SSMHT0010480 | SS.MH.T0010480 | 32.2525 | -95.2861 | N23 | 1467 OLD CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.66 | [19 empty] | 0
| 1545 | 20 | C | SSMHT0010481 | SS.MH.T0010481 | 32.2493 | -95.2849 | N24 | 9164 COUNTY RD 1165 | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.26 | [19 empty] | 0
| 1546 | 20 | A | SSMHT0010482 | SS.MH.T0010482 | 32.2491 | -95.2851 | N24 | 9164 OLD HICKORY RD | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.58 | [19 empty] | 0
| 1547 | 20 | D | SSMHT0010486 | SS.MH.T0010486 | 32.25 | -95.281 | O24 | 9102 STONE CREEK TRL | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.7 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 1548 | 20 | B | SSMHT0010487 | SS.MH.T0010487 | 32.2488 | -95.281 | O24 | 1625 WILLOW BEND | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.6 | [19 empty] | 0
| 1549 | 20 | D | SSMHT0010488 | SS.MH.T0010488 | 32.2488 | -95.2813 | O24 | 1625 WILLOW BEND | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.74 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1550 | 20 | B | SSMHT0010495 | SS.MH.T0010495 | 32.2479 | -95.2814 | O24 | 1649 SKIDMORE LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.59 | [19 empty] | 0
| 1551 | 20 | C | SSMHT0010496 | SS.MH.T0010496 | 32.2479 | -95.2818 | O24 | 1616 SKIDMORE LN | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 7.08 | [19 empty] | 0
| 1552 | 20 | C | SSMHT0010497 | SS.MH.T0010497 | 32.2481 | -95.279 | O24 | 1710 SKIDMORE LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | [20 empty] | 0
| 1553 | 20 | A | SSMHT0010498 | SS.MH.T0010498 | 32.2483 | -95.2863 | N24 | 1445 OLD HICKORY RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.96 | [19 empty] | 0
| 1554 | 20 | A | SSMHT0010499 | SS.MH.T0010499 | 32.2479 | -95.288 | N24 | 1347 OLD HICKORY RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.76 | [19 empty] | 0
| 1555 | 20 | A | SSMHT0010500 | SS.MH.T0010500 | 32.2479 | -95.2881 | N24 | 1327 OLD HICKORY RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.48 | [19 empty] | 0
| 1556 | 20 | A | SSMHT0010501 | SS.MH.T0010501 | 32.2489 | -95.289 | N24 | 1235 BUFFALO TRL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.34 | [19 empty] | 0
| 1557 | 20 | A | SSMHT0010502 | SS.MH.T0010502 | 32.2489 | -95.2888 | N24 | 1245BUFFALO TRL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.18 | [19 empty] | 0
| 1558 | 20 | D | SSMHT0010503 | SS.MH.T0010503 | 32.2469 | -95.2901 | N24 | 1221 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13.36 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1559 | 20 | D | SSMHT0010515 | SS.MH.T0010515 | 32.2477 | -95.3035 | M24 | 8966 S BROADWAY AVE | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 6.84 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1560 | 20 | D | SSMHT0010516 | SS.MH.T0010516 | 32.2576 | -95.3053 | M23 | NONE WILDER WAY | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | CO 6" | Other | 6.03 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1561 | 20 | X-CNL | SSMHT0010517 | SS.MH.T0010517 |  |  | M23 | 8668 S BROADWAY AVE |  |  |  | Parking Lot | Paved - Concrete | Below Grade | [23 empty] | 0
| 1562 | 20 | A | SSMHT0010533 | SS.MH.T0010533 | 32.2743 | -95.2665 | O21 | 2525 ROY RD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 7.78 | [19 empty] | 0
| 1563 | 20 | C | SSMHT0013024 | SS.MH.T0013024 | 32.2614 | -95.3103 | M23 | 7925 S BROADWAY AVE | Solid |  | Yes | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.63 | 89.5528 | [18 empty] | 0
| 1564 | 20 | B | SSMHT0013025 | SS.MH.T0013025 | 32.261 | -95.3102 | M23 | 7925 S BROADWAY AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.27 | 72.4712 | [18 empty] | 0
| 1565 | 20 | B | SSMHT0013026 | SS.MH.T0013026 | 32.2609 | -95.31 | M23 | 7925 S BROADWAY AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.78 | 78.8768 | [18 empty] | 0
| 1566 | 20 | X-Buried | SSMHT0013027 | SS.MH.T0013027 | 32.2609 | -95.3096 | M23 | 7925 S BROADWAY AVE |  |  |  | Parking Lot | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1567 | 20 | B | SSMHT0013028 | SS.MH.T0013028 | 32.2612 | -95.3095 | M23 | 7925 S BROADWAY AVE | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.58 | 88.9248 | [18 empty] | 0
| 1568 | 20 | B | SSMHT0013092 | SS.MH.T0013092 | 32.275 | -95.2897 | N21 | 8148 GREER DR. | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0
| 1569 | 20 | B | SSMHT0013093 | SS.MH.T0013093 | 32.275 | -95.2905 | N21 | 921 JOEL DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.42 | 99.4752 | [18 empty] | 0
| 1570 | 20 | A | SSMHT0013095 | SS.MH.T0013095 | 32.2664 | -95.2758 | O22 | 2120 BRANDON DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.69 | 115.4264 | [18 empty] | 0
| 1571 | 20 | D | SSMHT0013349 | SS.MH.T0013349 | 32.2397 | -95.2966 | N25 | 9210 STONEBANK CROSSING | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.96 | 118.8176 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair
| 1572 | 20 | C | SSMHT0013357 | SS.MH.T0013357 | 32.2363 | -95.2983 | N25 | 9344 STONEBANK CROSSING | Solid |  | No | Field | Unpaved | Above Grade | 35 | Std 48 Round | Concrete | 17.11 | 221.1816 | [18 empty] | 0
| 1573 | 20 | A | SSMHT0013368 | SS.MH.T0013368 | 32.2643 | -95.2791 | O22 | 8462 PALUXY DR | Solid |  | Yes | Drainage Ditch | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 12.02 | 157.2512 | [18 empty] | 0
| 1574 | 20 | A | SSMHT0013369 | SS.MH.T0013369 | 32.2656 | -95.2793 | O22 | 8332 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 10.49 | 138.0344 | [18 empty] | 0
| 1575 | 20 | B | SSMHT0013371 | SS.MH.T0013371 | 32.2695 | -95.2719 | O22 | 6047 GRACE AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 7.36 | 98.7216 | [18 empty] | 0
| 1576 | 20 | B | SSMHT0013375 | SS.MH.T0013375 | 32.2664 | -95.2793 | O22 | 8332 PALUXY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.16 | 83.6496 | [18 empty] | 0
| 1577 | 20 | D | SSMHT0013489 | SS.MH.T0013489 | 32.2518 | -95.2841 | N23 | 9010 OLD HICKORY RD | Solid |  | No | Creek | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 5.3 | 72.848 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 | 900 |  |  | 2555 | Repair
| 1578 | 20 | B | SSMHT0013675 | SS.MH.T0013675 | 32.2743 | -95.2905 | N21 | 921 PAM DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.42 | 112.0352 | [18 empty] | 0
| 1579 | 20 | C | SSMHT0013681 | SS.MH.T0013681 | 32.2781 | -95.2825 | N21 | 1510 E GRANDE BLVD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.5 | 100.48 | [18 empty] | 0
| 1580 | 20 | D | SSMHT0013779 | SS.MH.T0013779 | 32.2367 | -95.2997 | N25 | 9374 STONEBANK CROSSING | Solid |  | Yes | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.84 | 129.8704 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
| 1581 | 20 | B | SSMHT0013780 | SS.MH.T0013780 | 32.2371 | -95.2997 | N25 | 9374 TEAL FLIGHT WAY | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.72 | 128.3632 | [18 empty] | 0
| 1582 | 20 | B | SSMHT0013781 | SS.MH.T0013781 | 32.2371 | -95.2992 | N25 | 9356 STONE BANK CROSSING | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.82 | 117.0592 | [18 empty] | 0
| 1583 | 20 | B | SSMHT0013782 | SS.MH.T0013782 | 32.2372 | -95.2989 | N25 | 9344 STONEBANK CROSSING | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.92 | 130.8752 | [18 empty] | 0
| 1584 | 20 | B | SSMHT0013783 | SS.MH.T0013783 | 32.2375 | -95.2991 | N25 | 9180 EDDY WATER CIR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.55 | 126.228 | [18 empty] | 0
| 1585 | 20 | B | SSMHT0013784 | SS.MH.T0013784 | 32.2383 | -95.2991 | N25 | 9123 EDDY WATER CIR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.29 | 122.9624 | [18 empty] | 0
| 1586 | 20 | B | SSMHT0013785 | SS.MH.T0013785 | 32.2374 | -95.2985 | N25 | 9321 STONEBANK CROSSING | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.36 | 123.8416 | [18 empty] | 0
| 1587 | 20 | B | SSMHT0013786 | SS.MH.T0013786 | 32.2375 | -95.2984 | N25 | 9321 STONEBANK CROSSING | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.7 | [19 empty] | 0
| 1588 | 20 | B | SSMHT0013787 | SS.MH.T0013787 | 32.2371 | -95.3004 | N25 | 9390 TEAL FLIGHT WAY | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 14.96 | 194.1776 | [18 empty] | 0
| 1589 | 20 | B | SSMHT0013788 | SS.MH.T0013788 | 32.2371 | -95.3001 | N25 | 9390 TEAL FLIGHT WAY | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.86 | 130.1216 | [18 empty] | 0
| 1590 | 20 | B | SSMHT0013789 | SS.MH.T0013789 | 32.2381 | -95.3001 | N25 | 9140 TEAL FLIGHT WAY | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.38 | 136.6528 | [18 empty] | 0
| 1591 | 20 | A | SSMHT0013790 | SS.MH.T0013790 | 32.2389 | -95.3 | N25 | 9153 TEAL FLIGHT WAY | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 14.36 | [19 empty] | 0
| 1592 | 20 | A | SSMHT0013791 | SS.MH.T0013791 | 32.2383 | -95.2986 | N25 | 9114 EDDY WATER CIR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.25 | [19 empty] | 0
| 1593 | 20 | D | SSMHT0013805 | SS.MH.T0013805 | 32.2704 | -95.2974 | N22 | 739 CAMBRIDGE BEND CIR | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 5.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1594 | 20 | D | SSMHT0013806 | SS.MH.T0013806 | 32.2708 | -95.2987 | N22 | 627 CAMBRIDGE BEND CIR | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 1595 | 20 | D | SSMHT0013807 | SS.MH.T0013807 | 32.2712 | -95.2981 | N22 | 617 CAMBRIDGE BEND CIR | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1596 | 20 | B | SSMHT0013808 | SS.MH.T0013808 | 32.2705 | -95.2979 | N22 | 749 CAMBRIDGE BEND CIR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.92 | 105.7552 | [18 empty] | 0
| 1597 | 20 | C | SSMHT0013809 | SS.MH.T0013809 | 32.2704 | -95.2979 | N22 | 727 CAMBRIDGE BEND CIR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0
| 1598 | 20 | C | SSMHT0013810 | SS.MH.T0013810 | 32.2703 | -95.2987 | N22 | 703 CAMBRIDGE BEND CIR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.96 | 131.3776 | [18 empty] | 0
| 1599 | 20 | C | SSMHT0013811 | SS.MH.T0013811 | 32.2707 | -95.2988 | N22 | 631 CAMBRIDGE BEND CIR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.34 | 98.4704 | [18 empty] | 0
| 1600 | 20 | B | SSMHT0013812 | SS.MH.T0013812 | 32.2709 | -95.2983 | N22 | 613 CAMBRIDGE BEND CIR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.94 | 106.0064 | [18 empty] | 0
| 1601 | 20 | B | SSMHT0013813 | SS.MH.T0013813 | 32.271 | -95.2983 | N22 | 621 CAMBRIDGE BEND CIR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.96 | 106.2576 | [18 empty] | 0
| 1602 | 20 | X-CNL | SSMHT0013814 | SS.MH.T0013814 |  |  | N22 | 647 CAMBRIDGE BEND CIR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1603 | 20 | B | SSMHT0013937 | SS.MH.T0013937 | 32.2664 | -95.2769 | O22 | 2102 BRANDON DR | Vented |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 9 | 119.32 | [18 empty] | 0
| 1604 | 20 | X-CNO | SSMHT0013989 | SS.MH.T0013989 | 32.2516 | -95.2903 | N23 | 9285 CHISHOLM TRL | Solid |  |  | Yard | Unpaved | Above Grade | 4 | [22 empty] | 0
| 1605 | 20 | A | SSMHT0014132 | SS.MH.T0014132 | 32.2614 | -95.3096 | M23 | 7925 S BROADWAY AVE | Vented |  |  | Parking Lot | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.34 | [19 empty] | 0
| 1606 | 20 | B | SSMHT0014401 | SS.MH.T0014401 | 32.2385 | -95.3047 | N25 | 9025 LONGBRANCH | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.83 | 129.7448 | [18 empty] | 0
| 1607 | 20 | B | SSMHT0014402 | SS.MH.T0014402 | 32.2391 | -95.3047 | N25 | 500 BLK MARSH FARM RD | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 13.92 | 181.1152 | [18 empty] | 0
| 1608 | 20 | X-CNL | SSMHT0014403 | SS.MH.T0014403 |  |  | N25 | 9075 LONG BRANCH |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1609 | 20 | B | SSMHT0014404 | SS.MH.T0014404 | 32.2377 | -95.3047 | N25 | 9075 LONGBRANCH | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.46 | 137.6576 | [18 empty] | 0
| 1610 | 20 | B | SSMHT0014405 | SS.MH.T0014405 | 32.2377 | -95.3036 | N25 | NONE LONGBRANCH | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.52 | 138.4112 | [18 empty] | 0
| 1611 | 20 | X-Buried | SSMHT0014406 | SS.MH.T0014406 | 32.2377 | -95.3029 | M25 | 9100 BLK LONGBRANCH |  |  |  | Street | Paved - Asphalt | Below Grade | 1 | [22 empty] | 0
| 1612 | 20 | C | SSMHT0014407 | SS.MH.T0014407 | 32.2376 | -95.3024 | N25 | 9163 LONG BRANCH | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.27 | 135.2712 | [18 empty] | 0
| 1613 | 20 | B | SSMHT0014408 | SS.MH.T0014408 | 32.2376 | -95.3021 | N25 | 9163 LONGBRANCH | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.47 | 125.2232 | [18 empty] | 0
| 1614 | 20 | B | SSMHT0014409 | SS.MH.T0014409 | 32.2378 | -95.3015 | N25 | 551 MARCH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.64 | 177.5984 | [18 empty] | 0
| 1615 | 20 | B | SSMHT0014410 | SS.MH.T0014410 | 32.2375 | -95.3013 | N25 | 700 MARSH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.99 | 106.6344 | [18 empty] | 0
| 1616 | 20 | C | SSMHT0014411 | SS.MH.T0014411 | 32.2372 | -95.301 | N25 | 700 MARSH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.28 | 135.3968 | [18 empty] | 0
| 1617 | 20 | C | SSMHT0014412 | SS.MH.T0014412 | 32.237 | -95.3007 | N25 | 700 BLK MARSH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.22 | 147.2032 | [18 empty] | 0
| 1618 | 20 | B | SSMHT0014413 | SS.MH.T0014413 | 32.2381 | -95.3029 | N25 | 9157 CAVE BRANCH COVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.24 | 122.3344 | [18 empty] | 0
| 1619 | 20 | B | SSMHT0014414 | SS.MH.T0014414 | 32.2385 | -95.3041 | N25 | 9050 SHALLOH CV | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.4 | [19 empty] | 0
| 1620 | 20 | A | SSMHT0014415 | SS.MH.T0014415 | 32.2386 | -95.3031 | N25 | 9169 CAVE BRANCH COVE | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 23 | [19 empty] | 0
| 1621 | 20 | B | SSMHT0014461 | SS.MH.T0014461 | 32.2454 | -95.2831 | N24 | 1527 SKIDMORE LN | Solid |  | No | Field | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 9.39 | 124.2184 | [18 empty] | 0
| 1622 | 20 | A | SSMHT0014462 | SS.MH.T0014462 | 32.2457 | -95.2824 | O24 | 1600 CENTENNIAL PKWY | Solid |  | No | Field | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 5.3 | 72.848 | [18 empty] | 0
| 1623 | 20 | B | SSMHT0014463 | SS.MH.T0014463 | 32.246 | -95.2816 | O24 | 1600 CENTENNIAL PKWY | Solid |  | No | Field | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 6.82 | 91.9392 | [18 empty] | 0
| 1624 | 20 | C | SSMHT0014464 | SS.MH.T0014464 | 32.2469 | -95.2802 | O24 | 1600 CENTENNIAL PKWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12 | 157 | [18 empty] | 0
| 1625 | 20 | C | SSMHT0014465 | SS.MH.T0014465 | 32.2471 | -95.2799 | O24 | 1676 LEGACY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.94 | 156.2464 | [18 empty] | 0
| 1626 | 20 | B | SSMHT0014466 | SS.MH.T0014466 | 32.2476 | -95.2794 | O24 | 1700BLK CENTENNIAL PWKY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.28 | 185.6368 | [18 empty] | 0
| 1627 | 20 | B | SSMHT0014467 | SS.MH.T0014467 | 32.2481 | -95.2787 | O24 | 1700BLK CENTENNIAL PKWY | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 15.47 | 200.5832 | [18 empty] | 0
| 1628 | 20 | B | SSMHT0014468 | SS.MH.T0014468 | 32.2471 | -95.2803 | O24 | 1673 LEGACY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.88 | 142.9328 | [18 empty] | 0
| 1629 | 20 | D | SSMHT0014469 | SS.MH.T0014469 | 32.2471 | -95.2813 | O24 | 1653 LEGACY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.73 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1630 | 20 | D | SSMHT0014470 | SS.MH.T0014470 | 32.2471 | -95.2815 | O24 | 1649 LEGACY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.24 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1631 | 20 | B | SSMHT0014471 | SS.MH.T0014471 | 32.2471 | -95.2822 | O24 | 1637 LEGACY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 1632 | 20 | A | SSMHT0014472 | SS.MH.T0014472 | 32.2471 | -95.2833 | N24 | 1613 LEGACY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.42 | 112.0352 | [18 empty] | 0
| 1633 | 20 | B | SSMHT0014473 | SS.MH.T0014473 | 32.2471 | -95.2836 | N24 | 1613 LEGACY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.16 | 108.7696 | [18 empty] | 0
| 1634 | 20 | D | SSMHT0014482 | SS.MH.T0014482 | 32.2568 | -95.3199 | M23 | 620 W CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 60 Round | Concrete | 16.06 | 207.9936 | 2 | [11 empty] | 6239.808 | [5 empty] | 6239.808 | Rehabilitate
| 1635 | 20 | C | SSMHT0014545 | SS.MH.T0014545 | 32.267 | -95.2957 | N22 | 304 CAMBRIDGE COVE. | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.48 | 75.1088 | [18 empty] | 0
| 1636 | 20 | X-CNL | SSMHT0014546 | SS.MH.T0014546 |  |  | N22 | 701 CAMBRIDGE COVE. |  |  |  | Street | Paved - Concrete | [24 empty] | 0
| 1637 | 20 | B | SSMHT0014547 | SS.MH.T0014547 | 32.2634 | -95.2968 | N22 | 8454 WILKEN PLAZA | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.97 | 106.3832 | [18 empty] | 0
| 1638 | 20 | A | SSMHT0014548 | SS.MH.T0014548 | 32.2642 | -95.2968 | N22 | 8434 WILKEN PLAZA | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.7 | 77.872 | [18 empty] | 0
| 1639 | 20 | B | SSMHT0014583 | SS.MH.T0014583 | 32.2655 | -95.2674 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 19.72 | 253.9632 | [18 empty] | 0
| 1640 | 20 | B | SSMHT0014584 | SS.MH.T0014584 | 32.2664 | -95.268 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 15.76 | 204.2256 | [18 empty] | 0
| 1641 | 20 | A | SSMHT0014585 | SS.MH.T0014585 | 32.2675 | -95.268 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 20.56 | 264.5136 | [18 empty] | 0
| 1642 | 20 | D | SSMHT0014586 | SS.MH.T0014586 | 32.2687 | -95.2632 | O22 | 14600 COUNTY RD 2191 | Solid |  | Yes | Yard | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 19.24 | 247.9344 | 2 | [11 empty] | 7438.032 | [5 empty] | 7438.032 | Rehabilitate
| 1643 | 20 | B | SSMHT0014587 | SS.MH.T0014587 | 32.2685 | -95.2681 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.52 | 138.4112 | [18 empty] | 0
| 1644 | 20 | A | SSMHT0014588 | SS.MH.T0014588 | 32.2688 | -95.2681 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 9.94 | 131.1264 | [18 empty] | 0
| 1645 | 20 | D | SSMHT0014589 | SS.MH.T0014589 | 32.2688 | -95.2682 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 9.94 | 131.1264 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
| 1646 | 20 | A | SSMHT0014590 | SS.MH.T0014590 | 32.2785 | -95.2909 | N21 | 3902 E GRANDE BLVD | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 12.4 | [19 empty] | 0
| 1647 | 20 | B | SSMHT0014591 | SS.MH.T0014591 | 32.2783 | -95.2902 | N21 | 3502 E GRANDE BLVD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.14 | 108.5184 | [18 empty] | 0
| 1648 | 20 | B | SSMHT0014592 | SS.MH.T0014592 | 32.2779 | -95.2898 | N21 | 3203 E GRANDE BLVD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.58 | 114.0448 | [18 empty] | 0
| 1649 | 20 | B | SSMHT0014593 | SS.MH.T0014593 | 32.2773 | -95.2896 | N21 | 1016 ELAINE DR. | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0
| 1650 | 20 | B | SSMHT0014594 | SS.MH.T0014594 | 32.2773 | -95.2898 | N21 | 3203 E GRANDE BLVD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.78 | 116.5568 | [18 empty] | 0
| 1651 | 20 | B | SSMHT0014595 | SS.MH.T0014595 | 32.277 | -95.2898 | N21 | 3203 E GRANDE BLVD | Solid |  | Yes | Yard | Unpaved | Below Grade | 7 | Std 48 Round | Concrete | 8.98 | 119.0688 | [18 empty] | 0
| 1652 | 20 | D | SSMHT0014596 | SS.MH.T0014596 | 32.2773 | -95.2902 | N21 | 3203 E GRANDE BLVD | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
| 1653 | 20 | C | SSMHT0014597 | SS.MH.T0014597 | 32.2676 | -95.2629 | P22 | 14600 OSCAR BURKETT RD | Solid |  | Yes | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.04 | 132.3824 | [18 empty] | 0
| 1654 | 20 | C | SSMHT0014598 | SS.MH.T0014598 | 32.2687 | -95.2632 | O22 | 14600 COUNTY RD 2191 | Solid |  | Yes | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 10.16 | 133.8896 | [18 empty] | 0
| 1655 | 20 | B | SSMHT0014599 | SS.MH.T0014599 | 32.2687 | -95.2629 | P22 | 14600 COUNTY RD 2191 | Solid |  | Yes | Field | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 10.09 | 133.0104 | [18 empty] | 0
| 1656 | 20 | B | SSMHT0014600 | SS.MH.T0014600 | 32.2682 | -95.2629 | P22 | 14584 COUNTY RD 2191 | Solid |  | Yes | Field | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 10.9 | 143.184 | [18 empty] | 0
| 1657 | 20 | C | SSMHT0014601 | SS.MH.T0014601 | 32.2677 | -95.2622 | P22 | 14584 COUNTY RD 2191 | None |  |  | Field | Unpaved | Above Grade | 3 | CO 6" | PVC | 15.58 | [19 empty] | 0
| 1658 | 20 | C | SSMHT0014612 | SS.MH.T0014612 | 32.2784 | -95.2754 | O21 | NONE E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.94 | 118.5664 | [18 empty] | 0
| 1659 | 20 | X-CNL | SSMHT0014613 | SS.MH.T0014613 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1660 | 20 | B | SSMHT0014614 | SS.MH.T0014614 | 32.2786 | -95.2739 | O21 | NONE E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 19.51 | 251.3256 | [18 empty] | 0
| 1661 | 20 | B | SSMHT0014615 | SS.MH.T0014615 | 32.2786 | -95.2731 | O21 | NONE E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 20.45 | 263.132 | [18 empty] | 0
| 1662 | 20 | C | SSMHT0014616 | SS.MH.T0014616 | 32.2786 | -95.2718 | O21 | NONE E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 16.94 | 219.0464 | [18 empty] | 0
| 1663 | 20 | D | SSMHT0014617 | SS.MH.T0014617 | 32.2786 | -95.2705 | O21 | NONE GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 16.1 | 208.496 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 1664 | 20 | C | SSMHT0014618 | SS.MH.T0014618 | 32.2786 | -95.2692 | O21 | NONE GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 15.4 | 199.704 | [18 empty] | 0
| 1665 | 20 | C | SSMHT0014619 | SS.MH.T0014619 | 32.2786 | -95.2678 | O21 | NONE E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 19.87 | 255.8472 | [18 empty] | 0
| 1666 | 20 | B | SSMHT0014620 | SS.MH.T0014620 | 32.2786 | -95.2667 | O21 | NONE E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 14.19 | 184.5064 | [18 empty] | 0
| 1667 | 20 | X-CNL | SSMHT0014633 | SS.MH.T0014633 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1668 | 20 | X-CNL | SSMHT0014634 | SS.MH.T0014634 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1669 | 20 | A | SSMHT0014635 | SS.MH.T0014635 | 32.279 | -95.2678 | O21 | NONE E GRANDE BLVD | Vented | 2 |  | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 18.8 | [19 empty] | 0
| 1670 | 20 | X-CNL | SSMHT0014637 | SS.MH.T0014637 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1671 | 20 | X-CNL | SSMHT0014638 | SS.MH.T0014638 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1672 | 20 | X-CNL | SSMHT0014639 | SS.MH.T0014639 |  |  | O21 | NONE E GRANDE BLVD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1673 | 20 | B | SSMHT0014699 | SS.MH.T0014699 | 32.2707 | -95.2643 | O22 | 2835 GUINN FARMS | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | [20 empty] | 0
| 1674 | 20 | B | SSMHT0014846 | SS.MH.T0014846 | 32.2696 | -95.3012 | N22 | 8227 PURDUE DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6 | 81.64 | [18 empty] | 0
| 1675 | 20 | D | SSMHT0015235 | SS.MH.T0015235 | 32.2441 | -95.2914 | N24 | NONE COVENTRY PKWY | Solid |  | No | Yard | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 13.51 | 175.9656 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 1676 | 20 | A | SSMHT0015420 | SS.MH.T0015420 | 32.2757 | -95.2779 | O21 | 1906 NORTH DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 10.4 | 136.904 | [18 empty] | 0
| 1677 | 20 | B | SSMHT0015423 | SS.MH.T0015423 | 32.2479 | -95.3025 | N24 | NONE CENTENNIAL PKWY | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.44 | 112.2864 | [18 empty] | 0
| 1678 | 20 | B | SSMHT0015425 | SS.MH.T0015425 | 32.2739 | -95.2728 | O21 | 2211 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.98 | 131.6288 | [18 empty] | 0
| 1679 | 20 | B | SSMHT0015427 | SS.MH.T0015427 | 32.2732 | -95.2665 | O21 | 2525 ROY RD | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 6.84 | 92.1904 | [18 empty] | 0
| 1680 | 20 | A | SSMHT0015428 | SS.MH.T0015428 | 32.2737 | -95.2665 | O21 | 2448 ROY RD | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 9.4 | [19 empty] | 0
| 1681 | 20 | B | SSMHT0015429 | SS.MH.T0015429 | 32.2732 | -95.2659 | O21 | 2525 ROY RD | Solid |  | Yes | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.76 | 141.4256 | [18 empty] | 0
| 1682 | 20 | A | SSMHT0015430 | SS.MH.T0015430 | 32.2737 | -95.2659 | O21 | 2525 ROY RD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 12.36 | [19 empty] | 0
| 1683 | 20 | B | SSMHT0015431 | SS.MH.T0015431 | 32.2779 | -95.2809 | O21 | 6435 PALUXY DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 6.92 | 93.1952 | [18 empty] | 0
| 1684 | 20 | B | SSMHT0015435 | SS.MH.T0015435 | 32.2781 | -95.2809 | O21 | 6393 PALUXY DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.32 | 110.7792 | [18 empty] | 0
| 1685 | 20 | C | SSMHT0015441 | SS.MH.T0015441 | 32.2785 | -95.2809 | O21 | 6351 PALUXY DR | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 5.97 | 81.2632 | [18 empty] | 0
| 1686 | 20 | B | SSMHT0015442 | SS.MH.T0015442 | 32.2353 | -95.2981 | N25 | 700 BLK MARSH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.5 | 125.6 | [18 empty] | 0
| 1687 | 20 | B | SSMHT0015443 | SS.MH.T0015443 | 32.2354 | -95.2984 | N25 | 700 BLK MARSH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | [18 empty] | 0
| 1688 | 20 | A | SSMHT0015444 | SS.MH.T0015444 | 32.2359 | -95.2988 | N25 | 700 BLK MARSH FARM RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 14 | [19 empty] | 0
| 1689 | 20 | B | SSMHT0015445 | SS.MH.T0015445 | 32.2348 | -95.2985 | N25 | NONE CADDO RIDGE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.76 | 179.1056 | [18 empty] | 0
| 1690 | 20 | A | SSMHT0015446 | SS.MH.T0015446 | 32.2347 | -95.2983 | N25 | NONE CADDO RIDGE | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 14.57 | [19 empty] | 0
| 1691 | 20 | A | SSMHT0015447 | SS.MH.T0015447 | 32.2348 | -95.2995 | N25 | NONE CADDO RIDGE | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12 | [19 empty] | 0
| 1692 | 20 | A | SSMHT0015448 | SS.MH.T0015448 | 32.2363 | -95.3001 | N25 | 700 BLK MARSH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.08 | 132.8848 | [18 empty] | 0
| 1693 | 20 | A | SSMHT0015449 | SS.MH.T0015449 | 32.2362 | -95.2996 | N25 | 700 BLK MARSH FARM RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 2.34 | [19 empty] | 0
| 1694 | 20 | A | SSMHT0015450 | SS.MH.T0015450 | 32.2349 | -95.3 | N25 | NONE CADDO RIDGE | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.2 | [19 empty] | 0
| 1695 | 20 | C | SSMHT0015451 | SS.MH.T0015451 | 32.2367 | -95.3006 | N25 | 700 BLK MARSH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.98 | 206.9888 | [18 empty] | 0
| 1696 | 20 | B | SSMHT0015452 | SS.MH.T0015452 | 32.236 | -95.3002 | N25 | NONE CADDO RIDGE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.98 | 119.0688 | [18 empty] | 0
| 1697 | 20 | B | SSMHT0015453 | SS.MH.T0015453 | 32.2354 | -95.3002 | N25 | NONE CADDO RIDGE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.5 | 113.04 | [18 empty] | 0
| 1698 | 20 | B | SSMHT0015454 | SS.MH.T0015454 | 32.2362 | -95.2983 | N25 | 9356 STONEBANK CROSSING | Solid |  | Yes | Creek | Unpaved | Above Grade | 32 | Std 48 Round | Concrete | 14..77 | #VALUE! | [18 empty] | 0
| 1699 | 20 | C | SSMHT0015455 | SS.MH.T0015455 | 32.2357 | -95.2979 | N25 | 9356 STONEBANK CROSSING | Solid |  | No | Field | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 16.31 | 211.1336 | [18 empty] | 0
| 1700 | 20 | B | SSMHT0015457 | SS.MH.T0015457 | 32.2382 | -95.3017 | N25 | 551 MARCH FARM RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.45 | 162.652 | [18 empty] | 0
| 1701 | 20 | B | SSMHT0015458 | SS.MH.T0015458 | 32.238 | -95.301 | N25 | 551 MARCH FARM RD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.8 | 104.248 | [18 empty] | 0
| 1702 | 20 | B | SSMHT0015459 | SS.MH.T0015459 | 32.2381 | -95.3007 | N25 | 551 MARCH FARM RD | None |  |  | Yard | Unpaved | Above Grade | 7 | CO 6" | Other | 13.68 | [19 empty] | 0
| 1703 | 20 | B | SSMHT0015461 | SS.MH.T0015461 | 32.272 | -95.2651 | O22 | 7283 ROLLING ACRES PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.04 | 107.2624 | [18 empty] | 0
| 1704 | 20 | B | SSMHT0015462 | SS.MH.T0015462 | 32.2724 | -95.265 | O22 | 7283 ROLLING ACRES PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.29 | 110.4024 | [18 empty] | 0
| 1705 | 20 | B | SSMHT0015463 | SS.MH.T0015463 | 32.2728 | -95.265 | O22 | 7283 ROLLING ACRES PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.31 | 123.2136 | [18 empty] | 0
| 1706 | 20 | B | SSMHT0015464 | SS.MH.T0015464 | 32.2728 | -95.2649 | O22 | 7283 ROLLING ACRES PL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.53 | 125.9768 | [18 empty] | 0
| 1707 | 20 | A | SSMHT0015467 | SS.MH.T0015467 | 32.2657 | -95.276 | O22 | 8374 PALUXY DR | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.35 | 86.036 | [18 empty] | 0
| 1708 | 20 | B | SSMHT0015474 | SS.MH.T0015474 | 32.2622 | -95.2893 | N23 | 6566 FURMAN CT | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 11.09 | 145.5704 | [18 empty] | 0
| 1709 | 20 | B | SSMHT0015475 | SS.MH.T0015475 | 32.2636 | -95.2895 | N23 | 6566 FURMAN CT | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 11.31 | 148.3336 | [18 empty] | 0
| 1710 | 20 | A | SSMHT0015485 | SS.MH.T0015485 | 32.2618 | -95.3154 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 18 | 232.36 | [18 empty] | 0
| 1711 | 20 | A | SSMHT0015486 | SS.MH.T0015486 | 32.2618 | -95.3165 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 10.25 | 135.02 | [18 empty] | 0
| 1712 | 20 | A | SSMHT0015487 | SS.MH.T0015487 | 32.2619 | -95.3167 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 32 | Std 48 Round | Concrete | 12.57 | 164.1592 | [18 empty] | 0
| 1713 | 20 | A | SSMHT0015488 | SS.MH.T0015488 | 32.2621 | -95.317 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 32 | Std 48 Round | Concrete | 9.29 | 122.9624 | [18 empty] | 0
| 1714 | 20 | D | SSMHT0015489 | SS.MH.T0015489 | 32.2621 | -95.3172 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 9.86 | 130.1216 |  |  |  |  | 500 |  |  | 650 | [10 empty] | 1150 | Repair
| 1715 | 20 | C | SSMHT0015490 | SS.MH.T0015490 | 32.2623 | -95.3179 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 9.2 | 121.832 | [18 empty] | 0
| 1716 | 20 | B | SSMHT0015491 | SS.MH.T0015491 | 32.2612 | -95.3153 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 12.99 | 169.4344 | [18 empty] | 0
| 1717 | 20 | A | SSMHT0015492 | SS.MH.T0015492 | 32.2612 | -95.3144 | M23 | 7920 CROOKED TRL | Solid |  | No | Creek | Unpaved | Above Grade | 87 | Std 48 Round | Concrete | 12.82 | 167.2992 | [18 empty] | 0
| 1718 | 20 | B | SSMHT0015493 | SS.MH.T0015493 | 32.2604 | -95.3144 | M23 | 7927 CROOKED TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12 | 157 | [18 empty] | 0
| 1719 | 20 | A | SSMHT0015494 | SS.MH.T0015494 | 32.2604 | -95.3148 | M23 | 7915 CROOKED TRL | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.65 | [19 empty] | 0
| 1720 | 20 | B | SSMHT0015495 | SS.MH.T0015495 | 32.2604 | -95.3135 | M23 | 7923 CROOKED TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.14 | 171.3184 | [18 empty] | 0
| 1721 | 20 | B | SSMHT0015496 | SS.MH.T0015496 | 32.2604 | -95.3132 | M23 | 7927 CROOKED TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.7 | 115.552 | [18 empty] | 0
| 1722 | 20 | A | SSMHT0015500 | SS.MH.T0015500 | 32.2705 | -95.2776 | O22 | 7200 PALUXY DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.72 | 153.4832 | [18 empty] | 0
| 1723 | 20 | C | SSMHT0015501 | SS.MH.T0015501 | 32.2707 | -95.2772 | O22 | 7200 PALUXY DR | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.67 | 152.8552 | [18 empty] | 0
| 1724 | 20 | A | SSMHT0015502 | SS.MH.T0015502 | 32.2657 | -95.2789 | O22 | 8380 FM 756 | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.28 | 122.8368 | [18 empty] | 0
| 1725 | 20 | X-CNO | SSMHT0015503 | SS.MH.T0015503 | 32.2657 | -95.2777 | O22 | 8380 FM 756 | Solid |  |  | Alley | Paved - Concrete | At Grade | [23 empty] | 0
| 1726 | 20 | A | SSMHT0015504 | SS.MH.T0015504 | 32.2664 | -95.2783 | O22 | 1925 BRANDON DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.12 | 120.8272 | [18 empty] | 0
| 1727 | 20 | A | SSMHT0015505 | SS.MH.T0015505 | 32.2664 | -95.2772 | O22 | 2102 BRANDON DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.32 | [19 empty] | 0
| 1728 | 20 | C | SSMHT0015506 | SS.MH.T0015506 | 32.2628 | -95.2972 | N22 | 8420 WILKEN PLAZA | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 9.36 | 123.8416 | [18 empty] | 0
| 1729 | 20 | C | SSMHT0015507 | SS.MH.T0015507 | 32.2705 | -95.2988 | N22 | 639 CAMBRIDGE BEND CIR | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.72 | 115.8032 | [18 empty] | 0
| 1730 | 20 | D | SSMHT0015508 | SS.MH.T0015508 | 32.2588 | -95.3175 | M23 | 1502 W CUMBERLAND RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 1731 | 20 | B | SSMHT0015509 | SS.MH.T0015509 | 32.2791 | -95.2824 | N21 | 1518 E GRANDE BLVD | Other | NONE | No | Driveway | Unpaved | Above Grade | 6 | CO 6" | Other | 9.49 | [19 empty] | 0
| 1732 | 20 | B | SSMHT0015510 | SS.MH.T0015510 | 32.2776 | -95.2896 | N21 | 3203 E GRANDE BLVD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.5 | 100.48 | [18 empty] | 0
| 1733 | 20 | B | SSMHT0015511 | SS.MH.T0015511 | 32.2778 | -95.2897 | N21 | 3203 E GRANDE BLVD | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.89 | 105.3784 | [18 empty] | 0
| 1734 | 20 | A | SSMHT0015512 | SS.MH.T0015512 | 32.2779 | -95.2903 | N21 | 3203 E GRANDE BLVD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 4.2 | [19 empty] | 0
| 1735 | 20 | B | SSMHT0015518 | SS.MH.T0015518 | 32.259 | -95.3174 | M23 | 413 W CUMBERLAND RD | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.39 | 111.6584 | [18 empty] | 0
| 1736 | 20 | B | SSMHT0015522 | SS.MH.T0015522 | 32.2604 | -95.313 | M23 | 8005 CROOKER TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0
| 1737 | 20 | B | SSMHT0015524 | SS.MH.T0015524 | 32.2588 | -95.3174 | M23 | 413 CUMBERLAND RD | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.7 | 102.992 | [18 empty] | 0
| 1738 | 20 | D | SSMHT0015525 | SS.MH.T0015525 | 32.2573 | -95.317 | M23 | 413 CUMBERLAND DR | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 8.24 | 109.7744 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 1739 | 20 | D | SSMHT0015528 | SS.MH.T0015528 | 32.2618 | -95.2955 | N23 | 8429 CASTLETON WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 8.3 | 110.528 | 2 | [6 empty] | 650 |  |  |  |  | 3315.84 |  | 280 |  |  |  | 4245.84 | Rehabilitate
| 1740 | 20 | C | SSMHT0015529 | SS.MH.T0015529 | 32.2624 | -95.2956 | N23 | 8429 CASTLETON WAY | Solid |  | No | Yard | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 13.1 | 170.816 | [18 empty] | 0
| 1741 | 20 | B | SSMHT0015535 | SS.MH.T0015535 | 32.2604 | -95.3122 | M23 | 8112 CROOKED TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.88 | 105.2528 | [18 empty] | 0
| 1742 | 20 | A | SSMHT0015536 | SS.MH.T0015536 | 32.2604 | -95.3109 | M23 | 8112 CROOKED TRL | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.82 | [19 empty] | 0
| 1743 | 20 | D | SSMHT0015626 | SS.MH.T0015626 | 32.2538 | -95.2923 | N23 | 9116 CHEROKEE TRL | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 7.44 | 99.7264 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 | 900 |  |  | 2555 | Repair
| 1744 | 20 | C | SSMHT0015627 | SS.MH.T0015627 | 32.2561 | -95.2837 | N23 | 1516 WILANA DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.96 | 118.8176 | [18 empty] | 0
| 1745 | 20 | C | SSMHT0015650 | SS.MH.T0015650 | 32.2675 | -95.2671 | O22 | 14600 COUNTY RD 2191 | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 13.84 | 180.1104 | [18 empty] | 0
| 1746 | 20 | C | SSMHT0015651 | SS.MH.T0015651 | 32.2669 | -95.2671 | O22 | 14600 COUNTY RD 2191 | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 11.92 | 155.9952 | [18 empty] | 0
| 1747 | 20 | C | SSMHT0015652 | SS.MH.T0015652 | 32.2666 | -95.267 | O22 | 14600 COUNTY RD | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.96 | 143.9376 | [18 empty] | 0
| 1748 | 20 | C | SSMHT0015653 | SS.MH.T0015653 | 32.2663 | -95.2668 | O22 | 14600 COUNTY RD 2191 | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.52 | 113.2912 | [18 empty] | 0
| 1749 | 20 | C | SSMHT0015654 | SS.MH.T0015654 | 32.2659 | -95.2665 | O22 | 14600 COUNTY RD 2191 | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.96 | 93.6976 | [18 empty] | 0
| 1750 | 20 | A | SSMHT0015656 | SS.MH.T0015656 | 32.2756 | -95.2611 | P21 | 2924 ROY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 9.16 | 121.3296 | [18 empty] | 0
| 1751 | 20 | C | SSMHT0015666 | SS.MH.T0015666 | 32.2785 | -95.2883 | N23 | 1136 E GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.38 | 149.2128 | [18 empty] | 0
| 1752 | 20 | C | SSMHT0015667 | SS.MH.T0015667 | 32.2789 | -95.2898 | N21 | 6127 NEW COPELAND RD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11.46 | 150.2176 | [18 empty] | 0
| 1753 | 20 | B | SSMHT0015682 | SS.MH.T0015682 | 32.2552 | -95.3187 | M23 | 574 W CUMBERLAND RD | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 14.18 | 184.3808 | [18 empty] | 0
| 1754 | 21 | D | SSMHT0000275 | SS.MH.T0000275 | 32.3076 | -95.2509 | P18 | 3627 RIVER OAKS CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 20.14 | 259.2384 | 2 | [11 empty] | 7777.152 | [5 empty] | 7777.152 | Rehabilitate
| 1755 | 21 | B | SSMHT0000276 | SS.MH.T0000276 | 32.3098 | -95.2462 | P18 | 3730 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.4 | 111.784 | [18 empty] | 0
| 1756 | 21 | B | SSMHT0000277 | SS.MH.T0000277 | 32.309 | -95.2459 | P18 | 3802 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.6 | 114.296 | [18 empty] | 0
| 1757 | 21 | B | SSMHT0000278 | SS.MH.T0000278 | 32.3098 | -95.2469 | P18 | 3718 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.26 | 110.0256 | [18 empty] | 0
| 1758 | 21 | C | SSMHT0000280 | SS.MH.T0000280 | 32.3016 | -95.2538 | P19 | 3204 PEBBLEBROOK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.09 | 107.8904 | [18 empty] | 0
| 1759 | 21 | B | SSMHT0000281 | SS.MH.T0000281 | 32.3021 | -95.2538 | P19 | 3308 PEBBLE BROOK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.36 | 73.6016 | [18 empty] | 0
| 1760 | 21 | C | SSMHT0000335 | SS.MH.T0000335 | 32.3155 | -95.2624 | O18 | 2800 ANITA LANE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.8 | 79.128 | [18 empty] | 0
| 1761 | 21 | B | SSMHT0000392 | SS.MH.T0000392 | 32.321 | -95.2552 | P17 | 3308 LEXINGTON DR | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.65 | 114.924 | [18 empty] | 0
| 1762 | 21 | B | SSMHT0000393 | SS.MH.T0000393 | 32.321 | -95.2544 | P17 | 3404 LEXINGTON DR | Solid |  | Yes | Yard | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 5.85 | 79.756 | [18 empty] | 0
| 1763 | 21 | C | SSMHT0000620 | SS.MH.T0000620 | 32.3151 | -95.2596 | P18 | 3201 PATRIOT AVE. | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.74 | 116.0544 | [18 empty] | 0
| 1764 | 21 | B | SSMHT0000637 | SS.MH.T0000637 | 32.3077 | -95.2435 | P18 | 3824 BROADMOORE CT. | Solid |  | No | Gutter | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.1 | 133.136 | [18 empty] | 0
| 1765 | 21 | B | SSMHT0000638 | SS.MH.T0000638 | 32.3075 | -95.2435 | P18 | 3851 BROADMOORE CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.4 | 124.344 | [18 empty] | 0
| 1766 | 21 | B | SSMHT0000639 | SS.MH.T0000639 | 32.3074 | -95.2437 | P18 | 3849 BROADMOORE CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.82 | 129.6192 | [18 empty] | 0
| 1767 | 21 | B | SSMHT0000640 | SS.MH.T0000640 | 32.3069 | -95.2437 | P18 | 3738 WOODS BLVD. | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 14.8 | 192.168 | [18 empty] | 0
| 1768 | 21 | B | SSMHT0000641 | SS.MH.T0000641 | 32.3067 | -95.243 | P18 | 3802 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.72 | 90.6832 | [18 empty] | 0
| 1769 | 21 | B | SSMHT0000642 | SS.MH.T0000642 | 32.307 | -95.2428 | P18 | 3806 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.76 | 78.6256 | [18 empty] | 0
| 1770 | 21 | B | SSMHT0000643 | SS.MH.T0000643 | 32.3072 | -95.2427 | Q18 | 3807 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.34 | 85.9104 | [18 empty] | 0
| 1771 | 21 | B | SSMHT0000644 | SS.MH.T0000644 | 32.3075 | -95.2425 | Q18 | 3815 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.44 | 87.1664 | [18 empty] | 0
| 1772 | 21 | B | SSMHT0000645 | SS.MH.T0000645 | 32.3078 | -95.2426 | Q18 | 3814 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [18 empty] | 0
| 1773 | 21 | B | SSMHT0000646 | SS.MH.T0000646 | 32.3088 | -95.243 | P18 | 3826 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.1 | 95.456 | [18 empty] | 0
| 1774 | 21 | B | SSMHT0000647 | SS.MH.T0000647 | 32.3097 | -95.2433 | P18 | 3746 WINDING WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.88 | 92.6928 | [18 empty] | 0
| 1775 | 21 | B | SSMHT0000648 | SS.MH.T0000648 | 32.3098 | -95.2436 | P18 | 3721 WINDING WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.92 | 93.1952 | [18 empty] | 0
| 1776 | 21 | X-CNL | SSMHT0000689 | SS.MH.T0000689 |  |  | P19 | 4211 LAZY CREEK DR |  |  |  | Trees/Woods | Unpaved | Below Grade | [23 empty] | 0
| 1777 | 21 | B | SSMHT0000742 | SS.MH.T0000742 | 32.3078 | -95.2584 | P18 | 3702 LAZY CREEK DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.24 | 97.2144 | [18 empty] | 0
| 1778 | 21 | B | SSMHT0000842 | SS.MH.T0000842 | 32.3016 | -95.2367 | Q19 | 4213 FILLBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 1779 | 21 | C | SSMHT0000843 | SS.MH.T0000843 | 32.301 | -95.2361 | Q19 | 4005 CHAPEL WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.48 | 100.2288 | [18 empty] | 0
| 1780 | 21 | X-CNL | SSMHT0000886 | SS.MH.T0000886 |  |  | P18 | 3201 PATRIOT AVE. |  |  |  | Road Shoulder | Unpaved | [24 empty] | 0
| 1781 | 21 | C | SSMHT0004205 | SS.MH.T0004205 | 32.314 | -95.2626 | O18 | 2800 EMILY LANE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 4.86 | 67.3216 | [18 empty] | 0
| 1782 | 21 | X-CNL | SSMHT0005258 | SS.MH.T0005258 |  |  | P18 | 3601 OAK KNOLL DR. |  |  |  | Yard | Unpaved | [24 empty] | 0
| 1783 | 21 | B | SSMHT0005260 | SS.MH.T0005260 | 32.3087 | -95.2569 | P18 | 3109 LAKE FOREST DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 1784 | 21 | B | SSMHT0005261 | SS.MH.T0005261 | 32.3095 | -95.2549 | P18 | 3601 OAK KNOLL DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.98 | 156.7488 | [18 empty] | 0
| 1785 | 21 | B | SSMHT0005262 | SS.MH.T0005262 | 32.3102 | -95.2549 | P18 | 3405 OAK KNOLL DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1786 | 21 | B | SSMHT0005562 | SS.MH.T0005562 | 32.3066 | -95.2475 | P18 | 3650 OAK LEAF CIR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.3 | 110.528 | [18 empty] | 0
| 1787 | 21 | D | SSMHT0005563 | SS.MH.T0005563 | 32.3034 | -95.2493 | P19 | 3388 BRIDGEWOOD TRAIL | Vented | 2 | No | Trees/Woods | Unpaved | Below Grade | 7 | Std 48 Round | Brick | 5.94 | 80.8864 | 2 | [6 empty] | 650 |  | 1000 |  | 2426.592 |  |  | 280 |  |  |  | 4356.592 | Rehabilitate
| 1788 | 21 | B | SSMHT0005564 | SS.MH.T0005564 | 32.304 | -95.2546 | P19 | 3311 PINECREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.01 | 69.2056 | [18 empty] | 0
| 1789 | 21 | X-CNL | SSMHT0005565 | SS.MH.T0005565 |  |  | P19 | 4013 LAZY CREEK DR |  |  |  | Street | Paved - Asphalt | Below Grade |  | Std 48 Round | [21 empty] | 0
See Note for Cell | 1790 | 21 | B | SSMHT0006002 | SS.MH.T0006002 | 32.3103 | -95.2547 | P18 | 3301 OAK KNOLL DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.7 | 102.992 | [18 empty] | 0
| 1791 | 21 | B | SSMHT0006003 | SS.MH.T0006003 | 32.3095 | -95.2538 | P18 | 3310 OAK VILLAGE DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 1792 | 21 | B | SSMHT0006004 | SS.MH.T0006004 | 32.3095 | -95.2526 | P18 | 3602 ROCK CREEK DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.6 | 76.616 | [18 empty] | 0
| 1793 | 21 | B | SSMHT0006005 | SS.MH.T0006005 | 32.3098 | -95.2524 | P18 | 3504 ROCK CREEK DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.8 | 91.688 | [18 empty] | 0
| 1794 | 21 | B | SSMHT0006006 | SS.MH.T0006006 | 32.3085 | -95.2547 | P18 | 3701 OAK KNOLL DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 1795 | 21 | B | SSMHT0006007 | SS.MH.T0006007 | 32.3077 | -95.2541 | P18 | 3709 LAKE FOREST DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.9 | 92.944 | [18 empty] | 0
| 1796 | 21 | C | SSMHT0006008 | SS.MH.T0006008 | 32.3087 | -95.2526 | P18 | 3614 ROCK CREEK DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.82 | 179.8592 | [18 empty] | 0
| 1797 | 21 | C | SSMHT0006009 | SS.MH.T0006009 | 32.3086 | -95.2512 | P18 | 3615 RIVER OAKS CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.64 | 177.5984 | [18 empty] | 0
| 1798 | 21 | B | SSMHT0006010 | SS.MH.T0006010 | 32.3082 | -95.251 | P18 | 3623 RIVER OAKS CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.88 | 180.6128 | [18 empty] | 0
| 1799 | 21 | C | SSMHT0006011 | SS.MH.T0006011 | 32.3079 | -95.2509 | P18 | 3627 RIVER OAKS CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.28 | 198.1968 | [18 empty] | 0
| 1800 | 21 | C | SSMHT0006012 | SS.MH.T0006012 | 32.3095 | -95.2512 | P18 | 3610 WOODS BLVD. | Solid |  | No | Yard | Unpaved | Above Grade | 28 | Std 48 Round | Concrete | 17.62 | 227.5872 | [18 empty] | 0
| 1801 | 21 | C | SSMHT0006013 | SS.MH.T0006013 | 32.3096 | -95.2502 | P18 | 3510 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.72 | 166.0432 | [18 empty] | 0
| 1802 | 21 | C | SSMHT0006014 | SS.MH.T0006014 | 32.3094 | -95.2496 | P18 | 3605 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.24 | 210.2544 | [18 empty] | 0
| 1803 | 21 | C | SSMHT0006015 | SS.MH.T0006015 | 32.3097 | -95.2494 | P18 | 3610 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.9 | 143.184 | [18 empty] | 0
| 1804 | 21 | C | SSMHT0006016 | SS.MH.T0006016 | 32.3098 | -95.2492 | P18 | 3610 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 1805 | 21 | A | SSMHT0006017 | SS.MH.T0006017 | 32.3087 | -95.2497 | P18 | 3525 WOOD BLVD | Solid |  | No | Yard | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 16.08 | 208.2448 | [18 empty] | 0
| 1806 | 21 | B | SSMHT0006018 | SS.MH.T0006018 | 32.3089 | -95.2494 | P18 | 3529 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.26 | 210.5056 | [18 empty] | 0
| 1807 | 21 | B | SSMHT0006019 | SS.MH.T0006019 | 32.3084 | -95.249 | P18 | 3537 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.1 | 208.496 | [18 empty] | 0
| 1808 | 21 | B | SSMHT0006020 | SS.MH.T0006020 | 32.308 | -95.2487 | P18 | 3601 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16 | 207.24 | [18 empty] | 0
| 1809 | 21 | B | SSMHT0006021 | SS.MH.T0006021 | 32.3082 | -95.2484 | P18 | 3626 FLAGSTONE DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.78 | 129.1168 | [18 empty] | 0
| 1810 | 21 | B | SSMHT0006022 | SS.MH.T0006022 | 32.3102 | -95.2508 | P18 | 3606 BROOKVIEW CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.2 | 197.192 | [18 empty] | 0
| 1811 | 21 | C | SSMHT0006023 | SS.MH.T0006023 | 32.3103 | -95.2504 | P18 | 3610 BROOKVIEW CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.8 | 217.288 | [18 empty] | 0
| 1812 | 21 | B | SSMHT0006027 | SS.MH.T0006027 | 32.3077 | -95.2475 | P18 | 3615 OAK LEAF CR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.48 | 112.7888 | [18 empty] | 0
| 1813 | 21 | B | SSMHT0006028 | SS.MH.T0006028 | 32.3074 | -95.2468 | P18 | 3626 OAK LEAF CIR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.24 | 109.7744 | [18 empty] | 0
| 1814 | 21 | C | SSMHT0006029 | SS.MH.T0006029 | 32.3072 | -95.2468 | P18 | 3634 OAK LEAF CIR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.24 | 147.4544 | [18 empty] | 0
| 1815 | 21 | B | SSMHT0006030 | SS.MH.T0006030 | 32.3097 | -95.246 | P18 | 3734 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.32 | 110.7792 | [18 empty] | 0
| 1816 | 21 | B | SSMHT0006031 | SS.MH.T0006031 | 32.3065 | -95.2477 | P18 | 3621 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.88 | 117.8128 | [18 empty] | 0
| 1817 | 21 | B | SSMHT0006032 | SS.MH.T0006032 | 32.3073 | -95.2482 | P18 | 3609 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.7 | 178.352 | [18 empty] | 0
| 1818 | 21 | B | SSMHT0006033 | SS.MH.T0006033 | 32.3074 | -95.248 | P18 | 3603 OAK LEAF CR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.48 | 112.7888 | [18 empty] | 0
| 1819 | 21 | B | SSMHT0006034 | SS.MH.T0006034 | 32.3073 | -95.2506 | P18 | 3633 RIVER OAKS CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.14 | 95.9584 | [18 empty] | 0
| 1820 | 21 | B | SSMHT0006036 | SS.MH.T0006036 | 32.3075 | -95.2526 | P18 | 3633 ROCK CREEK DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.38 | 186.8928 | [18 empty] | 0
| 1821 | 21 | X-CNL | SSMHT0006037 | SS.MH.T0006037 |  |  | P18 | 3638 ROCK CREEK DR. |  |  |  | Yard | Unpaved | [24 empty] | 0
| 1822 | 21 | B | SSMHT0006040 | SS.MH.T0006040 | 32.3039 | -95.2519 | P19 | 4104 PINECREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.08 | 95.2048 | [18 empty] | 0
| 1823 | 21 | B | SSMHT0006041 | SS.MH.T0006041 | 32.3046 | -95.2525 | P19 | 4008 PINECREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.44 | 87.1664 | [18 empty] | 0
| 1824 | 21 | B | SSMHT0006042 | SS.MH.T0006042 | 32.3039 | -95.2535 | P19 | 3404 STOREY LAKE DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.9 | 67.824 | [18 empty] | 0
| 1825 | 21 | C | SSMHT0006043 | SS.MH.T0006043 | 32.3048 | -95.2528 | P19 | 4004 PINECREEK | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.91 | 93.0696 | [18 empty] | 0
| 1826 | 21 | B | SSMHT0006044 | SS.MH.T0006044 | 32.3049 | -95.2531 | P19 | 4004 PINECREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.59 | 89.0504 | [18 empty] | 0
| 1827 | 21 | B | SSMHT0006045 | SS.MH.T0006045 | 32.3049 | -95.2535 | P19 | 3407 PINECREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.61 | 101.8616 | [18 empty] | 0
| 1828 | 21 | B | SSMHT0006046 | SS.MH.T0006046 | 32.3055 | -95.2536 | P19 | NONE LAKEFOREST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.72 | 65.5632 | [18 empty] | 0
| 1829 | 21 | B | SSMHT0006049 | SS.MH.T0006049 | 32.3066 | -95.2538 | P18 | 3800 BLK. LAKE FOREST DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.35 | 73.476 | [18 empty] | 0
| 1830 | 21 | C | SSMHT0006050 | SS.MH.T0006050 | 32.3068 | -95.2541 | P18 | 3805 LAKE FOREST DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.56 | 63.5536 | [18 empty] | 0
| 1831 | 21 | D | SSMHT0006051 | SS.MH.T0006051 | 32.3064 | -95.2664 | NA | 2500 CALLOWAY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.94 | 93.4464 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 1832 | 21 | B | SSMHT0006052 | SS.MH.T0006052 | 32.3063 | -95.2663 | O18 | 2500 CALLOWAY RD | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 7.05 | 94.828 | [18 empty] | 0
| 1833 | 21 | C | SSMHT0006053 | SS.MH.T0006053 | 32.3072 | -95.2669 | O18 | 2504 CALLOWAY RD | Solid |  | No | Street | Unpaved | At Grade |  | Std 48 Round | Concrete | 12.6 | 164.536 | [18 empty] | 0
| 1834 | 21 | D | SSMHT0006055 | SS.MH.T0006055 | 32.3064 | -95.2648 | O18 | 2605 CALLOWAY RD | Solid |  | No | Yard | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 10.44 | 137.4064 | 2 | [6 empty] | 650 |  |  |  |  | 4122.192 | [5 empty] | 4772.192 | Rehabilitate
| 1835 | 21 | C | SSMHT0006056 | SS.MH.T0006056 | 32.3064 | -95.2637 | O18 | 2605 CALLOWAY RD | Solid |  | Yes | Driveway | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.12 | 183.6272 | [18 empty] | 0
| 1836 | 21 | C | SSMHT0006057 | SS.MH.T0006057 | 32.3065 | -95.2628 | O18 | 2801 CALLOWAY RD | Solid |  | No | Sidewalk | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.83 | 142.3048 | [18 empty] | 0
| 1837 | 21 | B | SSMHT0006058 | SS.MH.T0006058 | 32.3065 | -95.2665 | O18 | 2500 CALLOWAY RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 6.12 | 83.1472 | [18 empty] | 0
| 1838 | 21 | B | SSMHT0006059 | SS.MH.T0006059 | 32.3036 | -95.2566 | P19 | 4009 LAZYCREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.7 | 65.312 | [18 empty] | 0
| 1839 | 21 | X-CNL | SSMHT0006060 | SS.MH.T0006060 |  |  | P19 | 3909 LAZY CREEK DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1840 | 21 | X-CNL | SSMHT0006061 | SS.MH.T0006061 |  |  | P19 | 4007 LAZYCREEK DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 1841 | 21 | B | SSMHT0006062 | SS.MH.T0006062 | 32.3029 | -95.2557 | P19 | 4101 LAZY CREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.96 | 68.5776 | [18 empty] | 0
| 1842 | 21 | B | SSMHT0006063 | SS.MH.T0006063 | 32.3024 | -95.2553 | P19 | 3302 STOREY LAKE DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.75 | 103.62 | [18 empty] | 0
| 1843 | 21 | B | SSMHT0006064 | SS.MH.T0006064 | 32.3027 | -95.2533 | P19 | 3309 PEBBLE BROOK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.53 | 75.7368 | [18 empty] | 0
| 1844 | 21 | B | SSMHT0006065 | SS.MH.T0006065 | 32.3033 | -95.2528 | P19 | 3405 PEBBLEBROOK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 6.04 | 82.1424 | [18 empty] | 0
| 1845 | 21 | D | SSMHT0006066 | SS.MH.T0006066 | 32.299 | -95.2613 | P19 | 5050 TROUP HWY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 12.11 | 158.3816 | 2 | [6 empty] | 650 |  |  |  |  | 4751.448 | [5 empty] | 5401.448 | Rehabilitate
| 1846 | 21 | B | SSMHT0006067 | SS.MH.T0006067 | 32.2989 | -95.2621 | P19 | 4616 COMMANCHE TRL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.36 | 123.8416 | [18 empty] | 0
| 1847 | 21 | B | SSMHT0006070 | SS.MH.T0006070 | 32.3004 | -95.261 | P19 | 2927 SPECIALTY DR | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 12.15 | 158.884 | [18 empty] | 0
| 1848 | 21 | B | SSMHT0006071 | SS.MH.T0006071 | 32.3003 | -95.2625 | P19 | 2913 SPECIALTY DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.01 | 182.2456 | [18 empty] | 0
| 1849 | 21 | B | SSMHT0006072 | SS.MH.T0006072 | 32.2968 | -95.2574 | P19 | 5005 HAYES AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 11.96 | 156.4976 | [18 empty] | 0
| 1850 | 21 | B | SSMHT0006073 | SS.MH.T0006073 | 32.2963 | -95.2557 | P19 | 5012 PROFIT DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 14.87 | 193.0472 | [18 empty] | 0
| 1851 | 21 | B | SSMHT0006074 | SS.MH.T0006074 | 32.2969 | -95.255 | P19 | 5012 PROFIT DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 13.4 | 174.584 | [18 empty] | 0
| 1852 | 21 | D | SSMHT0006075 | SS.MH.T0006075 | 32.2985 | -95.2542 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 17.65 | 227.964 | 2 | [6 empty] | 650 |  |  |  |  | 6838.92 | [5 empty] | 7488.92 | Rehabilitate
| 1853 | 21 | D | SSMHT0006076 | SS.MH.T0006076 | 32.2983 | -95.2545 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.08 | 132.8848 | 2 | [6 empty] | 650 |  |  |  |  | 3986.544 | [5 empty] | 4636.544 | Rehabilitate
| 1854 | 21 | B | SSMHT0006077 | SS.MH.T0006077 | 32.2979 | -95.2556 | P19 | 4939 PROFIT DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.81 | 129.4936 | [18 empty] | 0
| 1855 | 21 | D | SSMHT0006078 | SS.MH.T0006078 | 32.2976 | -95.2532 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 12.75 | 166.42 | 2 | [6 empty] | 650 |  |  |  |  | 4992.6 | [5 empty] | 5642.6 | Rehabilitate
| 1856 | 21 | E | SSMHT0006079 | SS.MH.T0006079 | 32.2971 | -95.2524 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 11.06 | 145.1936 | [16 empty] | 7012 |  | 7012 | Replace
| 1857 | 21 | X-Buried | SSMHT0006081 | SS.MH.T0006081 | 32.2962 | -95.2538 | P19 | 5012 PROFIT DR |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1858 | 21 | D | SSMHT0006158 | SS.MH.T0006158 | 32.3012 | -95.2674 | O19 | 4610 TROUP HWY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 6.68 | 90.1808 | 2 | [6 empty] | 650 |  |  |  |  | 2705.424 | [5 empty] | 3355.424 | Rehabilitate
| 1859 | 21 | B | SSMHT0006159 | SS.MH.T0006159 | 32.3011 | -95.2672 | O19 | 4610 TROUP HWY | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 5.6 | 76.616 | [18 empty] | 0
| 1860 | 21 | B | SSMHT0006160 | SS.MH.T0006160 | 32.3011 | -95.2662 | O19 | 2715 HILLSIDE DR | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 10;18 | #VALUE! | [18 empty] | 0
| 1861 | 21 | B | SSMHT0006161 | SS.MH.T0006161 | 32.3012 | -95.2649 | O19 | 4598 OLD TROUP HWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.02 | 107.0112 | [18 empty] | 0
| 1862 | 21 | C | SSMHT0006162 | SS.MH.T0006162 | 32.3004 | -95.2646 | O19 | 4700 OLD TROUP HWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.64 | 215.2784 | [18 empty] | 0
| 1863 | 21 | B | SSMHT0006163 | SS.MH.T0006163 | 32.3001 | -95.2645 | O19 | 4750 OLD TROUP HWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.44 | 212.7664 | [18 empty] | 0
| 1864 | 21 | A | SSMHT0006164 | SS.MH.T0006164 | 32.3004 | -95.2654 | O19 | 2805 WILLARD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 13.48 | 175.5888 | [18 empty] | 0
| 1865 | 21 | B | SSMHT0006201 | SS.MH.T0006201 | 32.2995 | -95.2621 | P19 | 2812 NAVAHO TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.63 | 114.6728 | [18 empty] | 0
| 1866 | 21 | B | SSMHT0006202 | SS.MH.T0006202 | 32.2995 | -95.2628 | O19 | 2720 NAVAHO TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.83 | 129.7448 | [18 empty] | 0
| 1867 | 21 | B | SSMHT0006203 | SS.MH.T0006203 | 32.2991 | -95.2634 | O19 | 4609 PONDEROSA TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.62 | 101.9872 | [18 empty] | 0
| 1868 | 21 | B | SSMHT0006204 | SS.MH.T0006204 | 32.2992 | -95.2631 | O19 | 2708 NAVAHO TRAIL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.05 | 107.388 | [18 empty] | 0
| 1869 | 21 | C | SSMHT0006205 | SS.MH.T0006205 | 32.2985 | -95.2632 | O19 | 4708 PONDEROSA TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.1 | 120.576 | [18 empty] | 0
| 1870 | 21 | B | SSMHT0006206 | SS.MH.T0006206 | 32.2974 | -95.2626 | O19 | 2801 APACHE TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.91 | 118.1896 | [18 empty] | 0
| 1871 | 21 | B | SSMHT0006207 | SS.MH.T0006207 | 32.2974 | -95.2621 | P19 | 2813 APACHE TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.8 | 129.368 | [18 empty] | 0
| 1872 | 21 | B | SSMHT0006208 | SS.MH.T0006208 | 32.2981 | -95.2621 | P19 | 4722 COMMANCHE TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.14 | 83.3984 | [18 empty] | 0
| 1873 | 21 | C | SSMHT0006306 | SS.MH.T0006306 | 32.3074 | -95.2582 | P18 | 3700 LAZY CREEK DR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 1874 | 21 | B | SSMHT0006307 | SS.MH.T0006307 | 32.3075 | -95.2584 | P18 | 3702 LAZY CREEK DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 8.08 | 107.7648 | [18 empty] | 0
| 1875 | 21 | C | SSMHT0006308 | SS.MH.T0006308 | 32.3073 | -95.2576 | P18 | 3103 LAKE VISTA CIR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.2 | 159.512 | [18 empty] | 0
| 1876 | 21 | B | SSMHT0006309 | SS.MH.T0006309 | 32.3071 | -95.2564 | P18 | 3115 LAKE VISTA CIR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.68 | 90.1808 | [18 empty] | 0
| 1877 | 21 | B | SSMHT0006310 | SS.MH.T0006310 | 32.3074 | -95.2562 | P18 | 3710 LAKE VISTA CIR. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.3 | 85.408 | [18 empty] | 0
| 1878 | 21 | B | SSMHT0006311 | SS.MH.T0006311 | 32.3055 | -95.2567 | P19 | 3200 LAKEPINE CIR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.3 | 85.408 | [18 empty] | 0
| 1879 | 21 | B | SSMHT0006312 | SS.MH.T0006312 | 32.3054 | -95.2558 | P19 | 3209 LAKEPINE CIR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.4 | 86.664 | [18 empty] | 0
| 1880 | 21 | C | SSMHT0006313 | SS.MH.T0006313 | 32.3059 | -95.2587 | P18 | 3101 LAKEPINE CT. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.74 | 103.4944 | [18 empty] | 0
| 1881 | 21 | B | SSMHT0006314 | SS.MH.T0006314 | 32.3058 | -95.2588 | P18 | 3835 LAKEPINE CT. | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.22 | 84.4032 | [18 empty] | 0
| 1882 | 21 | D | SSMHT0006315 | SS.MH.T0006315 | 32.3053 | -95.2589 | P19 | 3839 LAZY CREEK DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 6 | Std 48 Round | Concrete | 8.07 | 107.6392 | 2 | [8 empty] | 1000 |  |  | 3229.176 |  | 280 |  |  |  | 4509.176 | Rehabilitate
| 1883 | 21 | B | SSMHT0006316 | SS.MH.T0006316 | 32.3044 | -95.2574 | P19 | 4000 LAZY CREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.34 | 98.4704 | [18 empty] | 0
| 1884 | 21 | X-CNL | SSMHT0006317 | SS.MH.T0006317 |  |  | P19 | 3306 LAKEPINE CIR |  |  |  | Trees/Woods | Unpaved | Below Grade | [23 empty] | 0
| 1885 | 21 | B | SSMHT0006318 | SS.MH.T0006318 | 32.3045 | -95.2556 | P19 | 3305 LAKEPINE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.3 | 97.968 | [18 empty] | 0
| 1886 | 21 | B | SSMHT0006319 | SS.MH.T0006319 | 32.31 | -95.2509 | P18 | 3505 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15 | 194.68 | [18 empty] | 0
| 1887 | 21 | C | SSMHT0006320 | SS.MH.T0006320 | 32.3098 | -95.2479 | P18 | 3630 LONG LEAF DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.3 | 110.528 | [18 empty] | 0
| 1888 | 21 | B | SSMHT0006321 | SS.MH.T0006321 | 32.3112 | -95.2588 | P18 | 3105 UNIVERSITY BLVD. | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 7.1 | 95.456 | [18 empty] | 0
| 1889 | 21 | B | SSMHT0006325 | SS.MH.T0006325 | 32.3113 | -95.2595 | P18 | 3105 UNIVERSITY BLVD. | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 5.68 | 77.6208 | [18 empty] | 0
| 1890 | 21 | B | SSMHT0006341 | SS.MH.T0006341 | 32.3114 | -95.2623 | P18 | 3001 UNIVERSITY BLVD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.98 | 131.6288 | [18 empty] | 0
| 1891 | 21 | B | SSMHT0006342 | SS.MH.T0006342 | 32.3114 | -95.2609 | P18 | 3001 UNIVERSITY BLVD. | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Sealed Concrete | 9.6 | 126.856 | [18 empty] | 0
| 1892 | 21 | B | SSMHT0006343 | SS.MH.T0006343 | 32.3114 | -95.2598 | P18 | 3025 UNIVERSITY BLVD. | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 7.2 | 96.712 | [18 empty] | 0
| 1893 | 21 | C | SSMHT0006344 | SS.MH.T0006344 | 32.3121 | -95.2603 | P18 | 3316 SHENANDOAH DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.92 | 93.1952 | [18 empty] | 0
| 1894 | 21 | C | SSMHT0006345 | SS.MH.T0006345 | 32.3121 | -95.2624 | O18 | 2824 LISA LANE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.8 | 104.248 | [18 empty] | 0
| 1895 | 21 | C | SSMHT0006346 | SS.MH.T0006346 | 32.3129 | -95.2624 | O18 | 2800 AMY LANE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.86 | 79.8816 | [18 empty] | 0
| 1896 | 21 | C | SSMHT0006347 | SS.MH.T0006347 | 32.3129 | -95.2613 | P18 | 2900 AMY LN. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.78 | 103.9968 | [18 empty] | 0
| 1897 | 21 | C | SSMHT0006348 | SS.MH.T0006348 | 32.3138 | -95.2613 | P18 | 3148 ROSEMARY LN. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.5 | 100.48 | [18 empty] | 0
| 1898 | 21 | C | SSMHT0006349 | SS.MH.T0006349 | 32.3138 | -95.2604 | P18 | 3147 SHENANDOAH DR. | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 5.82 | 79.3792 | [18 empty] | 0
| 1899 | 21 | C | SSMHT0006351 | SS.MH.T0006351 | 32.3144 | -95.2637 | O18 | 3100 ANDY LANE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 4.8 | 66.568 | [18 empty] | 0
| 1900 | 21 | C | SSMHT0006352 | SS.MH.T0006352 | 32.3155 | -95.2614 | P18 | 2906 ANITA LN. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.1 | 70.336 | [18 empty] | 0
| 1901 | 21 | B | SSMHT0006458 | SS.MH.T0006458 | 32.3192 | -95.2577 | P17 | 3105 CAMPUS CIR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.35 | 123.716 | [18 empty] | 0
| 1902 | 21 | B | SSMHT0006465 | SS.MH.T0006465 | 32.3201 | -95.2555 | P17 | 3400 VARSITY DR | Solid |  | No | Driveway | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.64 | 102.2384 | [18 empty] | 0
| 1903 | 21 | A | SSMHT0006466 | SS.MH.T0006466 | 32.3205 | -95.2555 | P17 | 3303 LEXINGTON DR | Solid |  | Yes | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Sealed Concrete | 13.06 | 170.3136 | [18 empty] | 0
| 1904 | 21 | B | SSMHT0006467 | SS.MH.T0006467 | 32.3205 | -95.2552 | P17 | 3307 LEXINGTON DR | Solid |  | Yes | Alley | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.38 | 136.6528 | [18 empty] | 0
| 1905 | 21 | A | SSMHT0006468 | SS.MH.T0006468 | 32.3209 | -95.2553 | P17 | 3311 LEXINGTON DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Concrete | 9.18 | 121.5808 | [18 empty] | 0
| 1906 | 21 | B | SSMHT0006469 | SS.MH.T0006469 | 32.3209 | -95.2544 | P17 | 3404 LEXINGTON DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.6 | 76.616 | [18 empty] | 0
| 1907 | 21 | B | SSMHT0006479 | SS.MH.T0006479 | 32.3211 | -95.2526 | P17 | 3502 OMEGA ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.82 | 117.0592 | [18 empty] | 0
| 1908 | 21 | B | SSMHT0006480 | SS.MH.T0006480 | 32.32 | -95.2519 | P17 | 3410 VARSITY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.12 | 158.5072 | [18 empty] | 0
| 1909 | 21 | B | SSMHT0006481 | SS.MH.T0006481 | 32.3185 | -95.2544 | P17 | 3400 VARSITY DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.16 | 83.6496 | [18 empty] | 0
| 1910 | 21 | B | SSMHT0006482 | SS.MH.T0006482 | 32.3193 | -95.2531 | P17 | 3400 VARSITY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.02 | 132.1312 | [18 empty] | 0
| 1911 | 21 | C | SSMHT0006483 | SS.MH.T0006483 | 32.3201 | -95.2537 | P17 | 3400 VARSITY DR | Solid |  | No | Yard | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 3.46 | 49.7376 | [18 empty] | 0
| 1912 | 21 | B | SSMHT0006532 | SS.MH.T0006532 | 32.319 | -95.2537 | P17 | 3400 VARSITY DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.08 | 82.6448 | [18 empty] | 0
| 1913 | 21 | A | SSMHT0006541 | SS.MH.T0006541 | 32.3171 | -95.2612 | P17 | 2941 SHENANDOAH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.02 | 182.3712 | [18 empty] | 0
| 1914 | 21 | A | SSMHT0006542 | SS.MH.T0006542 | 32.3174 | -95.2608 | P17 | 2933 SHENANDOAH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.44 | 87.1664 | [18 empty] | 0
| 1915 | 21 | A | SSMHT0006543 | SS.MH.T0006543 | 32.3175 | -95.2601 | P17 | 2918 SHANANDOAH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.87 | 80.0072 | [18 empty] | 0
| 1916 | 21 | A | SSMHT0006544 | SS.MH.T0006544 | 32.3178 | -95.2599 | P17 | 2910 SHENANDOAH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.4 | 86.664 | [18 empty] | 0
| 1917 | 21 | C | SSMHT0006549 | SS.MH.T0006549 | 32.3157 | -95.2596 | P18 | 3201 PATRIOT AVE. | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 7.04 | 94.7024 | [18 empty] | 0
| 1918 | 21 | B | SSMHT0006575 | SS.MH.T0006575 | 32.3209 | -95.2531 | P17 | 3427 LEXINGTON DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.26 | 110.0256 | [18 empty] | 0
| 1919 | 21 | B | SSMHT0006576 | SS.MH.T0006576 | 32.3209 | -95.2538 | P17 | 3415 LEXINGTON DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.46 | 74.8576 | [18 empty] | 0
| 1920 | 21 | C | SSMHT0006790 | SS.MH.T0006790 | 32.3163 | -95.2613 | P18 | 2913 ROCKBRIDGE RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.49 | 125.4744 | [18 empty] | 0
| 1921 | 21 | B | SSMHT0006791 | SS.MH.T0006791 | 32.3165 | -95.2604 | P18 | 2925 ROCKBRIDGE RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.06 | 182.8736 | [18 empty] | 0
| 1922 | 21 | B | SSMHT0006792 | SS.MH.T0006792 | 32.3163 | -95.261 | P18 | 2917 ROCKBRIDGE RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.06 | 145.1936 | [18 empty] | 0
| 1923 | 21 | B | SSMHT0006793 | SS.MH.T0006793 | 32.3168 | -95.2613 | P17 | 2949 SHENANDOAH DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.83 | 117.1848 | [18 empty] | 0
| 1924 | 21 | B | SSMHT0006796 | SS.MH.T0006796 | 32.3199 | -95.2537 | P17 | 3410 VARSITY DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.1 | 120.576 | [18 empty] | 0
| 1925 | 21 | D | SSMHT0006797 | SS.MH.T0006797 | 32.318 | -95.257 | P17 | 3333 VARSITY DR | Bolted | 4 BOLTS | No | Yard | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 7.35 | 98.596 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 1926 | 21 | C | SSMHT0006849 | SS.MH.T0006849 | 32.3089 | -95.2514 | P18 | 3611 RIVER OAKS CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.12 | 196.1872 | [18 empty] | 0
| 1927 | 21 | B | SSMHT0006850 | SS.MH.T0006850 | 32.309 | -95.245 | P18 | 3700 WINDING WAY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.86 | 180.3616 | [18 empty] | 0
| 1928 | 21 | B | SSMHT0006851 | SS.MH.T0006851 | 32.3093 | -95.2449 | P18 | 3701 WINDING WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | [18 empty] | 0
| 1929 | 21 | B | SSMHT0006852 | SS.MH.T0006852 | 32.3083 | -95.2447 | P18 | 3814 BROADMOORE CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.94 | 206.4864 | [18 empty] | 0
| 1930 | 21 | B | SSMHT0006853 | SS.MH.T0006853 | 32.3086 | -95.2439 | P18 | 3864 BROADMOORE CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.9 | 168.304 | [18 empty] | 0
| 1931 | 21 | B | SSMHT0006854 | SS.MH.T0006854 | 32.3082 | -95.2449 | P18 | 3814 BROADMORE CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.92 | 118.3152 | [18 empty] | 0
| 1932 | 21 | B | SSMHT0006855 | SS.MH.T0006855 | 32.3096 | -95.2449 | P18 | 3710 WINDING WAY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.9 | 118.064 | [18 empty] | 0
| 1933 | 21 | B | SSMHT0006856 | SS.MH.T0006856 | 32.303 | -95.2542 | P19 | 3310 STOREY LAKE DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.17 | 71.2152 | [18 empty] | 0
| 1934 | 21 | D | SSMHT0006859 | SS.MH.T0006859 | 32.299 | -95.2536 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 15.62 | 202.4672 | 2 | [11 empty] | 6074.016 | [5 empty] | 6074.016 | Rehabilitate
| 1935 | 21 | D | SSMHT0006860 | SS.MH.T0006860 | 32.2994 | -95.2533 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 9.58 | 126.6048 | 2 | [6 empty] | 650 |  |  |  |  | 3798.144 | [5 empty] | 4448.144 | Rehabilitate
| 1936 | 21 | C | SSMHT0006861 | SS.MH.T0006861 | 32.2997 | -95.2525 | P19 | 4211 LAZY CREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 13.62 | 177.3472 | [18 empty] | 0
| 1937 | 21 | D | SSMHT0006862 | SS.MH.T0006862 | 32.3027 | -95.2465 | P19 | 3885 BRIGHTEN CREEK CIR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 8.6 | 114.296 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 1938 | 21 | B | SSMHT0006863 | SS.MH.T0006863 | 32.3036 | -95.2447 | P19 | 3888 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.76 | 103.7456 | [18 empty] | 0
| 1939 | 21 | B | SSMHT0006864 | SS.MH.T0006864 | 32.3038 | -95.2442 | P19 | 3896BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.57 | 126.4792 | [18 empty] | 0
| 1940 | 21 | B | SSMHT0006865 | SS.MH.T0006865 | 32.3043 | -95.2435 | P19 | 3896 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.7 | 165.792 | [18 empty] | 0
| 1941 | 21 | B | SSMHT0006866 | SS.MH.T0006866 | 32.3055 | -95.2457 | P18 | 3662 CANYON CREEK PKWY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.36 | 111.2816 | [18 empty] | 0
| 1942 | 21 | B | SSMHT0006868 | SS.MH.T0006868 | 32.3062 | -95.2449 | P18 | 3646 CANYON CREEK PKWY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.12 | 108.2672 | [18 empty] | 0
| 1943 | 21 | B | SSMHT0006869 | SS.MH.T0006869 | 32.3063 | -95.2448 | P18 | 3642 CANYON CREEK PKWY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0
| 1944 | 21 | B | SSMHT0013058 | SS.MH.T0013058 | 32.3064 | -95.2447 | P18 | 3638 CANYON CREEK PKWY. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.64 | 102.2384 | [18 empty] | 0
| 1945 | 21 | B | SSMHT0006870 | SS.MH.T0006870 | 32.3057 | -95.2471 | P18 | 3633 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.82 | 117.0592 | [18 empty] | 0
| 1946 | 21 | B | SSMHT0006871 | SS.MH.T0006871 | 32.3065 | -95.2461 | P18 | 3619 CANYON CREEK CIR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.54 | 100.9824 | [18 empty] | 0
| 1947 | 21 | B | SSMHT0006872 | SS.MH.T0006872 | 32.3016 | -95.244 | P19 | 3861 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.72 | 103.2432 | [18 empty] | 0
| 1948 | 21 | B | SSMHT0006873 | SS.MH.T0006873 | 32.3015 | -95.2438 | P19 | 3855 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.79 | 104.1224 | [18 empty] | 0
| 1949 | 21 | B | SSMHT0006874 | SS.MH.T0006874 | 32.3013 | -95.2432 | P19 | 3849 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.22 | 109.5232 | [18 empty] | 0
| 1950 | 21 | B | SSMHT0006875 | SS.MH.T0006875 | 32.3012 | -95.2429 | P19 | 3843 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | [18 empty] | 0
| 1951 | 21 | D | SSMHT0006876 | SS.MH.T0006876 | 32.3028 | -95.2426 | Q19 | 3831 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.69 | 115.4264 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 1952 | 21 | B | SSMHT0006877 | SS.MH.T0006877 | 32.3045 | -95.2455 | P19 | 3657 WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.5 | 125.6 | [18 empty] | 0
| 1953 | 21 | B | SSMHT0006878 | SS.MH.T0006878 | 32.3051 | -95.2462 | P19 | 3645 WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.25 | 109.9 | [18 empty] | 0
| 1954 | 21 | B | SSMHT0006879 | SS.MH.T0006879 | 32.3046 | -95.2453 | P19 | 3701 WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.61 | 114.4216 | [18 empty] | 0
| 1955 | 21 | B | SSMHT0006880 | SS.MH.T0006880 | 32.3051 | -95.2447 | P19 | 3709 WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.17 | 96.3352 | [18 empty] | 0
| 1956 | 21 | B | SSMHT0006881 | SS.MH.T0006881 | 32.3057 | -95.244 | P18 | 3725 WOODS BLVD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.88 | 105.2528 | [18 empty] | 0
| 1957 | 21 | B | SSMHT0006882 | SS.MH.T0006882 | 32.3029 | -95.2391 | Q19 | 4101 STONEBROOK LN | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 9.97 | 131.5032 | [18 empty] | 0
| 1958 | 21 | B | SSMHT0006883 | SS.MH.T0006883 | 32.3021 | -95.2384 | Q19 | 4118 STONEBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.73 | 65.6888 | [18 empty] | 0
| 1959 | 21 | B | SSMHT0006884 | SS.MH.T0006884 | 32.3026 | -95.2376 | Q19 | 4122 FILLBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.26 | 135.1456 | [18 empty] | 0
| 1960 | 21 | B | SSMHT0006885 | SS.MH.T0006885 | 32.3035 | -95.2383 | Q19 | 4101 FILLBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.37 | 123.9672 | [18 empty] | 0
| 1961 | 21 | B | SSMHT0006886 | SS.MH.T0006886 | 32.3038 | -95.2379 | Q19 | 4011 STONEBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.8 | 116.808 | [18 empty] | 0
| 1962 | 21 | B | SSMHT0006887 | SS.MH.T0006887 | 32.3023 | -95.2373 | Q19 | 4129 FILLBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.01 | 132.0056 | [18 empty] | 0
| 1963 | 21 | B | SSMHT0006888 | SS.MH.T0006888 | 32.3026 | -95.2369 | Q19 | 4134 SAGEMONT LN | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.58 | 139.1648 | [18 empty] | 0
| 1964 | 21 | A | SSMHT0006889 | SS.MH.T0006889 | 32.3029 | -95.2368 | Q19 | 4122 SAGEMONT LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.46 | 112.5376 | [18 empty] | 0
| 1965 | 21 | B | SSMHT0006902 | SS.MH.T0006902 | 32.3023 | -95.2524 | P19 | 3307 BIG OAK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.99 | 81.5144 | [18 empty] | 0
| 1966 | 21 | B | SSMHT0006903 | SS.MH.T0006903 | 32.3006 | -95.2522 | P19 | 4211 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.18 | 83.9008 | [18 empty] | 0
| 1967 | 21 | B | SSMHT0006904 | SS.MH.T0006904 | 32.3008 | -95.2524 | P19 | 3301 CRIPPLE CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.29 | 110.4024 | [18 empty] | 0
| 1968 | 21 | B | SSMHT0006905 | SS.MH.T0006905 | 32.3006 | -95.2526 | P19 | 3205 CRIPPLE CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.45 | 124.972 | [18 empty] | 0
| 1969 | 21 | C | SSMHT0006906 | SS.MH.T0006906 | 32.3032 | -95.2561 | P19 | 4013 LAZY CREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.89 | 180.7384 | [18 empty] | 0
| 1970 | 21 | A | SSMHT0006907 | SS.MH.T0006907 | 32.2997 | -95.2529 | P19 | 4211 LAZY CREEK DR | Solid |  | No | Creek | Unpaved | Above Grade | 27 | Std 48 Round | Concrete | 9.77 | 128.9912 | [18 empty] | 0
| 1971 | 21 | X-CNL | SSMHT0006908 | SS.MH.T0006908 |  |  | P19 | 4211 LAZY CREEK DR |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 1972 | 21 | A | SSMHT0006909 | SS.MH.T0006909 | 32.3004 | -95.2519 | P19 | 4211 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.69 | 165.6664 | [18 empty] | 0
| 1973 | 21 | D | SSMHT0006910 | SS.MH.T0006910 | 32.3004 | -95.2516 | P19 | 4211 LAZYCREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 9.6 | 126.856 | 2 | [6 empty] | 650 |  |  |  |  | 3805.68 | [5 empty] | 4455.68 | Rehabilitate
| 1974 | 21 | C | SSMHT0006911 | SS.MH.T0006911 | 32.3007 | -95.2515 | P19 | 4128 PINECREEK DR. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 11.62 | 152.2272 | [18 empty] | 0
| 1975 | 21 | B | SSMHT0006912 | SS.MH.T0006912 | 32.3009 | -95.2509 | P19 | 4128 PINECREEK DR. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 10.68 | 140.4208 | [18 empty] | 0
| 1976 | 21 | C | SSMHT0006913 | SS.MH.T0006913 | 32.301 | -95.2505 | P19 | 4128 PINECREEK DR. | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 5.52 | 75.6112 | [18 empty] | 0
| 1977 | 21 | D | SSMHT0006914 | SS.MH.T0006914 | 32.3012 | -95.2492 | P19 | 4128 PINECREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 13.57 | 176.7192 | 2 | [11 empty] | 5301.576 | [5 empty] | 5301.576 | Rehabilitate
| 1978 | 21 | C | SSMHT0006915 | SS.MH.T0006915 | 32.3012 | -95.2491 | P19 | 4128 LAZYCREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 40 | Std 48 Round | Concrete | 15.72 | 203.7232 | [18 empty] | 0
| 1979 | 21 | A | SSMHT0006916 | SS.MH.T0006916 | 32.3011 | -95.2482 | P19 | 4128 LAZYCREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 24 | Std 48 Round | Concrete | 4.7 | 65.312 | [18 empty] | 0
| 1980 | 21 | B | SSMHT0006919 | SS.MH.T0006919 | 32.3032 | -95.2512 | P19 | 4110 PINECREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.97 | 81.2632 | [18 empty] | 0
| 1981 | 21 | B | SSMHT0006920 | SS.MH.T0006920 | 32.3028 | -95.252 | P19 | 3401 BIG OAK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.6 | 76.616 | [18 empty] | 0
| 1982 | 21 | B | SSMHT0006921 | SS.MH.T0006921 | 32.3021 | -95.2502 | P19 | 4122 PINECREEK DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 1983 | 21 | B | SSMHT0006922 | SS.MH.T0006922 | 32.3015 | -95.2513 | P19 | 3309 CRIPPLE CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.42 | 61.7952 | [18 empty] | 0
| 1984 | 21 | B | SSMHT0006923 | SS.MH.T0006923 | 32.3013 | -95.2515 | P19 | 3305 CRIPPLE CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.1 | 95.456 | [18 empty] | 0
| 1985 | 21 | C | SSMHT0006924 | SS.MH.T0006924 | 32.3015 | -95.2495 | P19 | 4128 PINECREEK DR | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.92 | 118.3152 | [18 empty] | 0
| 1986 | 21 | D | SSMHT0006925 | SS.MH.T0006925 | 32.2992 | -95.255 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 15.64 | 202.7184 | 2 | [6 empty] | 650 |  |  |  |  | 6081.552 | [5 empty] | 6731.552 | Rehabilitate
| 1987 | 21 | C | SSMHT0006926 | SS.MH.T0006926 | 32.2994 | -95.2555 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 13.7 | 178.352 | [18 empty] | 0
| 1988 | 21 | D | SSMHT0006927 | SS.MH.T0006927 | 32.2996 | -95.2563 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 11.51 | 150.8456 | 2 | [11 empty] | 4525.368 | [5 empty] | 4525.368 | Rehabilitate
| 1989 | 21 | D | SSMHT0006928 | SS.MH.T0006928 | 32.2996 | -95.2567 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 36 | Std 48 Round | Concrete | 13.62 | 177.3472 | 2 | [6 empty] | 650 |  |  |  |  | 5320.416 | [5 empty] | 5970.416 | Rehabilitate
| 1990 | 21 | D | SSMHT0006929 | SS.MH.T0006929 | 32.2997 | -95.2572 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 27 | Std 48 Round | Concrete | 13.91 | 180.9896 | 2 | [11 empty] | 5429.688 | [5 empty] | 5429.688 | Rehabilitate
| 1991 | 21 | B | SSMHT0006930 | SS.MH.T0006930 | 32.2996 | -95.2583 | P19 | 4295 HAYES AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 9.7 | 128.112 | [18 empty] | 0
| 1992 | 21 | A | SSMHT0006931 | SS.MH.T0006931 | 32.2994 | -95.2591 | P19 | 5050 TROUP HWY | Solid |  | No | Creek | Unpaved | Above Grade | 39 | Std 48 Round | Concrete | 6.83 | 92.0648 | [18 empty] | 0
| 1993 | 21 | C | SSMHT0006932 | SS.MH.T0006932 | 32.2992 | -95.2597 | P19 | 5050 TROUP HWY | Bolted |  | No | Field | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 9.75 | 128.74 | [18 empty] | 0
| 1994 | 21 | A | SSMHT0006933 | SS.MH.T0006933 | 32.2953 | -95.2544 | P19 | 3450 SHILOH RD | Solid |  | Yes | Road Shoulder | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.06 | 120.0736 | [18 empty] | 0
| 1995 | 21 | A | SSMHT0006934 | SS.MH.T0006934 | 32.2954 | -95.2523 | P19 | 3632 SHILOH RD | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 8.18 | 109.0208 | [18 empty] | 0
| 1996 | 21 | X-CNL | SSMHT0006935 | SS.MH.T0006935 |  |  | P19 | 3636 SHILOH RD |  |  |  | Road Shoulder | Unpaved | Below Grade | [23 empty] | 0
| 1997 | 21 | C | SSMHT0006936 | SS.MH.T0006936 | 32.2962 | -95.2509 | P19 | 3708 SHILOH RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 11.84 | 154.9904 | [18 empty] | 0
| 1998 | 21 | A | SSMHT0006937 | SS.MH.T0006937 | 32.2965 | -95.251 | P19 | 3708 SHILOH RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 10.78 | 141.6768 | [18 empty] | 0
| 1999 | 21 | C | SSMHT0006938 | SS.MH.T0006938 | 32.2956 | -95.2597 | P19 | 3101 SHILOH RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.89 | 193.2984 | [18 empty] | 0
| 2000 | 21 | C | SSMHT0006939 | SS.MH.T0006939 | 32.2953 | -95.2587 | P19 | 3131 SHILOH RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.6 | 151.976 | [18 empty] | 0
| 2001 | 21 | B | SSMHT0006940 | SS.MH.T0006940 | 32.2953 | -95.258 | P19 | 3226 SHILOH RD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 9.36 | 123.8416 | [18 empty] | 0
| 2002 | 21 | C | SSMHT0006941 | SS.MH.T0006941 | 32.2953 | -95.2574 | P19 | 3226 SHILOH RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 10 | 131.88 | [18 empty] | 0
| 2003 | 21 | X-CNL | SSMHT0006942 | SS.MH.T0006942 |  |  | P19 | 3131 SHILOH RD |  |  |  | Driveway | Paved - Asphalt | Below Grade | [23 empty] | 0
| 2004 | 21 | X-CNL | SSMHT0006943 | SS.MH.T0006943 |  |  | P19 | 3310 SHILOH RD |  |  |  | Driveway | Paved - Concrete | At Grade | [23 empty] | 0
| 2005 | 21 | C | SSMHT0006944 | SS.MH.T0006944 | 32.2953 | -95.2557 | P19 | 3310 SHILOH DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 14.47 | 188.0232 | [18 empty] | 0
| 2006 | 21 | B | SSMHT0007004 | SS.MH.T0007004 | 32.3028 | -95.2456 | P19 | 3879 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.99 | 106.6344 | [18 empty] | 0
| 2007 | 21 | B | SSMHT0007005 | SS.MH.T0007005 | 32.3025 | -95.2453 | P19 | 3873 BRIGHTON CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.74 | 103.4944 | [18 empty] | 0
| 2008 | 21 | B | SSMHT0007006 | SS.MH.T0007006 | 32.3023 | -95.245 | P19 | 3873 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.3 | 97.968 | [18 empty] | 0
| 2009 | 21 | B | SSMHT0007007 | SS.MH.T0007007 | 32.3045 | -95.2437 | P19 | 3802 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.16 | 133.8896 | [18 empty] | 0
| 2010 | 21 | D | SSMHT0007008 | SS.MH.T0007008 | 32.3049 | -95.2433 | P19 | 3802 BRIGHTON CREEK CIR | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 11.42 | 149.7152 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 2011 | 21 | B | SSMHT0007009 | SS.MH.T0007009 | 32.3041 | -95.2434 | P19 | 3814 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.01 | 144.5656 | [18 empty] | 0
| 2012 | 21 | B | SSMHT0007010 | SS.MH.T0007010 | 32.3033 | -95.2431 | P19 | 3823 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 2013 | 21 | B | SSMHT0007011 | SS.MH.T0007011 | 32.3031 | -95.243 | P19 | 3823 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.69 | 115.4264 | [18 empty] | 0
| 2014 | 21 | B | SSMHT0007018 | SS.MH.T0007018 | 32.3105 | -95.2426 | Q18 | 3510 OLD OMEN RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.54 | 188.9024 | [18 empty] | 0
| 2015 | 21 | B | SSMHT0007028 | SS.MH.T0007028 | 32.3013 | -95.2427 | Q19 | 3843 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.04 | 107.2624 | [18 empty] | 0
| 2016 | 21 | B | SSMHT0007029 | SS.MH.T0007029 | 32.3044 | -95.2554 | P19 | 3306 LAKEPINE CIR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 78 | Std 48 Round | Concrete | 7.79 | 104.1224 | [18 empty] | 0
| 2017 | 21 | C | SSMHT0007255 | SS.MH.T0007255 | 32.3071 | -95.2375 | Q18 | 4012 CHAPEL QUARTERS. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.58 | 126.6048 | [18 empty] | 0
| 2018 | 21 | B | SSMHT0007256 | SS.MH.T0007256 | 32.3067 | -95.2375 | Q18 | 4001 CHAPEL RIDGE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.52 | 150.9712 | [18 empty] | 0
| 2019 | 21 | C | SSMHT0007588 | SS.MH.T0007588 | 32.3109 | -95.2518 | P18 | 3807 UNIVERSITY BLVD. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 16 | Std 48 Round | Concrete | 7.98 | 106.5088 | [18 empty] | 0
| 2020 | 21 | B | SSMHT0007676 | SS.MH.T0007676 | 32.3176 | -95.2435 | P17 | 4016 HANDLER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 18.45 | 238.012 | [18 empty] | 0
| 2021 | 21 | D | SSMHT0007677 | SS.MH.T0007677 | 32.3181 | -95.2435 | Q17 | 4016 HANOVER PL | Solid |  | No | Yard | Unpaved | Above Grade | 22 | Std 48 Round | Concrete | 10.18 | 134.1408 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 2022 | 21 | A | SSMHT0007678 | SS.MH.T0007678 | 32.3181 | -95.244 | P17 | NONE SAVANNAH CREED | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.03 | 144.8168 | [18 empty] | 0
| 2023 | 21 | C | SSMHT0007790 | SS.MH.T0007790 | 32.3033 | -95.2408 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 56 | Std 48 Round | Concrete | 12.86 | 167.8016 | [18 empty] | 0
| 2024 | 21 | B | SSMHT0007791 | SS.MH.T0007791 | 32.3021 | -95.24 | Q19 | 3963 CHAPEL WOOD BLVD | Solid |  | No | Street | Unpaved | Above Grade | 43 | Std 48 Round | Concrete | 10.38 | 136.6528 | [18 empty] | 0
| 2025 | 21 | B | SSMHT0007792 | SS.MH.T0007792 | 32.3024 | -95.2407 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 34 | Std 48 Round | Concrete | 10.9 | 143.184 | [18 empty] | 0
| 2026 | 21 | D | SSMHT0007893 | SS.MH.T0007893 | 32.3114 | -95.2421 | Q18 | 3402 PICKENS DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.16 | 133.8896 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 2027 | 21 | C | SSMHT0007894 | SS.MH.T0007894 | 32.3115 | -95.2414 | Q18 | 3402 PICKENS DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.6 | 76.616 | [18 empty] | 0
| 2028 | 21 | B | SSMHT0007972 | SS.MH.T0007972 | 32.3006 | -95.2597 | P19 | 2947SPECIALTY DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 7.7 | 102.992 | [18 empty] | 0
| 2029 | 21 | B | SSMHT0008092 | SS.MH.T0008092 | 32.3078 | -95.2604 | P18 | 3001 UNIVERSITY BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 10.4 | 136.904 | [18 empty] | 0
| 2030 | 21 | B | SSMHT0008605 | SS.MH.T0008605 | 32.3011 | -95.2386 | Q19 | 3960 CHAPEL WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 24.2 | 310.232 | [18 empty] | 0
| 2031 | 21 | D | SSMHT0008606 | SS.MH.T0008606 | 32.3011 | -95.2397 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.38 | 111.5328 | [7 empty] | 650 | [10 empty] | 650 | Repair
| 2032 | 21 | C | SSMHT0008608 | SS.MH.T0008608 | 32.2967 | -95.244 | P19 | 4396 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.32 | 186.1392 | [18 empty] | 0
| 2033 | 21 | A | SSMHT0008609 | SS.MH.T0008609 | 32.2971 | -95.2432 | P19 | 4388 LAZYCREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 8.44 | 112.2864 | [18 empty] | 0
| 2034 | 21 | C | SSMHT0008610 | SS.MH.T0008610 | 32.2975 | -95.2425 | Q19 | 4388 LAZYCREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 19 | Std 48 Round | Concrete | 8.98 | 119.0688 | [18 empty] | 0
| 2035 | 21 | B | SSMHT0008611 | SS.MH.T0008611 | 32.2978 | -95.2419 | Q19 | 4388 LAZY CREEK | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 8.26 | 110.0256 | [18 empty] | 0
| 2036 | 21 | B | SSMHT0008612 | SS.MH.T0008612 | 32.2979 | -95.2415 | Q19 | 4388 LAZYCREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 38 | Std 48 Round | Concrete | 17.82 | 230.0992 | [18 empty] | 0
| 2037 | 21 | D | SSMHT0008618 | SS.MH.T0008618 | 32.3036 | -95.2409 | NA | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 22 | Std 48 Round | Concrete | 14.8 | 192.168 | 2 | [11 empty] | 5765.04 | [5 empty] | 5765.04 | Rehabilitate
| 2038 | 21 | C | SSMHT0008621 | SS.MH.T0008621 | 32.3033 | -95.2457 | P19 | 3885 BRIGHTON CREEK CIR. | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.7 | 115.552 | [18 empty] | 0
| 2039 | 21 | B | SSMHT0008622 | SS.MH.T0008622 | 32.303 | -95.2457 | P19 | 3879 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.89 | 105.3784 | [18 empty] | 0
| 2040 | 21 | A | SSMHT0008623 | SS.MH.T0008623 | 32.3039 | -95.2471 | P19 | 3388 BRIDGEWOOD TRAIL | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.12 | 108.2672 | [18 empty] | 0
| 2041 | 21 | B | SSMHT0008624 | SS.MH.T0008624 | 32.3034 | -95.2475 | P19 | 3388 BRIDGEWOOD TRAIL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 9.82 | 129.6192 | [18 empty] | 0
| 2042 | 21 | C | SSMHT0008633 | SS.MH.T0008633 | 32.3071 | -95.2369 | Q18 | 4031 CHAPEL QUARTERS. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.82 | 129.6192 | [18 empty] | 0
| 2043 | 21 | C | SSMHT0008634 | SS.MH.T0008634 | 32.3071 | -95.2359 | Q18 | 4048 CHAPEL QUARTERS. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.34 | 186.3904 | [18 empty] | 0
| 2044 | 21 | C | SSMHT0008635 | SS.MH.T0008635 | 32.3071 | -95.2353 | Q18 | 4121 CHAPEL QUARTERS. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.9 | 143.184 | [18 empty] | 0
| 2045 | 21 | C | SSMHT0008636 | SS.MH.T0008636 | 32.3069 | -95.2359 | Q18 | 3507 CLARION LN. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.34 | 111.0304 | [18 empty] | 0
| 2046 | 21 | D | SSMHT0008637 | SS.MH.T0008637 | 32.3063 | -95.2356 | Q18 | 3521 CLARION LANE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.88 | 105.2528 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 2047 | 21 | B | SSMHT0008638 | SS.MH.T0008638 | 32.3053 | -95.235 | Q18 | 4129 CHAPEL RIDGE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.02 | 107.0112 | [18 empty] | 0
| 2048 | 21 | C | SSMHT0008639 | SS.MH.T0008639 | 32.3053 | -95.2357 | Q18 | 4111 CHAPEL RIDGE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.44 | 200.2064 | [18 empty] | 0
| 2049 | 21 | B | SSMHT0008640 | SS.MH.T0008640 | 32.3054 | -95.2361 | Q18 | 4043 CHAPEL RIDGE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.74 | 191.4144 | [18 empty] | 0
| 2050 | 21 | C | SSMHT0008641 | SS.MH.T0008641 | 32.3058 | -95.2366 | Q18 | 4019 CHAPEL RIDGE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.28 | 135.3968 | [18 empty] | 0
| 2051 | 21 | C | SSMHT0008642 | SS.MH.T0008642 | 32.3063 | -95.2368 | Q18 | 4008 CHAPEL RIDGE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.18 | 121.5808 | [18 empty] | 0
| 2052 | 21 | C | SSMHT0008643 | SS.MH.T0008643 | 32.3062 | -95.2371 | Q18 | 4002 CHAPEL RIDGE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.04 | 157.5024 | [18 empty] | 0
| 2053 | 21 | C | SSMHT0008644 | SS.MH.T0008644 | 32.3063 | -95.2372 | Q18 | 4000 CHAPEL RIDGE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.46 | 187.8976 | [18 empty] | 0
| 2054 | 21 | C | SSMHT0008645 | SS.MH.T0008645 | 32.3064 | -95.2373 | Q18 | 4007 CHAPEL RIDGE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.12 | 171.0672 | [18 empty] | 0
| 2055 | 21 | C | SSMHT0008646 | SS.MH.T0008646 | 32.3055 | -95.238 | Q18 | 4000 CHAPEL LANE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.98 | 219.5488 | [18 empty] | 0
| 2056 | 21 | C | SSMHT0008647 | SS.MH.T0008647 | 32.3062 | -95.2389 | Q18 | 3900 OLD OMEN RD. | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 14.28 | 185.6368 | [18 empty] | 0
| 2057 | 21 | C | SSMHT0008648 | SS.MH.T0008648 | 32.3077 | -95.2409 | Q18 | 3900 OLD OWEN RD. | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 8.32 | 110.7792 | [18 empty] | 0
| 2058 | 21 | C | SSMHT0008649 | SS.MH.T0008649 | 32.308 | -95.2412 | Q18 | 3700 OLD OMEN RD. | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 28 | Std 48 Round | Sealed Concrete | 11.22 | 147.2032 | [18 empty] | 0
| 2059 | 21 | B | SSMHT0008650 | SS.MH.T0008650 | 32.3079 | -95.2414 | Q18 | 3700 OLD OMEN RD. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0
| 2060 | 21 | D | SSMHT0008651 | SS.MH.T0008651 | 32.3051 | -95.2385 | Q19 | 4001 STONEBROOK LN | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 9.84 | 129.8704 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
| 2061 | 21 | B | SSMHT0008652 | SS.MH.T0008652 | 32.3046 | -95.2392 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 26 | Std 48 Round | Concrete | 12.86 | 167.8016 | [18 empty] | 0
| 2062 | 21 | D | SSMHT0008653 | SS.MH.T0008653 | 32.3043 | -95.2396 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 19.24 | 247.9344 | 2 | [6 empty] | 650 |  |  |  |  | 7438.032 | [5 empty] | 8088.032 | Rehabilitate
| 2063 | 21 | A | SSMHT0008654 | SS.MH.T0008654 | 32.3039 | -95.2401 | Q19 | 3963 CHAPEL BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 38 | Std 48 Round | Concrete | 11.36 | 148.9616 | [18 empty] | 0
| 2064 | 21 | C | SSMHT0008655 | SS.MH.T0008655 | 32.3037 | -95.2404 | Q19 | 3963 CHAPEL WOOD BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 28 | Std 48 Round | Concrete | 12.8 | 167.048 | [18 empty] | 0
| 2065 | 21 | B | SSMHT0008656 | SS.MH.T0008656 | 32.307 | -95.2399 | Q18 | 3900 OMEN RD. | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.26 | 110.0256 | [18 empty] | 0
| 2066 | 21 | B | SSMHT0008657 | SS.MH.T0008657 | 32.301 | -95.2387 | Q19 | 3960 CHAPEL WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.2 | 121.832 | [18 empty] | 0
| 2067 | 21 | B | SSMHT0008658 | SS.MH.T0008658 | 32.3001 | -95.2379 | Q19 | 3980 CHAPEL WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.76 | 116.3056 | [18 empty] | 0
| 2068 | 21 | C | SSMHT0008659 | SS.MH.T0008659 | 32.3 | -95.2376 | Q19 | 3991 CHAPEL WOODS BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.8 | 129.368 | [18 empty] | 0
| 2069 | 21 | B | SSMHT0008660 | SS.MH.T0008660 | 32.2998 | -95.2512 | P19 | 4211 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.62 | 114.5472 | [18 empty] | 0
| 2070 | 21 | A | SSMHT0008661 | SS.MH.T0008661 | 32.2991 | -95.2509 | P19 | 4215 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.56 | 101.2336 | [18 empty] | 0
| 2071 | 21 | X-CNL | SSMHT0008662 | SS.MH.T0008662 |  |  | P19 | 3312 RIDGE BLUFF CIR |  |  |  | Trees/Woods | Unpaved | Below Grade | [23 empty] | 0
| 2072 | 21 | B | SSMHT0008663 | SS.MH.T0008663 | 32.2991 | -95.249 | M20 | 3311 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.67 | 152.8552 | [18 empty] | 0
| 2073 | 21 | B | SSMHT0008664 | SS.MH.T0008664 | 32.299 | -95.2479 | P19 | 3403 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.42 | 149.7152 | [18 empty] | 0
| 2074 | 21 | A | SSMHT0008665 | SS.MH.T0008665 | 32.2974 | -95.2494 | P19 | 3428 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.99 | 169.4344 | [18 empty] | 0
| 2075 | 21 | B | SSMHT0008666 | SS.MH.T0008666 | 32.2978 | -95.2498 | P19 | 4230 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.11 | 108.1416 | [18 empty] | 0
| 2076 | 21 | B | SSMHT0008667 | SS.MH.T0008667 | 32.2978 | -95.2489 | P19 | 3421 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.53 | 138.5368 | [18 empty] | 0
| 2077 | 21 | A | SSMHT0008668 | SS.MH.T0008668 | 32.2981 | -95.2481 | P19 | 3421 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.97 | 144.0632 | [18 empty] | 0
| 2078 | 21 | B | SSMHT0008669 | SS.MH.T0008669 | 32.2983 | -95.2479 | P19 | 3417 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.25 | 147.58 | [18 empty] | 0
| 2079 | 21 | D | SSMHT0008670 | SS.MH.T0008670 | 32.2985 | -95.2478 | P19 | 3417 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.64 | 139.9184 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 2080 | 21 | D | SSMHT0008671 | SS.MH.T0008671 | 32.2988 | -95.2477 | P19 | 3410 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.33 | 148.5848 | [10 empty] | 725 | [7 empty] | 725 | Repair
| 2081 | 21 | A | SSMHT0008674 | SS.MH.T0008674 | 32.2946 | -95.2459 | P19 | 3669 SOUTHWOOD DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.61 | 152.1016 | [18 empty] | 0
| 2082 | 21 | A | SSMHT0008675 | SS.MH.T0008675 | 32.2955 | -95.2452 | P19 | 3677 SOUTHWOOD DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.72 | 166.0432 | [18 empty] | 0
| 2083 | 21 | B | SSMHT0008676 | SS.MH.T0008676 | 32.2963 | -95.2439 | P19 | 4404 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.72 | 166.0432 | [18 empty] | 0
| 2084 | 21 | B | SSMHT0008677 | SS.MH.T0008677 | 32.2958 | -95.2433 | P19 | 4417 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.3 | 135.648 | [18 empty] | 0
| 2085 | 21 | B | SSMHT0008678 | SS.MH.T0008678 | 32.2957 | -95.2431 | P19 | 4416 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.12 | 133.3872 | [18 empty] | 0
| 2086 | 21 | B | SSMHT0008679 | SS.MH.T0008679 | 32.2957 | -95.2429 | Q19 | 4416 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.91 | 130.7496 | [18 empty] | 0
| 2087 | 21 | B | SSMHT0008680 | SS.MH.T0008680 | 32.2958 | -95.2427 | P19 | 4416 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.08 | 132.8848 | [18 empty] | 0
| 2088 | 21 | C | SSMHT0008681 | SS.MH.T0008681 | 32.2969 | -95.244 | P19 | 4388 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14 | 182.12 | [18 empty] | 0
| 2089 | 21 | B | SSMHT0008682 | SS.MH.T0008682 | 32.2977 | -95.2447 | P19 | 4366 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.52 | 201.2112 | [18 empty] | 0
| 2090 | 21 | C | SSMHT0008683 | SS.MH.T0008683 | 32.2978 | -95.2449 | P19 | 4362 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 15.34 | 198.9504 | [18 empty] | 0
| 2091 | 21 | C | SSMHT0008684 | SS.MH.T0008684 | 32.2978 | -95.2452 | P19 | 4358 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.1 | 183.376 | [18 empty] | 0
| 2092 | 21 | B | SSMHT0008685 | SS.MH.T0008685 | 32.2975 | -95.2458 | P19 | 4354 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.64 | 139.9184 | [18 empty] | 0
| 2093 | 21 | B | SSMHT0008686 | SS.MH.T0008686 | 32.2969 | -95.2453 | P19 | 3683 BENTRIDGE CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13 | 169.56 | [18 empty] | 0
| 2094 | 21 | B | SSMHT0008687 | SS.MH.T0008687 | 32.2967 | -95.2453 | P19 | 3683 BENTRIDGE CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0
| 2095 | 21 | B | SSMHT0008688 | SS.MH.T0008688 | 32.2965 | -95.2454 | P19 | 3683 BENTRIDGE CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.4 | 111.784 | [18 empty] | 0
| 2096 | 21 | B | SSMHT0008689 | SS.MH.T0008689 | 32.2961 | -95.2462 | P19 | 3659 BENTRIDGE CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0
| 2097 | 21 | B | SSMHT0008690 | SS.MH.T0008690 | 32.2969 | -95.2469 | P19 | 4330 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 9.87 | 130.2472 | [18 empty] | 0
| 2098 | 21 | B | SSMHT0008691 | SS.MH.T0008691 | 32.2967 | -95.2473 | P19 | 4324 LAZYCREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.3 | 135.648 | [18 empty] | 0
| 2099 | 21 | B | SSMHT0008692 | SS.MH.T0008692 | 32.2966 | -95.2478 | P19 | 4324 LAZY CREEK DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.86 | 130.1216 | [18 empty] | 0
| 2100 | 21 | B | SSMHT0008694 | SS.MH.T0008694 | 32.3011 | -95.2377 | Q19 | 4214 STONEBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.87 | 105.1272 | [18 empty] | 0
| 2101 | 21 | B | SSMHT0008695 | SS.MH.T0008695 | 32.3004 | -95.237 | Q19 | 4306 STONEBROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.74 | 166.2944 | [18 empty] | 0
| 2102 | 21 | B | SSMHT0009012 | SS.MH.T0009012 | 32.3187 | -95.2472 | P17 | 3942 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.43 | 112.1608 | [18 empty] | 0
| 2103 | 21 | B | SSMHT0009013 | SS.MH.T0009013 | 32.3187 | -95.2459 | P17 | 3966 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 13.78 | 179.3568 | [18 empty] | 0
| 2104 | 21 | B | SSMHT0009014 | SS.MH.T0009014 | 32.3187 | -95.2452 | P17 | 3976 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.22 | 147.2032 | [18 empty] | 0
| 2105 | 21 | B | SSMHT0009015 | SS.MH.T0009015 | 32.3187 | -95.244 | P17 | 4012 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 18.02 | 232.6112 | [18 empty] | 0
| 2106 | 21 | B | SSMHT0009016 | SS.MH.T0009016 | 32.3187 | -95.2437 | P17 | 4020 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.19 | 184.5064 | [18 empty] | 0
| 2107 | 21 | B | SSMHT0009017 | SS.MH.T0009017 | 32.3188 | -95.2434 | P17 | 4023 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.49 | 138.0344 | [18 empty] | 0
| 2108 | 21 | B | SSMHT0009018 | SS.MH.T0009018 | 32.3189 | -95.2431 | P17 | 4029 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 8.16 | 108.7696 | [18 empty] | 0
| 2109 | 21 | B | SSMHT0009019 | SS.MH.T0009019 | 32.3194 | -95.2427 | P17 | 4048 CHARLESTON PARK | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.01 | 69.2056 | [18 empty] | 0
| 2110 | 21 | A | SSMHT0009020 | SS.MH.T0009020 | 32.3196 | -95.2429 | P17 | 4019 SPARTANBURG LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.02 | 119.5712 | [18 empty] | 0
| 2111 | 21 | B | SSMHT0009021 | SS.MH.T0009021 | 32.3196 | -95.2431 | P17 | 4019 SPARTANBURG LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.26 | 122.5856 | [18 empty] | 0
| 2112 | 21 | B | SSMHT0009022 | SS.MH.T0009022 | 32.3196 | -95.2435 | P17 | 4011 SPARTANBURG LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.02 | 107.0112 | [18 empty] | 0
| 2113 | 21 | A | SSMHT0009023 | SS.MH.T0009023 | 32.3196 | -95.2443 | P17 | 3993 SPARTANBUR LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.6 | 126.856 | [18 empty] | 0
| 2114 | 21 | A | SSMHT0009024 | SS.MH.T0009024 | 32.3193 | -95.2453 | P17 | 2720 HERMINGWAY LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.3 | 97.968 | [18 empty] | 0
| 2115 | 21 | B | SSMHT0009025 | SS.MH.T0009025 | 32.3176 | -95.2467 | P17 | 3929 HANOVER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.68 | 102.7408 | [18 empty] | 0
| 2116 | 21 | B | SSMHT0009026 | SS.MH.T0009026 | 32.3175 | -95.246 | P17 | 3949 HANOVER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.78 | 103.9968 | [18 empty] | 0
| 2117 | 21 | B | SSMHT0009027 | SS.MH.T0009027 | 32.3174 | -95.2446 | P17 | 3979 HANOVER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.61 | 164.6616 | [18 empty] | 0
| 2118 | 21 | A | SSMHT0009028 | SS.MH.T0009028 | 32.3175 | -95.244 | P17 | 4016 HANOVER PL | Solid |  | No | Gutter | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.51 | 138.2856 | [18 empty] | 0
| 2119 | 21 | B | SSMHT0009029 | SS.MH.T0009029 | 32.3175 | -95.2426 | P17 | 4016 HANBLER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.69 | 190.7864 | [18 empty] | 0
| 2120 | 21 | B | SSMHT0009030 | SS.MH.T0009030 | 32.3176 | -95.2422 | Q17 | 4047 HANOVER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 17.67 | 228.2152 | [18 empty] | 0
| 2121 | 21 | B | SSMHT0009031 | SS.MH.T0009031 | 32.3178 | -95.2418 | Q17 | 4017 HANOVER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.95 | 194.052 | [18 empty] | 0
| 2122 | 21 | B | SSMHT0009032 | SS.MH.T0009032 | 32.3182 | -95.2413 | Q17 | 4047 HANOVER PL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.93 | 131.0008 | [18 empty] | 0
| 2123 | 21 | B | SSMHT0009033 | SS.MH.T0009033 | 32.3177 | -95.2416 | Q17 | 4041 VERANDA PLACE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.41 | 187.2696 | [18 empty] | 0
| 2124 | 21 | B | SSMHT0009034 | SS.MH.T0009034 | 32.3176 | -95.2412 | Q17 | 4045 VERANDA PLACE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.4 | 149.464 | [18 empty] | 0
| 2125 | 21 | D | SSMHT0009306 | SS.MH.T0009306 | 32.3087 | -95.2534 | P18 | 3312 SHADY COVE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2126 | 21 | X-Buried | SSMHT0009307 | SS.MH.T0009307 | 32.3078 | -95.2534 | P18 | 3307 SHADOW GLEN |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 2127 | 21 | A | SSMHT0009308 | SS.MH.T0009308 | 32.3088 | -95.2507 | P18 | 3514 MELANIE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.28 | [19 empty] | 0
| 2128 | 21 | X-CNL | SSMHT0009309 | SS.MH.T0009309 |  |  | P18 | 3616 BROOKVIEW CT. |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 2129 | 21 | X-CNL | SSMHT0009310 | SS.MH.T0009310 |  |  | P19 | 3201 PEBBLEBROOK DR |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 2130 | 21 | X-CNL | SSMHT0009324 | SS.MH.T0009324 |  |  | P19 | 3905 BARKWOOD CIR |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 2131 | 21 | D | SSMHT0009325 | SS.MH.T0009325 | 32.3049 | -95.2586 | P19 | 3903 LAZY CREEK DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 14 | CO 6" | Other | 6.64 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2132 | 21 | D | SSMHT0009326 | SS.MH.T0009326 | 32.3051 | -95.2585 | P19 | 3902 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 11.24 | 147.4544 |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2133 | 21 | D | SSMHT0009327 | SS.MH.T0009327 | 32.305 | -95.2582 | P19 | 3904 LAZYCREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.33 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2134 | 21 | D | SSMHT0009328 | SS.MH.T0009328 | 32.3055 | -95.2573 | P19 | 3109 LAKEPINE CIR. | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 5.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2135 | 21 | D | SSMHT0009366 | SS.MH.T0009366 | 32.3003 | -95.2666 | O19 | 2701 WILLARD DR | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.88 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2136 | 21 | D | SSMHT0009423 | SS.MH.T0009423 | 32.3182 | -95.2599 | P17 | 2902 SHERNANDOAH DR | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2137 | 21 | D | SSMHT0009424 | SS.MH.T0009424 | 32.3163 | -95.2622 | O18 | 2901 ROCKBRIDGE RD. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2138 | 21 | D | SSMHT0009457 | SS.MH.T0009457 | 32.3078 | -95.2448 | P18 | 3819 BROADMOORE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2139 | 21 | X-CNL | SSMHT0009517 | SS.MH.T0009517 |  |  | P18 | 3610 ROCK CREEK DR. |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 2140 | 21 | A | SSMHT0009518 | SS.MH.T0009518 | 32.3085 | -95.2481 | P18 | 3622 FLAGSTONE DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.78 | [19 empty] | 0
| 2141 | 21 | D | SSMHT0009519 | SS.MH.T0009519 | 32.3087 | -95.2579 | P18 | 3101 LAKE FOREST DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Concrete | 10.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2142 | 21 | B | SSMHT0009520 | SS.MH.T0009520 | 32.3025 | -95.2547 | P19 | 3304 STOREY LAKE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.02 | [19 empty] | 0
| 2143 | 21 | X-CNL | SSMHT0009521 | SS.MH.T0009521 |  |  | P19 | 4103 LAZYCREEK DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 2144 | 21 | A | SSMHT0009522 | SS.MH.T0009522 | 32.3017 | -95.2543 | P19 | 4115 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.22 | [19 empty] | 0
| 2145 | 21 | D | SSMHT0009523 | SS.MH.T0009523 | 32.2958 | -95.2508 | P19 | 3708 SHILOH RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.03 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2146 | 21 | D | SSMHT0009524 | SS.MH.T0009524 | 32.2954 | -95.2498 | P19 | 3734 SHILOH RD | Vented | 2 | No | Driveway | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.94 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2147 | 21 | D | SSMHT0009539 | SS.MH.T0009539 | 32.3056 | -95.2575 | P19 | 3107 LAKEPINE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
| 2148 | 21 | X-CNL | SSMHT0009540 | SS.MH.T0009540 |  |  | P19 | 3905 LAZYCREEK DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 2149 | 21 | X-CNL | SSMHT0009541 | SS.MH.T0009541 |  |  | P18 | 3706 PINE BLUFF CIR. |  |  |  | Street | Paved - Asphalt | [24 empty] | 0
| 2150 | 21 | D | SSMHT0009546 | SS.MH.T0009546 | 32.3011 | -95.252 | P19 | 3303 CRIPPLE CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.92 | [15 empty] | 280 |  |  |  | 280 | Repair | 2
| 2151 | 21 | D | SSMHT0009606 | SS.MH.T0009606 | 32.3083 | -95.2564 | P18 | 3702 LAKE VISTA CIR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.42 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 3
| 2152 | 21 | X-CNL | SSMHT0009640 | SS.MH.T0009640 |  |  | P17 | 3224 LEXINGTON DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 2153 | 21 | D | SSMHT0009641 | SS.MH.T0009641 | 32.321 | -95.2531 | P17 | 3428 LEXINGTON DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other | 4.54 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 5
| 2154 | 21 | X-CNL | SSMHT0009642 | SS.MH.T0009642 |  |  | P17 | 3308 LEXINGTON DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 2155 | 21 | X-CNL | SSMHT0009645 | SS.MH.T0009645 |  |  | P17 | 3117 CAMPUS CIR |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 2156 | 21 | D | SSMHT0009646 | SS.MH.T0009646 | 32.3192 | -95.2581 | P17 | 3101 CAMPUS CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.01 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 8
| 2157 | 21 | A | SSMHT0009647 | SS.MH.T0009647 | 32.3205 | -95.2567 | P17 | 3201 LEXINGTON DR | Vented | 2 |  | Alley | Paved - Concrete | At Grade |  | CO 6" | Other | 5.58 | [19 empty] | 0 |  | 9
| 2158 | 21 | A | SSMHT0009685 | SS.MH.T0009685 | 32.3041 | -95.2373 | Q19 | 4002 STONEBROOK LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.28 | [19 empty] | 0 |  | 10
| 2159 | 21 | A | SSMHT0009686 | SS.MH.T0009686 | 32.3033 | -95.2386 | Q19 | 4104 FILLBROOK LN | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.24 | [19 empty] | 0 |  | 11
| 2160 | 21 | A | SSMHT0009708 | SS.MH.T0009708 | 32.309 | -95.2441 | P18 | 3868 BROADMOORE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.3 | [19 empty] | 0 |  | 12
| 2161 | 21 | D | SSMHT0009709 | SS.MH.T0009709 | 32.3098 | -95.2445 | P18 | 3709 3709 WINDING WAY. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 13
| 2162 | 21 | A | SSMHT0009710 | SS.MH.T0009710 | 32.3098 | -95.2447 | P18 | 3705 WINDING WAY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | [20 empty] | 0 |  | 14
| 2163 | 21 | D | SSMHT0009711 | SS.MH.T0009711 | 32.3063 | -95.2433 | P18 | 3788 WOODS BLVD. | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 11.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 15
| 2164 | 21 | A | SSMHT0009712 | SS.MH.T0009712 | 32.3069 | -95.2455 | P18 | 3626 CANYON CREEK PKWY. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.06 | [19 empty] | 0 |  | 16
| 2165 | 21 | A | SSMHT0009713 | SS.MH.T0009713 | 32.3069 | -95.2457 | P18 | 3622 CANYON CREEK CIR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.5 | [19 empty] | 0 |  | 17
| 2166 | 21 | B | SSMHT0009714 | SS.MH.T0009714 | 32.3059 | -95.2473 | P18 | 3629 WOODS BLVD. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.84 | [19 empty] | 0 |  | 18
| 2167 | 21 | D | SSMHT0009715 | SS.MH.T0009715 | 32.3016 | -95.2425 | Q19 | 3838 BRIGHTON CREEK CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.41 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 19
| 2168 | 21 | A | SSMHT0009716 | SS.MH.T0009716 | 32.3036 | -95.2374 | Q19 | 4101 SAGEMONT LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13.34 | [19 empty] | 0 |  | 20
| 2169 | 21 | D | SSMHT0009820 | SS.MH.T0009820 | 32.3062 | -95.2527 | P18 | 3505 RICHMOND | Solid |  |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 21
| 2170 | 21 | D | SSMHT0009821 | SS.MH.T0009821 | 32.3062 | -95.2521 | P18 | 3513 LALEMONT | Vented |  |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.65 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 22
| 2171 | 21 | D | SSMHT0009822 | SS.MH.T0009822 | 32.3061 | -95.2516 | P18 | 3519 LAKEMONT | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.42 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 23
| 2172 | 21 | D | SSMHT0009823 | SS.MH.T0009823 | 32.3071 | -95.2388 | Q18 | 3934 CHAPEL QUARTERS. | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.18 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 24
| 2173 | 21 | A | SSMHT0009824 | SS.MH.T0009824 | 32.3059 | -95.2355 | Q18 | 3533CLARION LANE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.7 | [19 empty] | 0 |  | 25
| 2174 | 21 | D | SSMHT0009825 | SS.MH.T0009825 | 32.3062 | -95.2366 | Q18 | 4014 CHAPEL RIDGE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 0 | 6.28 |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 26
| 2175 | 21 | D | SSMHT0009826 | SS.MH.T0009826 | 32.3048 | -95.2371 | O18 | 3992 OLD OMEN RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Concrete | 12.56 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 27
| 2176 | 21 | D | SSMHT0009827 | SS.MH.T0009827 | 32.3001 | -95.2368 | Q19 | 4310 STONEBROOK LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 28
| 2177 | 21 | D | SSMHT0009828 | SS.MH.T0009828 | 32.2986 | -95.2504 | P19 | 4222 LAZY CREEK DR | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.01 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 29
| 2178 | 21 | D | SSMHT0009829 | SS.MH.T0009829 | 32.2992 | -95.2502 | M20 | 3308 RIDGE BLUFF CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.76 | [15 empty] | 280 |  |  |  | 280 | Repair | 30
| 2179 | 21 | D | SSMHT0009830 | SS.MH.T0009830 | 32.2982 | -95.2501 | P19 | 4230 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.36 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 31
| 2180 | 21 | D | SSMHT0009832 | SS.MH.T0009832 | 32.3006 | -95.2372 | Q19 | 4232 STONEBROOK LN | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.48 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 32
| 2181 | 21 | B | SSMHT0009849 | SS.MH.T0009849 | 32.3196 | -95.2425 | P17 | 4048 CHARLESTON PARK | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.28 | [19 empty] | 0 |  | 33
| 2182 | 21 | B | SSMHT0009850 | SS.MH.T0009850 | 32.3197 | -95.2423 | P17 | 4048 CHARLESTON PARK | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.62 | [19 empty] | 0 |  | 34
| 2183 | 21 | A | SSMHT0009851 | SS.MH.T0009851 | 32.3196 | -95.2449 | P17 | 3985 SPARTANBURG | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.22 | [19 empty] | 0 |  | 35
| 2184 | 21 | A | SSMHT0009852 | SS.MH.T0009852 | 32.3202 | -95.2453 | P17 | 2704 HEMINGWAY LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.63 | [19 empty] | 0 |  | 36
| 2185 | 21 | D | SSMHT0009853 | SS.MH.T0009853 | 32.3176 | -95.2475 | P17 | 3921 HANOVER PL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 37
| 2186 | 21 | A | SSMHT0009854 | SS.MH.T0009854 | 32.3186 | -95.241 | Q17 | 4051 HANOVER PL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.03 | [19 empty] | 0 |  | 38
| 2187 | 21 | D | SSMHT0009876 | SS.MH.T0009876 | 32.3015 | -95.2529 | P19 | 4117 BIG OAK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.62 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 39
| 2188 | 21 | D | SSMHT0009877 | SS.MH.T0009877 | 32.3011 | -95.2525 | P19 | 4119 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.12 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 40
| 2189 | 21 | D | SSMHT0009878 | SS.MH.T0009878 | 32.3004 | -95.2531 | P19 | 3200 CRIPPLE CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.05 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 41
| 2190 | 21 | B | SSMHT0009879 | SS.MH.T0009879 | 32.302 | -95.2516 | P19 | 4117 HOLLOW OAK CIR. | Vented |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 7.08 | 95.2048 | [18 empty] | 0 |  | 42
| 2191 | 21 | D | SSMHT0009880 | SS.MH.T0009880 | 32.3029 | -95.2509 | P19 | 4113 PINECREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 1.77 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 43
| 2192 | 21 | C | SSMHT0009881 | SS.MH.T0009881 | 32.2978 | -95.2575 | P19 | 4295 HAYES AVE | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 7.02 | [19 empty] | 0 |  | 44
| 2193 | 21 | X-CNL | SSMHT0009882 | SS.MH.T0009882 |  |  | P19 | 3310 SHILOH RD |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 2194 | 21 | X-CNL | SSMHT0009883 | SS.MH.T0009883 |  |  | P19 | 3456 SHILOH RD |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 2195 | 21 | X-CNL | SSMHT0009899 | SS.MH.T0009899 |  |  | P19 | 4013 LAZYCREEK DR |  |  |  | Yard | Unpaved | Below Grade | [23 empty] | 0
| 2196 | 21 | D | SSMHT0010064 | SS.MH.T0010064 | 32.3081 | -95.2449 | P18 | 3815 BROADMOORE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.1 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 48
| 2197 | 21 | D | SSMHT0010065 | SS.MH.T0010065 | 32.3103 | -95.2534 | P18 | 3313 OAK KNOLL DR. | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | CO 6" | Other | 0 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 49
| 2198 | 21 | A | SSMHT0010068 | SS.MH.T0010068 | 32.3102 | -95.2524 | P18 | 3501 ROCK CREEK DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.42 | [19 empty] | 0 |  | 50
| 2199 | 21 | D | SSMHT0010069 | SS.MH.T0010069 | 32.3093 | -95.2527 | P18 | 3604 ROCK CREEK DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 51
| 2200 | 21 | D | SSMHT0010070 | SS.MH.T0010070 | 32.3092 | -95.2548 | P18 | 3601 OAK KNOLL DR. | Vented | 2 | No | Street | Paved - Asphalt | Above Grade |  | CO 6" | Other | 8.66 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 52
| 2201 | 21 | X-CNL | SSMHT0010124 | SS.MH.T0010124 |  |  | P19 | 3802 BRIGHTON CREEK CIR |  |  |  | Trees/Woods | Unpaved | Below Grade | [23 empty] | 0
| 2202 | 21 | D | SSMHT0010125 | SS.MH.T0010125 | 32.3083 | -95.2459 | P18 | 3814 LONG LEAF DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 0 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 54
| 2203 | 21 | D | SSMHT0010130 | SS.MH.T0010130 | 32.3032 | -95.2512 | P19 | 4112 PINECREEK DR | Vented | IRON | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.69 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 55
| 2204 | 21 | X-CNL | SSMHT0010131 | SS.MH.T0010131 |  |  | P19 | 4109 LAZY CREEK DR |  |  |  | Street | Paved - Asphalt | Below Grade | [23 empty] | 0
| 2205 | 21 | C | SSMHT0010133 | SS.MH.T0010133 | 32.3087 | -95.2469 | P18 | 3620 TRAILWOOD CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.24 | [19 empty] | 0 |  | 57
| 2206 | 21 | A | SSMHT0010134 | SS.MH.T0010134 | 32.3077 | -95.2473 | P18 | 3618 OAK LEAF CIR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.74 | [19 empty] | 0 |  | 58
| 2207 | 21 | A | SSMHT0010135 | SS.MH.T0010135 | 32.3075 | -95.2469 | P18 | 3622 OAK LEAF CIR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9 | [19 empty] | 0 |  | 59
| 2208 | 21 | C | SSMHT0010136 | SS.MH.T0010136 | 32.3069 | -95.2534 | P18 | 3308 LAKEMONT DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.88 | [19 empty] | 0 |  | 60
| 2209 | 21 | D | SSMHT0010137 | SS.MH.T0010137 | 32.3074 | -95.25 | P18 | 3636 RIVER OAKS CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 0 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 61
| 2210 | 21 | B | SSMHT0010138 | SS.MH.T0010138 | 32.3078 | -95.2492 | P18 | 3645 RIVER OAKS CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.6 | [19 empty] | 0 |  | 62
| 2211 | 21 | A | SSMHT0010139 | SS.MH.T0010139 | 32.3062 | -95.2476 | P18 | 3625 WOODS BLVD. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.7 | [19 empty] | 0 |  | 63
| 2212 | 21 | D | SSMHT0010140 | SS.MH.T0010140 | 32.3083 | -95.2675 | NA | 3900 OLD TROUP HWY | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | IRON | 6.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 64
| 2213 | 21 | D | SSMHT0010157 | SS.MH.T0010157 | 32.2993 | -95.2642 | O19 | 4764 OLD TROUP HWY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.65 | [15 empty] | 280 |  |  |  | 280 | Repair | 65
| 2214 | 21 | D | SSMHT0010158 | SS.MH.T0010158 | 32.298 | -95.263 | O19 | 4714 PONDEROSA TRAIL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.01 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 66
| 2215 | 21 | D | SSMHT0010159 | SS.MH.T0010159 | 32.298 | -95.263 | O19 | 4720 PONDEROSA TRAIL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.63 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 67
| 2216 | 21 | D | SSMHT0010279 | SS.MH.T0010279 | 32.3202 | -95.252 | P17 | 3516 OMEGA DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.21 | [15 empty] | 280 |  |  |  | 280 | Repair | 68
| 2217 | 21 | D | SSMHT0010325 | SS.MH.T0010325 | 32.3031 | -95.239 | Q19 | 4101 STONEBROOK LN | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 69
| 2218 | 21 | D | SSMHT0010326 | SS.MH.T0010326 | 32.3024 | -95.2424 | Q19 | 3831 BRIGHTON CREEK CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 70
| 2219 | 21 | D | SSMHT0010327 | SS.MH.T0010327 | 32.302 | -95.2362 | Q19 | 4002 CHAPEL CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | IRON | 9.28 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 71
| 2220 | 21 | D | SSMHT0010328 | SS.MH.T0010328 | 32.3013 | -95.2356 | Q19 | 4017 CHAPEL WOODS BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 7.78 | 103.9968 |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 72
| 2221 | 21 | D | SSMHT0010329 | SS.MH.T0010329 | 32.3008 | -95.2364 | Q19 | 4001 CHAPEL WOODS BLVD | Other | 0 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Concrete | 6.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 73
| 2222 | 21 | B | SSMHT0010360 | SS.MH.T0010360 | 32.309 | -95.2585 | P18 | 3703 LAZY CREEK DR | Vented | 2 |  | Yard | Unpaved | Above Grade |  | CO 6" | Other | 11.48 | [19 empty] | 0 |  | 74
| 2223 | 21 | D | SSMHT0010376 | SS.MH.T0010376 | 32.3061 | -95.2365 | Q18 | 4020 CHAPEL RIDGE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 0 | 6.28 |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout | 75
| 2224 | 21 | C | SSMHT0011507 | SS.MH.T0011507 | 32.31 | -95.2423 | O18 | 3510 OLD OMEN RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.26 | 135.1456 | [18 empty] | 0 |  | 76
| 2225 | 21 | B | SSMHT0012377 | SS.MH.T0012377 | 32.2957 | -95.2596 | P19 | 3101 SHILOH RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 12 | 157 | [18 empty] | 0 |  | 77
| 2226 | 21 | C | SSMHT0012865 | SS.MH.T0012865 | 32.2973 | -95.255 | P19 | 5012 PROFIT DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Sealed Concrete | 16.17 | 209.3752 | [18 empty] | 0 |  | 78
| 2227 | 21 | B | SSMHT0013204 | SS.MH.T0013204 | 32.3035 | -95.2453 | P19 | 3889 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.6 | 126.856 | [18 empty] | 0 |  | 79
| 2228 | 21 | B | SSMHT0013493 | SS.MH.T0013493 | 32.3069 | -95.2597 | P18 | 2801 CALLOWAY RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 7.9 | 105.504 | [18 empty] | 0 |  | 81
| 2229 | 21 | B | SSMHT0013494 | SS.MH.T0013494 | 32.3124 | -95.2576 | P18 | 3201 UNIVERSITY BLVD. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 11.2 | 146.952 | [18 empty] | 0 |  | 82
| 2230 | 21 | B | SSMHT0013683 | SS.MH.T0013683 | 32.3029 | -95.2584 | P19 | 4542 OLD TROUP HWY | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 6.87 | 92.5672 | [18 empty] | 0 |  | 83
| 2231 | 21 | B | SSMHT0013684 | SS.MH.T0013684 | 32.3023 | -95.2584 | P19 | 4542 OLD TROUP HWY | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 10.9 | 143.184 | [18 empty] | 0 |  | 84
| 2232 | 21 | A | SSMHT0013685 | SS.MH.T0013685 | 32.3017 | -95.2583 | P19 | 4542 OLD TROUP HWY | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 14.49 | 188.2744 | [18 empty] | 0 |  | 85
| 2233 | 21 | A | SSMHT0013686 | SS.MH.T0013686 | 32.3014 | -95.2583 | P19 | 4542 OLD TROUP HWY | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 15.95 | 206.612 | [18 empty] | 0 |  | 86
| 2234 | 21 | A | SSMHT0013687 | SS.MH.T0013687 | 32.301 | -95.2584 | P19 | 4542 OLD TROUP HWY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 11.89 | 155.6184 | [18 empty] | 0 |  | 87
| 2235 | 21 | A | SSMHT0013688 | SS.MH.T0013688 | 32.3005 | -95.2584 | P19 | 4542 OLD TROUP HWY | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 10.45 | 137.532 | [18 empty] | 0 |  | 88
| 2236 | 21 | A | SSMHT0013689 | SS.MH.T0013689 | 32.3004 | -95.2582 | P19 | 4552 OLD TROUP HWY | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 35 | Std 48 Round | Concrete | 12.39 | 161.8984 | [18 empty] | 0 |  | 89
| 2237 | 21 | A | SSMHT0013690 | SS.MH.T0013690 | 32.2999 | -95.2582 | P19 | 4542 OLD TROUP HWY | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 11.03 | 144.8168 | [18 empty] | 0 |  | 90
| 2238 | 21 | A | SSMHT0013691 | SS.MH.T0013691 | 32.2996 | -95.2582 | P19 | 4295 HAYES AVE | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 24 | Std 48 Round | Concrete | 9.84 | 129.8704 | [18 empty] | 0 |  | 91
| 2239 | 21 | C | SSMHT0013918 | SS.MH.T0013918 | 32.2968 | -95.2487 | P19 | 4312 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.23 | [19 empty] | 0 |  | 92
| 2240 | 21 | D | SSMHT0013919 | SS.MH.T0013919 | 32.2966 | -95.2482 | P19 | 4320 LAZY CREEK DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.44 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 93
| 2241 | 21 | A | SSMHT0013920 | SS.MH.T0013920 | 32.2959 | -95.2477 | P19 | 4325 WESTBLUFF DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.34 | [19 empty] | 0 |  | 94
| 2242 | 21 | B | SSMHT0013921 | SS.MH.T0013921 | 32.2965 | -95.2421 | P19 | 4452 LAZYCREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 11.4 | 149.464 | [18 empty] | 0 |  | 95
| 2243 | 21 | A | SSMHT0013922 | SS.MH.T0013922 | 32.2957 | -95.2466 | P19 | 3647 BENTRIDGE CT | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9 | [19 empty] | 0 |  | 96
| 2244 | 21 | B | SSMHT0013964 | SS.MH.T0013964 | 32.3031 | -95.2459 | P19 | 3885 BRIGHTON CREEK CIR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.8 | 91.688 | [18 empty] | 0 |  | 97
| 2245 | 21 | B | SSMHT0013966 | SS.MH.T0013966 | 32.3005 | -95.2604 | P19 | 2947 SPECIALTY DR | Solid |  | Yes | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 10.01 | 132.0056 | [18 empty] | 0 |  | 98
| 2246 | 21 | X-CNL | SSMHT0014143 | SS.MH.T0014143 |  |  | P18 | 3513 WOODS BLVD. |  |  |  | Yard | Unpaved | [24 empty] | 0
| 2247 | 21 | B | SSMHT0014144 | SS.MH.T0014144 | 32.3024 | -95.238 | Q19 | 4113 FILLBROOK LN | Solid |  | No | Alley | Unpaved | Above Grade | 21 | Std 48 Round | Concrete | 16.26 | 210.5056 | [18 empty] | 0 |  | 100
| 2248 | 21 | B | SSMHT0014146 | SS.MH.T0014146 | 32.3113 | -95.2518 | P18 | 3807 UNIVERSITY BLVD. | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 10.2 | 134.392 | [18 empty] | 0 |  | 101
| 2249 | 21 | B | SSMHT0014147 | SS.MH.T0014147 | 32.311 | -95.2518 | P18 | 3807 UNIVERSITY BLVD. | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 6.78 | 91.4368 | [18 empty] | 0 |  | 102
| 2250 | 21 | B | SSMHT0014148 | SS.MH.T0014148 | 32.3115 | -95.2508 | P18 | 3807 UNIVERSITY BLVD. | Solid |  | Yes | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 6.12 | 83.1472 | [18 empty] | 0 |  | 103
| 2251 | 21 | B | SSMHT0014149 | SS.MH.T0014149 | 32.3116 | -95.2498 | P18 | 3979 UNIVERSITY BLVD. | Solid |  | Yes | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 9.26 | 122.5856 | [18 empty] | 0 |  | 104
| 2252 | 21 | B | SSMHT0014490 | SS.MH.T0014490 | 32.3044 | -95.2497 | P19 | 3388 BRIDGEWOOD TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 9 | Std 48 Round | Brick | 17.75 | 229.22 | [18 empty] | 0 |  | 105
| 2253 | 21 | D | SSMHT0014500 | SS.MH.T0014500 | X-CNL | X-CNL | P18 | 255' DS of 14500 & 266' US of 06048 | X-CNL |  |  | Yard | Unpaved | Below Grade | [22 empty] | 2600 | 2600 | Repair | 106
| 2254 | 21 | D | SSMHT0014693 | SS.MH.T0014693 | 32.2998 | -95.2574 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 15.4 | 199.704 | 2 | [11 empty] | 5991.12 | [5 empty] | 5991.12 | Rehabilitate | 107
| 2255 | 21 | X-CNL | SSMHT0014729 | SS.MH.T0014729 |  |  | P18 | 3807 UNIVERSITY BLVD. |  |  |  | Trees/Woods | Unpaved | [24 empty] | 0
| 2256 | 21 | D | SSMHT0014730 | SS.MH.T0014730 | 32.311 | -95.2514 | P18 | 3807 UNIVERSITY BLVD. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 5.16 | 71.0896 | 2 | [6 empty] | 650 |  |  |  | 2132.688 | [6 empty] | 2782.688 | Rehabilitate | 109
| 2257 | 21 | C | SSMHT0014785 | SS.MH.T0014785 | 32.3029 | -95.2485 | P19 | 3388 BRIDGEWOOD TRAIL | Solid | 0 | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Brick | 5.1 | 70.336 | [18 empty] | 0 |  | 110
| 2258 | 21 | C | SSMHT0014788 | SS.MH.T0014788 | 32.3002 | -95.2444 | P19 | 3388 BRIDGE WOOD TRAIL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 4 | Std 48 Round | Brick | 8.1 | 108.016 | [18 empty] | 0 |  | 111
| 2259 | 21 | C | SSMHT0014789 | SS.MH.T0014789 | 32.3018 | -95.2464 | P19 | 3388 BRIDGEWOOD TRLS | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Brick | 9.75 | 128.74 | [18 empty] | 0 |  | 112
| 2260 | 21 | B | SSMHT0015217 | SS.MH.T0015217 | 32.3 | -95.2597 | P19 | 2947 SPECIALTY DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 27 | Std 48 Round | Concrete | 8.2 | 109.272 | [18 empty] | 0 |  | 113
| 2261 | 21 | C | SSMHT0015218 | SS.MH.T0015218 | 32.2968 | -95.2562 | P19 | 4939 PROFIT DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 10.95 | 143.812 | [18 empty] | 0 |  | 114
| 2262 | 21 | A | SSMHT0015219 | SS.MH.T0015219 | 32.3029 | -95.2588 | P19 | 4542 OLD TROUP HWY | Solid |  | Yes | Yard | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 10.92 | 143.4352 | [18 empty] | 0 |  | 115
| 2263 | 21 | A | SSMHT0015220 | SS.MH.T0015220 | 32.3125 | -95.2574 | P18 | 3201 UNIVERSITY BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 18.22 | 235.1232 | [18 empty] | 0 |  | 116
| 2264 | 21 | B | SSMHT0015222 | SS.MH.T0015222 | 32.3012 | -95.2391 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 11.04 | 144.9424 | [18 empty] | 0 |  | 117
| 2265 | 21 | D | SSMHT0015223 | SS.MH.T0015223 | 32.3045 | -95.2392 | P19 | NONE OLD OMEN RD | Solid |  | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.99 | 144.3144 | 2 | [6 empty] | 650 |  |  |  |  | 4329.432 | [5 empty] | 4979.432 | Rehabilitate | 118
| 2266 | 21 | B | SSMHT0015224 | SS.MH.T0015224 | 32.3048 | -95.2388 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 11.28 | 147.9568 | [18 empty] | 0 |  | 119
| 2267 | 21 | B | SSMHT0015226 | SS.MH.T0015226 | 32.2958 | -95.26 | P19 | 3101 SHILOH RD | Solid |  | No | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 7.72 | 103.2432 | [18 empty] | 0 |  | 120
| 2268 | 21 | A | SSMHT0015227 | SS.MH.T0015227 | 32.2958 | -95.2605 | P19 | 3101 SHILOH RD | Solid |  | No | Yard | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 13.22 | 172.3232 | [18 empty] | 0 |  | 121
| 2269 | 21 | B | SSMHT0015228 | SS.MH.T0015228 | 32.305 | -95.2386 | Q19 | 4001 STONEBROOK LN | Solid |  | Yes | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 9.34 | 123.5904 | [18 empty] | 0 |  | 122
| 2270 | 21 | B | SSMHT0015229 | SS.MH.T0015229 | 32.3042 | -95.2478 | P19 | 3336 BRIDGE WOOD TRAIL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.74 | [19 empty] | 0 |  | 123
| 2271 | 21 | B | SSMHT0015233 | SS.MH.T0015233 | 32.3013 | -95.2647 | O19 | 4598 OLD TROUP HWY | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 5.3 | 72.848 | [18 empty] | 0 |  | 124
| 2272 | 21 | D | SSMHT0015234 | SS.MH.T0015234 | 32.3017 | -95.2648 | O19 | 4580 OLD TROUP HWY | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 3.12 | 45.4672 | [7 empty] | 650 | [10 empty] | 650 | Repair | 125
| 2273 | 21 | A | SSMHT0015237 | SS.MH.T0015237 | 32.3056 | -95.2393 | Q18 | 3905 CHAPEL QUARTERS | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.96 | 169.0576 | [18 empty] | 0 |  | 126
| 2274 | 21 | B | SSMHT0015238 | SS.MH.T0015238 | 32.3062 | -95.2401 | Q18 | 3900BLK CHAPEL QUARTERS | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.96 | 106.2576 | [18 empty] | 0 |  | 127
| 2275 | 21 | A | SSMHT0015239 | SS.MH.T0015239 | 32.3066 | -95.2407 | Q18 | 3900BLK CHAPER QUARTER | Solid |  | Yes | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 4.38 | 61.2928 | [18 empty] | 0 |  | 128
| 2276 | 21 | A | SSMHT0015419 | SS.MH.T0015419 | 32.3072 | -95.2414 | Q18 | 3900 BLK CHAPEL QUARTERS | Vented |  | No | Road Shoulder | Unpaved | Above Grade | 2 | CO 6" | Other | 7.56 | [19 empty] | 0 |  | 129
| 2277 | 21 | C | SSMHT0015659 | SS.MH.T0015659 | 32.3078 | -95.2585 | P18 | 3702 LAZY CREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 7.38 | 98.9728 | [18 empty] | 0 |  | 130
| 2278 | U2 | C | SSMHT0014321 | SS.MH.T0014321 | 32.2559 | -95.3315 | L23 | 1300 BLK. W. CUMBERLAND. | Solid |  | Yes | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 11 | 144.44 | [18 empty] | 0 |  | 131
| 2279 | U2 | A | SSMHT0015216 | SS.MH.T0015216 | 32.2569 | -95.3294 | L23 | 1000 BLK. W. CUMBERLAND RD. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 50 | Std 48 Round | Concrete | 8.3 | 110.528 | [18 empty] | 0 |  | 132
| 2280 | 2 | C | SSMHT0007549 | SS.MH.T0007549 | 32.3902 | -95.366 | J11 | 6172 HWY 110 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 32 | Std 60 Round | Brick | 20.12 | 258.9872 | [18 empty] | 0 |  | 133
| 2281 | 2 | B | SSMHT0015422 | SS.MH.T0015422 | 32.3902 | -95.366 | J11 | 6172 HWY 110 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 30 | Std 60 Round | Concrete | 20.86 | 268.2816 | [18 empty] | 0 |  | 134
| 2282 | 7 | D | SSMHT0014387 | SS.MH.T0014387 | X-CNL | X-CNL | K14 | 257' DS of 02017 | X-CNL |  |  | Field | [24 empty] | 2600 | 2600 | Repair | 135
| 2283 | 8 | D | SSMHT0015647 | SS.MH.T0015647 | X-CNL | X-CNL | K14 | 11' DS of 01084 & 107' US of 13042 | X-CNL |  |  | Trees/Woods | [24 empty] | 2600 | 2600 | Repair | 136
| 2284 | 12 | C | SSMHT0000880 | SS.MH.T0000880 | T-CON | T-CON | N11 | Tee 394' DS of 07314 & 446' US of 8583 | T-CON |  |  | Trees/Woods | [27 empty] | 137
| 2285 | 7 | C | SSMHT0014343 | SS.MH.T0014343 | EOLS | EOLS | K14 | 3820HWY 64 | EOLS |  |  | Within Building | [27 empty] | 138
| 2286 | 17 | D | SSMHT0014322 | SS.MH.T0014322 | X-CNL | X-CNL | M21 | 408' DS of 03676 & 99' US of 03674 | X-CNL |  |  | Road Shoulder | [24 empty] | 2600 | 2600 | Repair | 139
| 2287 | 17 | D | SSMHT0014368 | SS.MH.T0014368 | X-CNL | X-CNL | M20 | 138' DS of 14368 & 157' of 03514 | X-CNL |  |  | Yard | [24 empty] | 2600 | 2600 | Repair | 140
| 2288 | 17 | D | SSMHT0014397 | SS.MH.T0014397 | X-CNL | X-CNL | L18 | 158' DS of 14396 & 155' US of 14398 | X-CNL |  |  | Street | [24 empty] | 2600 | 2600 | Repair | 141
| 2289 | 17 | D | SSMHT0015243 | SS.MH.T0015243 | X-CNL | X-CNL | L20 | 13' DS of 15244 & 57' US 15243 | X-CNL |  |  | Parking Lot | [24 empty] | 2600 | 2600 | Repair | 142
| 2290 | 17 | D | SSMHT0015244 | SS.MH.T0015244 | X-CNL | X-CNL | L20 | 187' DS of 01546 & 13' 15243 | X-CNL |  |  | Parking Lot | [24 empty] | 2600 | 2600 | Repair | 143
| 2291 | 17 | D | SSMHT0015253 | SS.MH.T0015253 | X-CNL | X-CNL | M20 | 48' DS of 02439 & 149' US of 02440. | X-CNL |  |  | Yard | [24 empty] | 2600 | 2600 | Repair | 144
| 2292 | 17 | D | SSMHT0015300 | SS.MH.T0015300 | X-CNL | X-CNL | L20 | 301' DS of 00542 & 234' US of 00541 | X-CNL |  |  | Trees/Woods | [24 empty] | 2600 | 2600 | Repair | 145
| 2293 | 18 | D | SSMHT0014502 | SS.MH.T0014502 | X-CNL | X-CNL | N20 | 105' DS 05308 & 80' US of 05307 | X-CNL |  |  | Street | [24 empty] | 2600 | 2600 | Repair | 146
| 2294 | 18 | D | SSMHT0014505 | SS.MH.T0014505 | X-CNL | X-CNL | N20 | 255' DS of 05398 & 301 US of 00363 | X-CNL |  |  | Yard | [24 empty] | 2600 | 2600 | Repair | 147
| 2295 | 5 | D | SSMHT0001171 | SS.MH.T0001171 | 32.3319 | -95.3405 | K16 | 1530 SSW LOOP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 10 | Std 48 Round | Brick | 4.64 | 64.5584 | 2 | [11 empty] | 1936.752 | [5 empty] | 1936.752 | Rehabilitate | 148
| 2296 | 5 | B | SSMHT0001228 | SS.MH.T0001228 | 32.3335 | -95.3403 | K16 | 1300 SSW LOOP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.58 | 114.0448 | [18 empty] | 0 |  | 149
| 2297 | 5 | C | SSMHT0001231 | SS.MH.T0001231 | 32.3131 | -95.3391 | L18 | 3200 S SW LOOP 323 | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.54 | 126.1024 | [18 empty] | 0 |  | 150
| 2298 | 5 | C | SSMHT0001421 | SS.MH.T0001421 | 32.315 | -95.3572 | K18 | 4085 HOGAN DR | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.91 | 118.1896 | [18 empty] | 0 |  | 151
| 2299 | 5 | C | SSMHT0002066 | SS.MH.T0002066 | 32.3362 | -95.3401 | K16 | 1230 SSW LOOP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.2 | 109.272 | [18 empty] | 0 |  | 152
| 2300 | 5 | B | SSMHT0002125 | SS.MH.T0002125 | 32.3376 | -95.3405 | K16 | 917 SSW LOOP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Brick | 13.59 | 176.9704 | [18 empty] | 0 |  | 153
Upated | 2301 | 5 | D | SSMHT0002144 | SS.MH.T0002144 | 32.3401 | -95.3303 | L16 | 823 CLARK ST | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Brick | 8.08 | 107.7648 | 2 | [11 empty] | 3232.944 |  | 280 |  |  |  | 3512.944 | Rehabilitate
| 2302 | 5 | B | SSMHT0002292 | SS.MH.T0002292 | 32.3125 | -95.3374 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.66 | 89.9296 | [18 empty] | 0 |  | 155
| 2303 | 6 | B | SSMHT0003102 | SS.MH.T0003102 | 32.3415 | -95.3669 | J15 | 5721 STATE HWY 31 W | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 7.26 | 97.4656 | [18 empty] | 0 |  | 156
| 2304 | 6 | D | SSMHT0015677 | SS.MH.T0015677 | 32.3439 | -95.3553 | K15 | 4707 STATE HWY 31 W | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.58 | 76.3648 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair | 157
| 2305 | 7 | D | SSMHT0001013 | SS.MH.T0001013 | 32.3564 | -95.349 | K14 | 104 JORDAN PLAZA BLVD | Solid |  | No | Yard | Unpaved | Below Grade | 12 | Std 48 Round | Concrete | 8.94 | 118.5664 | 2 | [8 empty] | 1000 |  |  | 3556.992 |  | 280 |  |  |  | 4836.992 | Rehabilitate | 158
| 2306 | 7 | B | SSMHT0001015 | SS.MH.T0001015 | 32.3555 | -95.3493 | K14 | 115 JORDAN PLAZA BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.24 | 109.7744 | [18 empty] | 0 |  | 159
| 2307 | 7 | D | SSMHT0001016 | SS.MH.T0001016 | 32.3558 | -95.3482 | K14 | 115 JORDAN PLAZA BLVD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 6.08 | 82.6448 | [9 empty] | 1000 | [8 empty] | 1000 | Repair | 160
| 2308 | 7 | D | SSMHT0001052 | SS.MH.T0001052 | 32.3726 | -95.3409 | K13 | 3330 COPE ST | Solid |  | Yes | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Brick | 7.32 | 98.2192 | 2 | [11 empty] | 2946.576 | [5 empty] | 2946.576 | Rehabilitate | 161
| 2309 | 7 | D | SSMHT0015269 | SS.MH.T0015269 | 32.3561 | -95.3484 | K14 | 115 JORDAN PLAZA BLVD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 5.8 | 79.128 |  |  |  |  | 500 |  |  |  |  | 1000 |  |  |  |  | 280 |  |  |  | 1780 | Repair | 162
| 2310 | 8 | D | SSMHT0002019 | SS.MH.T0002019 | 32.3585 | -95.3375 | L14 | 3205 W ERWIN ST | Solid |  | Yes | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Brick | 10.84 | 142.4304 | 2 | [11 empty] | 4272.912 | [5 empty] | 4272.912 | Rehabilitate | 163
| 2311 | 8 | D | SSMHT0012920 | SS.MH.T0012920 | 32.3528 | -95.3192 | M14 | 202 GLENWOOD BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 4.54 | 63.3024 | 2 | [10 empty] | 1899.072 |  |  | 280 |  |  |  | 2179.072 | Rehabilitate | 164
| 2312 | 8 | C | SSMHT0013838 | SS.MH.T0013838 | 32.3573 | -95.3192 | L14 | 625 N GLENWOOD BLVD/ HWY110 | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.34 | 73.3504 | [18 empty] | 0 |  | 165
| 2313 | 10 | C | SSMHT0002816 | SS.MH.T0002816 | 32.3732 | -95.3083 | M12 | 2325 TENNEHA AVE | Solid |  | Yes | Driveway | Unpaved | At Grade |  | Std 48 Round | Brick | 7.3 | 97.968 | [18 empty] | 0 |  | 166
| 2314 | 11 | C | SSMHT0013036 | SS.MH.T0013036 | 32.366 | -95.3133 | M13 | 1121 W HARMONY ST | Solid |  | Yes | Gutter | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 3.42 | 49.2352 | [18 empty] | 0 |  | 167
| 2315 | 13 | B | SSMHT0002721 | SS.MH.T0002721 | 32.3421 | -95.3469 | K15 | 4191 BELLWOOD RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 7.1 | 95.456 | [18 empty] | 0 |  | 168
| 2316 | 13 | C | SSMHT0002783 | SS.MH.T0002783 | 32.3622 | -95.292 | N13 | 1124 E GENTRY PKWY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Sealed Brick | 13.06 | 170.3136 | [18 empty] | 0 |  | 169
| 2317 | 13 | D | SSMHT0005855 | SS.MH.T0005855 | 32.3424 | -95.2855 | N15 | 643 BAXTER | Vented | 1 | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Brick | 5.04 | 69.5824 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair | 170
| 2318 | 13 | D | SSMHT0005952 | SS.MH.T0005952 | 32.3466 | -95.2743 | O18 | 2117 E FRONT ST | Solid |  | Yes | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Brick | 12.73 | 166.1688 | 2 | [11 empty] | 4985.064 |  | 280 |  |  |  | 5265.064 | Rehabilitate | 171
| 2319 | 13 | B | SSMHT0011448 | SS.MH.T0011448 | 32.3383 | -95.2971 | N16 | 403 E. DODGE ST. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.11 | 57.9016 | [18 empty] | 0 |  | 172
| 2320 | 13 | D | SSMHT0014136 | SS.MH.T0014136 | 32.3628 | -95.2928 | N13 | 1224 N WINONA AVE | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 10 | Std 48 Round | Brick | 9.65 | 127.484 | 2 | [11 empty] | 3824.52 |  | 280 |  |  |  | 4104.52 | Rehabilitate | 173
| 2321 | 13 | C | SSMHT0014844 | SS.MH.T0014844 | 32.339 | -95.3044 | M16 | 407 W. DOBBS ST. | Solid |  | No | Street | Paved - Asphalt | Above Grade | 3 | Std 48 Round | Concrete | 5.1 | 70.336 | [18 empty] | 0 |  | 174
| 2322 | 13 | D | SSMHT0015685 | SS.MH.T0015685 | 32.3393 | -95.2974 | N16 | 400BLK FRAZIER ST | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.68 | 77.6208 | 2 | [10 empty] | 2328.624 | [6 empty] | 2328.624 | Rehabilitate | 175
| 2323 | 13 | D | SSMHT0015686 | SS.MH.T0015686 | 32.3392 | -95.2974 | N16 | 400 BLK FRAZIER ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.1 | 82.896 | 2 | [11 empty] | 2486.88 |  | 280 |  |  |  | 2766.88 | Rehabilitate | 176
| 2324 | 13 | D | SSMHT0015689 | SS.MH.T0015689 | 32.36 | -95.2957 | N14 | 1002 N. NORMANDY AVE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.3 | 72.848 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair | 177
| 2325 | 13 | C | SSMHT0015692 | SS.MH.T0015692 | 32.3669 | -95.2916 | N13 | 1611 N. WINONA AVE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.1 | 57.776 | [18 empty] | 0 |  | 178
| 2326 | 13 | C | SSMHT0015693 | SS.MH.T0015693 | 32.3658 | -95.2874 | N13 | 1530 N. CENTRAL AVE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.25 | 59.66 | [18 empty] | 0 |  | 179
| 2327 | 13 | B | SSMHT0015694 | SS.MH.T0015694 | 32.3678 | -95.2951 | N13 | 1722 N. CARLYLE AVE. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 3.4 | 48.984 | [18 empty] | 0 |  | 180
| 2328 | 13 | B | SSMHT0015695 | SS.MH.T0015695 | 32.337 | -95.3085 | M16 | 700 BLK. W. SHAW ST. | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 3.65 | 52.124 | [18 empty] | 0 |  | 181
| 2329 | 13 | D | SSMHT0015696 | SS.MH.T0015696 | 32.3444 | -95.2881 | N15 | 512 S. FLEISHEL AVE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.37 | 61.1672 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair | 182
| 2330 | 13 | C | SSMHT0015697 | SS.MH.T0015697 | 32.3424 | -95.2868 | N15 | 644 CRESTWAY DR. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.62 | 114.5472 | [18 empty] | 0 |  | 183
| 2331 | 13 | B | SSMHT0015698 | SS.MH.T0015698 | 32.3692 | -95.2841 | N16 | 1775 E DUNCAN ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 34 | Std 48 Round | Concrete | 11.94 | 156.2464 | [18 empty] | 0 |  | 184
| 2332 | 13 | A | SSMHT0015834 | SS.MH.T0015834 | 32.3327 | -95.2992 | N16 | 223 E. 3RD ST. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 42 | Concrete | 3.13 | 45.5928 | [18 empty] | 0 |  | 185
| 2333 | 13 | B | SSMHT0015836 | SS.MH.T0015836 | 32.3451 | -95.304 | N16 | 401 W. BRYAN ST. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 42 | Concrete | 4.82 | 66.8192 | [18 empty] | 0 |  | 186
| 2334 | 13 | D | SSMHT0015837 | SS.MH.T0015837 | 32.3378 | -95.2971 | N16 | 409 E. DODGE ST. | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 1.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 187
| 2335 | 13 | D | SSMHT0015838 | SS.MH.T0015838 | 32.3383 | -95.2972 | N16 | 403 E. DODGE ST. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 188
| 2336 | 13 | D | SSMHT0015839 | SS.MH.T0015839 | 32.3564 | -95.3141 | M14 | 516 N. ROSS AVE. | Solid |  | No | Street | Paved - Asphalt | Above Grade | 2 | Std 48 Round | Concrete | 4.6 | 64.056 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair | 189
| 2337 | 14 | D | SSMHT0006577 | SS.MH.T0006577 | 32.3186 | -95.2638 | O17 | 2729 WILLIAMSBURG DR | Solid |  | No | Creek | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 7 | 94.2 | 2 |  | 1000 | [9 empty] | 2826 |  | 280 |  |  |  | 4106 | Rehabilitate | 190
| 2338 | 14 | C | SSMHT0006597 | SS.MH.T0006597 | 32.3122 | -95.2698 | O18 | 2421 E SE LOOP 323 | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Sealed Concrete | 12.02 | 157.2512 | [18 empty] | 0 |  | 191
| 2339 | 14 | B | SSMHT0009648 | SS.MH.T0009648 | 32.3291 | -95.2639 | O16 | 2807 MARYLIN DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.82 | 91.9392 | [18 empty] | 0 |  | 192
| 2340 | 14 | C | SSMHT0014493 | SS.MH.T0014493 | 32.3306 | -95.267 | O16 | 1801 S SE LOOP 323 | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 10.84 | 142.4304 | [18 empty] | 0 |  | 193
| 2341 | 14 | C | SSMHT0015318 | SS.MH.T0015318 | 32.3393 | -95.2778 | O15 | 1819 E DON ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.3 | 97.968 | [18 empty] | 0 |  | 194
| 2342 | 16 | D | SSMHT0001620 | SS.MH.T0001620 | 32.2691 | -95.3309 | L22 | 2010 PINEHURST ST | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 9 | 119.32 | 2 | [11 empty] | 3579.6 | [5 empty] | 3579.6 | Rehabilitate | 195
| 2343 | 16 | D | SSMHT0014318 | SS.MH.T0014318 | 32.2696 | -95.3358 | L22 | 2311 MIRABEAU DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 11.3 | 148.208 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair | 196
| 2344 | 16 | D | SSMHT0014320 | SS.MH.T0014320 | 32.269 | -95.3345 | L22 | 6938 PARK SLOPE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 9.54 | 126.1024 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair | 197
| 2345 | 17 | B | SSMHT0002243 | SS.MH.T0002243 | 32.3216 | -95.3223 | L17 | 2611 HUGHEY DR | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8 | 106.76 | [18 empty] | 0 |  | 198
| 2346 | 17 | D | SSMHT0002397 | SS.MH.T0002397 | 32.3146 | -95.3225 | L18 | 1743 ALAMO CROSSING RD | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Brick | 7.98 | 106.5088 | 2 | [11 empty] | 3195.264 |  | 280 |  |  |  | 3475.264 | Rehabilitate | 199
| 2347 | 17 | D | SSMHT0003386 | SS.MH.T0003386 | 32.2998 | -95.3192 | M19 | 1500 WSW LOOP 323 | Solid |  | No | Creek | Unpaved | Below Grade | 23 | Std 48 Round | Concrete | 6.14 | 83.3984 | 2 |  |  |  | 500 |  |  |  |  | 1000 |  |  | 2501.952 |  | 280 |  |  |  | 4281.952 | Rehabilitate | 200
| 2348 | 17 | B | SSMHT0003484 | SS.MH.T0003484 | 32.2948 | -95.3091 | M20 | 506 RICE RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.37 | 111.4072 | [18 empty] | 0 |  | 201
| 2349 | 17 | D | SSMHT0014362 | SS.MH.T0014362 | 32.3084 | -95.3197 | M18 | 1537 WOODLAND HILLS DR | Vented | 2 | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Brick | 5.2 | 71.592 | 2 | [6 empty] | 650 |  |  |  | 2147.76 |  |  | 280 |  |  |  | 3077.76 | Rehabilitate | 202 | deleted by Taplin DNE
| 2350 | 17 | D | SSMHT0014367 | SS.MH.T0014367 | 32.2941 | -95.3131 | M20 | 5109 KATIE DR | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 8.1 | 108.016 | [7 empty] | 650 | [10 empty] | 650 | Repair | 203
| 2351 | 17 | C | SSMHT0015068 | SS.MH.T0015068 | 32.2827 | -95.3307 | L21 | 5976 OLD JACKSONVILLE HWY | Solid |  | No | Parking Lot | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 12.18 | 159.2608 | [18 empty] | 0 |  | 204
| 2352 | 17 | D | SSMHT0015251 | SS.MH.T0015251 | 32.3033 | -95.3201 | L19 | 3000 WSW LOOP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 6.34 | 85.9104 | 2 | [11 empty] | 2577.312 |  | 280 |  |  |  | 2857.312 | Rehabilitate | 205
| 2353 | 17 | D | SSMHT0015275 | SS.MH.T0015275 | 32.3026 | -95.3243 | L19 | 4334 DC DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Brick | 9.86 | 130.1216 | 2 | [11 empty] | 3903.648 |  | 280 |  |  |  | 4183.648 | Rehabilitate | 206
| 2354 | 17 | A | SSMHT0015302 | SS.MH.T0015302 | 32.2901 | -95.3273 | L20 | 5348 OLD JACKSONVILLE HWY | Solid |  | Yes | Field | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 17.24 | 222.8144 | [18 empty] | 0 |  | 207
| 2355 | 17 | B | SSMHT0015672 | SS.MH.T0015672 | 32.2782 | -95.3197 | M21 | 908 LAGUNA DR | Solid |  | No | Field | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.82 | 117.0592 | [18 empty] | 0 |  | 208
| 2356 | 17 | C | SSMHT0015676 | SS.MH.T0015676 | 32.2815 | -95.3045 | M21 | 6210 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 5.7 | 77.872 | [18 empty] | 0 |  | 209
| 2357 | 18 | C | SSMHT0005203 | SS.MH.T0005203 | 32.2929 | -95.296 | N20 | 455 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 17.89 | 230.9784 | [18 empty] | 0 |  | 210
| 2358 | 18 | D | SSMHT0006192 | SS.MH.T0006192 | 32.2922 | -95.2442 | P20 | 5401 KENT DR | Solid |  | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Brick | 4.62 | 64.3072 | 2 | [6 empty] | 650 |  |  |  | 1929.216 |  |  | 280 |  |  |  | 2859.216 | Rehabilitate | 211
| 2359 | 18 | D | SSMHT0006377 | SS.MH.T0006377 | 32.3159 | -95.2813 | N18 | 1700 DENNIS DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.41 | 111.9096 | 2 | [11 empty] | 3357.288 | [5 empty] | 3357.288 | Rehabilitate | 212
| 2360 | 18 | B | SSMHT0007283 | SS.MH.T0007283 | 32.2954 | -95.2762 | O19 | 2040 SHILOH RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 6.86 | 92.4416 | [18 empty] | 0 |  | 213
| 2361 | 18 | B | SSMHT0009529 | SS.MH.T0009529 | 32.2824 | -95.2977 | N21 | 6110 COVEY LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.67 | 90.0552 | [18 empty] | 0 |  | 214
| 2362 | 18 | D | SSMHT0009955 | SS.MH.T0009955 | 32.308 | -95.272 | O19 | 3830 TROUP HWY | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | CO 8" | Other | 9.11 | 120.7016 |  | 140 | [16 empty] | 140 | Replace/Install Cleanout | 215
| 2363 | 18 | C | SSMHT0011108 | SS.MH.T0011108 | 32.3159 | -95.2811 | N19 | 3002 DINAH LN | Vented | 1 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 9.67 | 127.7352 | [18 empty] | 0 |  | 216
| 2364 | 18 | D | SSMHT0013013 | SS.MH.T0013013 | 32.3147 | -95.2743 | O18 | 3110 GOLDEN RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.1 | 208.496 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair | 217
| 2365 | 18 | D | SSMHT0013192 | SS.MH.T0013192 | 32.3077 | -95.2813 | O18 | 1600 BLK E SOUTH EAST LOOP 323 | Bolted |  | No | Drainage Ditch | Paved - Concrete | Below Grade | 2 | Std 48 Round | Concrete | 5.84 | 79.6304 | see note 1 |  |  | 2800 | [7 empty] | 2388.912 | [6 empty] | 5188.912 | Rehabilitate | 218
| 2366 | 18 | D | SSMHT0015197 | SS.MH.T0015197 | 32.2952 | -95.2748 | O19 | 2101 SHILOH RD | Solid |  | No | Gutter | Paved - Concrete | Below Grade | 1 | Std 48 Round | Concrete | 11.64 | 152.4784 | [14 empty] | 280 |  |  |  | 280 | Repair | 219
| 2367 | 18 | C | SSMHT0015437 | SS.MH.T0015437 | 32.2962 | -95.2725 | O19 | 4917 KIRKCALDEY DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.74 | 90.9344 | [18 empty] | 0 |  | 220
| 2368 | 18 | B | SSMHT0015722 | SS.MH.T0015722 | 32.304 | -95.2755 | O19 | 4222 SOUTHPARK DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 7.27 | 97.5912 | [18 empty] | 0 |  | 221
| 2369 | 18 | B | SSMHT0015723 | SS.MH.T0015723 | 32.3054 | -95.2769 | O19 | 2002 SYBIL LN | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.84 | 79.6304 | [18 empty] | 0 |  | 222
| 2370 | 18 | C | SSMHT0015765 | SS.MH.T0015765 | 32.2988 | -95.3055 | M19 | 4622 LEISURE LN | Solid |  | No | Driveway | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.01 | 94.3256 | [18 empty] | 0 |  | 223
| 2371 | 20 | C | SSMHT0014495 | SS.MH.T0014495 | 32.2608 | -95.2886 | O22 | 1217 WILDER WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 8.56 | 113.7936 | [18 empty] | 0 |  | 224
| 2372 | 20 | B | SSMHT0015473 | SS.MH.T0015473 | 32.2629 | -95.289 | N22 | NO # FURMAN CT | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 7.31 | 98.0936 | [18 empty] | 0 |  | 225
| 2373 | 20 | D | SSMHT0015673 | SS.MH.T0015673 | 32.2669 | -95.2801 | O22 | 8331 PALUXY DR | Bolted |  | No | Yard | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 8.5 | 113.04 | 2 | [6 empty] | 650 |  |  |  |  | 3391.2 |  | 280 |  |  |  | 4321.2 | Rehabilitate | 226
| 2374 | 20 | C | SSMHT0015674 | SS.MH.T0015674 | 32.2646 | -95.2808 | O19 | 8348 PALUXY DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 2 | Std 48 Round | Sealed Concrete | 9.96 | 131.3776 | [18 empty] | 0 |  | 227
| 2375 | 21 | C | SSMHT0015735 | SS.MH.T0015735 | 32.309 | -95.243 | P18 | 3831 WOODS BLVD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 7.92 | 105.7552 | [18 empty] | 0 |  | 228
| 2376 | 21 | D | SSMHT0015736 | SS.MH.T0015736 | 32.3125 | -95.2509 | P18 | 3905 UNIVERSITY BLVD | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 4.3 | 60.288 | [14 empty] | 280 |  |  |  | 280 | Repair | 229
| 2377 | 21 | B | SSMHT0015737 | SS.MH.T0015737 | 32.3028 | -95.2367 | Q19 | 4130 SAGEMONT LN | Solid |  | No | Driveway | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 10.12 | 133.3872 | [18 empty] | 0 |  | 230
[22 empty] | 22960 | 2000 | 2800 | 4000 | 6250 | 72000 | 62400 | 9750 | 9000 | 31900 | 36881.184 | 555395.664 | 1400 | 22120 | 16200 | 7012 | 33800 | 895868.848
[22 empty] | 164 | 2 | 1 | 8 | 5 | 24 | 96 | 5 | 9 | 44 | 18 | 136 | 2 | 79 | 18 | 1 | 13
[35 empty] | 89 vf | 1406 vf | Contingency 15% |  | 134380.3272
[35 empty] | 1229 sq.ft. | 18513 sq.ft. | Total |  | 1030249.1752
[25 empty] | Rehabilitation Methods: | [6 empty] | Quantity | Unit Price | Total
[25 empty] | Rehab 1001: Raise Manhole to Grade $1000 ea. | [6 empty] | 9 | 1000 | 9000
[25 empty] | Rehab.1010: Install Inflow Protector Insert $280 ea. | [6 empty] | 79 | 280 | 22120
[25 empty] | Rehab 1012: Install/Replace Missing or Defective Mainline Cleanout Cap or T-cone stopper $140 ea. | [6 empty] | 164 | 140 | 22960
|  |  |  | Condition Code | Occurrences | Total | [18 empty] | Rehab 1015: Mechanical Seal Chimney $1500 ea. | [6 empty] | 0 | 1500 | 0
|  |  |  | A | 191 | 0 | [18 empty] | Rehab 1020: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Unpaved $650 ea. | [6 empty] | 96 | 650 | 62400
|  |  |  | B | 986 | 0 | [18 empty] | Rehab 1021: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Paved $1950 ea. | [6 empty] | 5 | 1950 | 9750
|  |  |  | C | 543 | 0 | [18 empty] | Rehab 1022: Replace Manhole Ring & Cover (Rebuild Chimney as required) - Unpaved $1000 ea. | [6 empty] | 2 | 1000 | 2000
|  |  |  | D | 426 | 896031.848 | [18 empty] | Rehab 1024: Replace Manhole Lid $500 ea. | [6 empty] | 8 | 500 | 4000
|  |  |  | E | 1 | 7012 | [18 empty] | Rehab 1023WT: Watertight Bolt Down Ring and Cover - $2800 (See Note 1) | [6 empty] | 1 | 2800 | 2800
|  |  |  | X | 230 | 0 | [18 empty] | Rehab 1026: Replace Cleanout Casting and Cover (Unpaved) $1250 ea. | [6 empty] | 5 | 1250 | 6250
|  |  |  | Total | 2377 | 903043.848 | [18 empty] | Rehab 1028: Replace Cleanout Casting and Cover (Paved) $3000 ea. | [6 empty] | 24 | 3000 | 72000
|  |  |  | Design and Contingency -15% |  | 135456.5772 | [18 empty] | Rehab 1040: Clean Manhole, Remove any Roots, Repair as Needed and Coat , including bench (sq.ft.) | [6 empty] | 1229 | 30 | 36881
|  |  |  | Total Estimated Cost |  | 1038500.4252 | [18 empty] | Rehab 1041: Clean Manhole, Remove any Roots, Repair as Needed and Coat , including bench (sq.ft.) | [6 empty] | 18513 | 30 | 555396
[25 empty] | Rehab 1047: Seal Manhole Pipe Connection $900 ea. | [6 empty] | 18 | 900 | 16200
[25 empty] | Rehab 1110: Reconstruct 4 ft. diameter Manhole Bench & Invert $700 ea. | [6 empty] | 2 | 700 | 1400
[25 empty] | Rehab 1205: Repair Chimney and Seal with Elastomeric $725 ea. | [6 empty] | 44 | 725 | 31900
[25 empty] | Rehab 1505: Replace Manhole (>6 feet deep) Unpaved $6000+$200/vf > 6 feet | [6 empty] | 1 | 7012 | 7012
[25 empty] | Rehab 1600: Rehab 1600: Locate and Raise Manhole to Grade $2600 ea. | [6 empty] | 13 | 2600 | 33800
[31 empty] | Sub-total |  |  | 895869
[31 empty] | Design and Contingency -15% |  |  | 134380.35
[31 empty] | Total Estimated Cost |  |  | 1030249.35
Note on A481: Temple Williamson: 2143 with whatever rating at 805 Clark St 2144 – X rating, Buried at 823 Clark St (has since been inspected and will be reported in 2022) 2145 – X rating, Buried at 835 Clark St (has since been inspected and will be reported in 2022) 9194 – X rating, CNL 847 Clark St (has since been inspected and will be reported in 2022) NO 15806 from Mattie's email on 2-23-22
Note on A482: Temple Williamson: 2143 with whatever rating at 805 Clark St 2144 – X rating, Buried at 823 Clark St (has since been inspected and will be reported in 2022) 2145 – X rating, Buried at 835 Clark St (has since been inspected and will be reported in 2022) 9194 – X rating, CNL 847 Clark St (has since been inspected and will be reported in 2022) NO 15806 from Mattie's email on 2-23-22
Note on A702: Temple Williamson: 2143 with whatever rating at 805 Clark St 2144 – X rating, Buried at 823 Clark St (has since been inspected and will be reported in 2022) 2145 – X rating, Buried at 835 Clark St (has since been inspected and will be reported in 2022) 9194 – X rating, CNL 847 Clark St (has since been inspected and will be reported in 2022) NO 15806 from Mattie's email on 2-23-22
Note on A1823: Temple Williamson: SS.MH.T0005596 (condition rating X on your submitted table) was deleted from our GIS on Feb 14 due to Taplin reporting it DNE. See the asset change form they submitted. We will remove from the table and update our info accordingly.
Note on A2334: Temple Williamson: 2143 with whatever rating at 805 Clark St 2144 – X rating, Buried at 823 Clark St (has since been inspected and will be reported in 2022) 2145 – X rating, Buried at 835 Clark St (has since been inspected and will be reported in 2022) 9194 – X rating, CNL 847 Clark St (has since been inspected and will be reported in 2022) NO 15806 from Mattie's email on 2-23-22
Preliminary Repair Methods:
Rehabilitation Methods:
Rehab 1001: Raise Manhole to Grade $1000 ea.
Rehab 1002: Raise Manhole to Grade - Paved $1850
Rehab 1003: Locate and Raise Cleanout to Pavement Grade and Install T-Cone Stopper $1500 ea.
Rehab 1004: Locate and Raise Cleanout to Grade and Install T-Cone Stopper $600 ea.
Rehab.1010: Install Inflow Protector Insert $280 ea.
Rehab 1012: Install/Replace Missing or Defective Mainline Cleanout Cap or T-cone stopper $140 ea.
Rehab 1015: Mechanical Seal Chimney $1500 ea.
Rehab 1020: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Unpaved $650 ea.
Rehab 1021: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Paved $1950 ea.
Rehab 1022: Replace Manhole Ring & Cover (Rebuild Chimney as required) - Unpaved $1000 ea.
Rehab 1022WT: Same as 1022 except use Bolt Down Ring and Cover - $1500
Rehab 1023: Replace Manhole Ring & Cover (Rebuild Chimney as required) -Paved $1220 ea.
Rehab 1023WT: Same as 1023 except use Watertight Bolt Down Ring and Cover - $2800 (See Note 1)
Rehab 1024: Replace Manhole Lid $500 ea.
Rehab 1026: Replace Cleanout Casting and Cover (Unpaved) $1250 ea.
Rehab 1028: Replace Cleanout Casting and Cover (Paved) $3000 ea.
Rehab 1040/1041: Clean Manhole, Remove any Roots, Repair as Needed and Coat , including bench
Condition 1 - $21/sq.ft.
Condition 2 - $30/sq.ft.
Condition 3 - $40/sq.ft.
Rehab 1043: Repair/Plug Manhole Lift Holes $700 ea. Manhole (all holes)
Rehab 1047: Seal Manhole Pipe Connection $900 ea.
Rehab 1055: Remove Steps, Stop I/I and Repair as needed $700 ea.
Rehab 1110: Reconstruct 4 ft. diameter Manhole Bench & Invert $700 ea.
Rehab 1205: Repair Chimney and Seal with Elastomeric $725 ea.
Rehab 1215: Reconstruct Chimney/Cone $1000 ea.
Rehab 1502: Replace Manhole (< 6 feet deep) Paved $8400 ea.
Rehab 1503: Replace Manhole (>6 feet deep) Paved $8400+$250/vf>6 feet
Rehab 1504: Replace Manhole (< 6 feet deep) Unpaved $6000 ea.
Rehab 1505: Replace Manhole (>6 feet deep) Unpaved $6000+$200/vf > 6 feet
Rehab 1600: Locate and Raise Manhole to Grade $2600 ea.
Wall Condition 1
Condition Standard: An Existing structure that is considered structurally sound with no indications of settlement, cracking or other signs of fatigue. Infiltration or exfiltration through pre-cast joints, mortar joints, or around the pipe connections may exist and structure may be experiencing mild corrosion or deterioration.
Wall Condition 2
Condition Standard: An existing structure that is exhibiting early signs of structural fatigue evidenced by minor cracks, loss of mortar or brick, moderate to moderately severe corrosion (less ½ inch in depth), minor cross sectional distortion (less than 10 %); however, it is currently supporting the soil and live load.
Wall Condition 3
Condition Standard: An existing structure that is exhibiting severe structural fatigue and collapse is eminent. Conditions indicating this degree of deterioration may include very severe corrosion (loss of original profile of one inch or greater), cross sectional distortion beyond 10 percent, exposed reinforcing steel, loose or missing bricks, missing mortar, or large sections of the structure that are gone completely.
Note: Standard 48 inch diameter manhole used for estimating repair costs. Some brick manhole diameters are smaller and range from 24 inch to 48 inch diameter.
Condition Assessment Rating
A = Very Good
Minor defects are mostly cosmetic in nature and do not impact system hydraulics nor contribute to significant infiltration/inflow. No active infiltration.
B = Good
Manhole has no significant structural defects. Minor defects do not impact system hydraulics nor contribute to significant infiltration/inflow. No active infiltration. Minor defects may include slightly loose casting, minor corrosion of metal surfaces, minor deterioration of concrete mortar between bricks, minor cracks, etc. .
C = Fair
Manhole has no significant structural defects although minor defects were noted during inspection. System hydraulics are good and no significant infiltration/inflow sources noted. Light infiltration/inflow may be present. Nominal defects may include loose casting, nominal corrosion of metal surfaces, deterioration of concrete mortar between bricks or concrete walls, minor evidence of infiltration/inflow at precast joint sections, etc.
D = Poor
Manhole has moderate structural defects that may include cracks, loose bricks, separated casting, moderate root intrusion, broken cover and defects that may impact system hydraulics due to structural issues or contribute to significant infiltration/inflow. Some visible staining due to infiltration/inflow may be present. Active infiltration may have been observed. Moderate to severe defects may include loose casting, moderate to severe corrosion of metal surfaces, deterioration of concrete mortar between bricks, moderate to severe deterioration of precast wall sections and precast joint defects, etc. Manhole inspection was completed and the manhole will be addressed in the remediation plan.
E=Very Poor
Manhole may have severe structural defects that may include potential for structural failure, missing bricks, separated/broken casting, severe root intrusion, broken/missing cover and defects that may impact system hydraulics or contribute to significant infiltration/inflow. Visible staining due to infiltration/inflow ma y be present. Active infiltration may have been observed. Severe defects may include separated/broken casting/cover, severe corrosion of metal surfaces, missing mortar between bricks, etc. Manhole inspection was completed and the manhole will be addressed in the remediation plan or immediate repair may be warranted based on condition.
X= Incomplete Data
The asset may not exist, is a end of line segment, or could not be inspected due to being buried, no access, could not open, etc. CCTV results will be used to confirm if the asset exists. Buried and could not open manholes are being raised to grade and/or casting replaced to facilitate inspection. No other remedial measures at this time.
X-CNL (Could Not Locate- awaiting CCTV)
X-CNO (Could Not Open) - On Problem List
X-Buried - On Problem List
X-Access - On Problem List
*Note 1: Rehab 1023WT - Verify waterproof seal condition and and if good replace missing bolts or replace ring and cover with watertight ring and cover.

## Manhole Remedial Measures Plan
[35 empty] | Condition Code | Occurrences | Total
[35 empty] | A | 191 | 0
[35 empty] | B | 986 | 0
[35 empty] | C | 543 | 0
[35 empty] | D | 427 | 888856.848
[35 empty] | E | 1 | 7012
[35 empty] | X | 229 | 0
[35 empty] | Total | 2377 | 895868.848
[35 empty] | Design and Contingency -15% |  | 134380.3272
[35 empty] | Total Estimated Cost |  | 1030249.1752
Group 5 Manhole Remedial Measures Plan
Manhole Inspection Basins 1, 2, 3, 5, 6, 7, 8, 10, 11, 12, 13, 14, 15, 16, 17, 18, 19, 20, 21, U2 | [20 empty] | Preliminary Rehabilitation Code | [16 empty] | Total | Remedial Measures Plan Recommendation
Item | Basin | Condition Rating | Manhole ID | Asset ID | GPS Lat | GPS Long | Map Grid | Address | Lid Type | Vent Holes | Inflow Dish | Surface Cover | Surface Material | Manhole Grade | Grade (inches) | Manhole Diameter | MH Material | Rim to Invert (feet) | Wall Coating (sq.ft.) | Wall Condition Rating | 1012 | 1022 | 1023WT | 1024 | 1026 | 1028 | 1020 | 1021 | 1001 | 1205 | 1040 | 1041 | 1110 | 1010 | 1047 | 1505 | 1600
1 | 2 | D | SSMHT0002370 | SS.MH.T0002370 | 32.3768 | -95.3227 | L12 | 2524 CECIL AVE | Vented | 2 | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Brick | 5.6 | 76.616 | 2 | [10 empty] | 2298.48 |  |  | 280 |  |  |  | 2578.48 | Rehabilitate
2 | 2 | D | SSMHT0002739 | SS.MH.T0002739 | 32.3685 | -95.319 | L13 | 1800 N. GLENWOOD BLVD | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 10.18 | 134.1408 | 2 | [11 empty] | 4024.224 | [5 empty] | 4024.224 | Rehabilitate
3 | 2 | D | SSMHT0002740 | SS.MH.T0002740 | 32.3685 | -95.3181 | M13 | 1803 N. HILL AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 32 | Brick | 7.26 | 97.4656 | 2 | [11 empty] | 2923.968 | [5 empty] | 2923.968 | Rehabilitate
4 | 2 | D | SSMHT0002741 | SS.MH.T0002741 | 32.3685 | -95.3176 | M13 | 1530 W. NUTBUSH ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 5.34 | 73.3504 | 2 | [7 empty] | 1950 |  |  | 2200.512 | [6 empty] | 4150.512 | Rehabilitate
5 | 2 | D | SSMHT0002744 | SS.MH.T0002744 | 32.3685 | -95.3146 | M13 | 1221 W. NUTBUSH ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.1 | 82.896 | 2 | [11 empty] | 2486.88 |  | 280 |  |  |  | 2766.88 | Rehabilitate
6 | 2 | D | SSMHT0002749 | SS.MH.T0002749 | 32.3661 | -95.318 | M13 | 1533 N. HILL AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.32 | 85.6592 | 2 | [11 empty] | 2569.776 | [5 empty] | 2569.776 | Rehabilitate
7 | 2 | D | SSMHT0002753 | SS.MH.T0002753 | 32.3768 | -95.3217 | L12 | 2524 CECIL AVE | Vented | 1 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.18 | 96.4608 | 2 | [11 empty] | 2893.824 | [5 empty] | 2893.824 | Rehabilitate
8 | 2 | D | SSMHT0002754 | SS.MH.T0002754 | 32.3764 | -95.3217 | L12 | 2524 CECIL AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 46 | Brick | 6.98 | 93.9488 | 2 | [11 empty] | 2818.464 | [5 empty] | 2818.464 | Rehabilitate
9 | 2 | D | SSMHT0002773 | SS.MH.T0002773 | 32.3791 | -95.3199 | L12 | 2801 COMMONWEALTH DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.95 | 118.692 | [10 empty] | 725 | [7 empty] | 725 | Repair
10 | 2 | D | SSMHT0002920 | SS.MH.T0002920 | 32.3703 | -95.3185 | M13 | 1621 W. MLK JR BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 9.02 | 119.5712 | 2 | [7 empty] | 1950 |  |  |  | 3587.136 |  | 280 |  |  |  | 5817.136 | Rehabilitate
11 | 2 | D | SSMHT0002930 | SS.MH.T0002930 | 32.3712 | -95.3219 | L13 | 2801 N. WOLFORD AVE | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 9.78 | 129.1168 | 2 | [11 empty] | 3873.504 | [5 empty] | 3873.504 | Rehabilitate
12 | 2 | D | SSMHT0002932 | SS.MH.T0002932 | 32.3699 | -95.322 | L13 | 1824 W. MLK JR. BLVD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 3 | 42 | Brick | 14.3 | 185.888 | 2 | [8 empty] | 1000 |  |  | 5576.64 |  | 280 |  |  |  | 6856.64 | Rehabilitate
13 | 2 | D | SSMHT0002933 | SS.MH.T0002933 | 32.3708 | -95.3232 | L13 | 2203 W. MLK JR. BLVD | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.2 | 121.832 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
14 | 2 | D | SSMHT0002982 | SS.MH.T0002982 | 32.3749 | -95.3155 | M12 | 2500 N CONFEDERATE AVE | Vented | 2 | No | Yard | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 5.84 | 79.6304 | [7 empty] | 650 | [10 empty] | 650 | Repair
15 | 2 | D | SSMHT0008237 | SS.MH.T0008237 | 32.3849 | -95.3351 | L11 | 3137 CLUB LAKE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.6 | 89.176 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
16 | 2 | D | SSMHT0008250 | SS.MH.T0008250 | 32.3802 | -95.3423 | K12 | 3400 BLK BENBROOK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.77 | 91.3112 | 2 | [11 empty] | 2739.336 |  | 280 |  |  |  | 3019.336 | Rehabilitate
17 | 2 | D | SSMHT0008251 | SS.MH.T0008251 | 32.3811 | -95.3423 | K12 | 2928 ORR DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.97 | 93.8232 | 2 |  |  |  | 500 | [7 empty] | 2814.696 |  | 280 |  |  |  | 3594.696 | Rehabilitate
18 | 2 | D | SSMHT0008252 | SS.MH.T0008252 | 32.3813 | -95.3423 | K12 | 2932 ORR DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.14 | 83.3984 | [14 empty] | 280 |  |  |  | 280 | Repair
19 | 2 | D | SSMHT0008253 | SS.MH.T0008253 | 32.3815 | -95.3423 | K12 | 3000 ORR DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | 42 | Brick | 6.2 | 84.152 | 2 | [11 empty] | 2524.56 | [5 empty] | 2524.56 | Rehabilitate
20 | 2 | D | SSMHT0008292 | SS.MH.T0008292 | 32.3819 | -95.3432 | K12 | 3504 PINE HAVEN RD | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 29 | Std 48 Round | Concrete | 9.58 | 126.6048 | 2 | [11 empty] | 3798.144 | [5 empty] | 3798.144 | Rehabilitate
21 | 2 | D | SSMHT0008293 | SS.MH.T0008293 | 32.3812 | -95.3432 | K12 | 3504 PINE HAVEN RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 5.67 | 77.4952 | 2 | [6 empty] | 650 |  |  |  | 2324.856 | [6 empty] | 2974.856 | Rehabilitate
22 | 2 | D | SSMHT0008596 | SS.MH.T0008596 | 32.3778 | -95.3482 | K12 | 3812 CR 427 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 4.42 | 61.7952 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
23 | 2 | D | SSMHT0008983 | SS.MH.T0008983 | 32.3838 | -95.3289 | L12 | 3357 POINTE N DR | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 13.2 | 172.072 | 2 | [11 empty] | 5162.16 |  | 280 |  |  |  | 5442.16 | Rehabilitate
24 | 2 | D | SSMHT0008984 | SS.MH.T0008984 | 32.3861 | -95.3282 | L11 | 3450 CORPORATE DR | Solid |  | No | Parking Lot | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.06 | 120.0736 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
25 | 2 | D | SSMHT0008991 | SS.MH.T0008991 | 32.3861 | -95.3353 | L11 | 3141 LAKE CLUB DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 6.42 | 86.9152 |  |  |  |  | 500 | [5 empty] | 725 | [7 empty] | 1225 | Repair
26 | 2 | D | SSMHT0008993 | SS.MH.T0008993 | 32.3888 | -95.335 | L11 | 3728 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.53 | 100.8568 | 2 | [6 empty] | 650 |  |  |  |  | 3025.704 |  | 280 |  |  |  | 3955.704 | Rehabilitate
27 | 2 | D | SSMHT0009001 | SS.MH.T0009001 | 32.3878 | -95.3371 | L11 | 3141 LAKE CLUB DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 6.87 | 92.5672 | 2 | [11 empty] | 2777.016 | [5 empty] | 2777.016 | Rehabilitate
28 | 2 | D | SSMHT0009008 | SS.MH.T0009008 | 32.3841 | -95.3333 | L11 | 3364 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | Above Grade | 23 | Std 48 Round | Brick | 10.74 | 141.1744 | 2 | [11 empty] | 4235.232 | [5 empty] | 4235.232 | Rehabilitate
29 | 2 | D | SSMHT0009009 | SS.MH.T0009009 | 32.3845 | -95.3331 | L11 | 3364 MINEOLA HWY (69) | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.14 | 108.5184 | 2 | [11 empty] | 3255.552 | [5 empty] | 3255.552 | Rehabilitate
30 | 2 | D | SSMHT0009010 | SS.MH.T0009010 | 32.3878 | -95.3336 | L11 | 3611 MINEOLA HWY (69) | Vented | 2 | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 7.4 | 99.224 | 2 | [11 empty] | 2976.72 | [5 empty] | 2976.72 | Rehabilitate
31 | 2 | D | SSMHT0009205 | SS.MH.T0009205 | 32.3692 | -95.3218 | L13 | 1806 NANCY DR | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Brick | 7.2 | 96.712 | 2 | [6 empty] | 650 |  |  |  |  | 2901.36 |  | 280 |  |  |  | 3831.36 | Rehabilitate
32 | 2 | D | SSMHT0009861 | SS.MH.T0009861 | 32.3796 | -95.3368 | L12 | 3111 W. NW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 5 | CO 6" | Other | 7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
33 | 2 | D | SSMHT0010121 | SS.MH.T0010121 | 32.368 | -95.319 | L13 | 1715 N. GLENWOOD BLVD | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 7.8 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
34 | 2 | D | SSMHT0010473 | SS.MH.T0010473 | 32.3839 | -95.3374 | L12 | 3108 LAKEWOOD DR | Solid |  | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 11.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
35 | 2 | D | SSMHT0010475 | SS.MH.T0010475 | 32.3805 | -95.3358 | L12 | 3016 BENBROOK DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | CO 6" | Other | 10.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
36 | 2 | D | SSMHT0010489 | SS.MH.T0010489 | 32.3759 | -95.3482 | K12 | 3750 CR 427 | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other |  |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
37 | 2 | D | SSMHT0011340 | SS.MH.T0011340 | 32.3745 | -95.3175 | M12 | 1424 SOUTHRIDGE DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
38 | 2 | D | SSMHT0012508 | SS.MH.T0012508 | 32.3693 | -95.319 | L13 | 1825 N. GLENWOOD BLVD | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 5.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
39 | 2 | D | SSMHT0013422 | SS.MH.T0013422 | 32.3736 | -95.3229 | L12 | 2203 W. MLK JR. BLVD | Solid |  | No | Creek | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 8.47 | 112.6632 | [7 empty] | 650 |  |  | 725 |  |  | 700 |  | 900 |  |  | 2975 | Repair
40 | 2 | D | SSMHT0013423 | SS.MH.T0013423 | 32.372 | -95.3235 | L13 | 2203 W. MLK JR. BLVD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | Std 48 Round | Brick | 8.24 | 109.7744 | 2 | [6 empty] | 650 |  |  |  |  | 3293.232 |  | 280 |  |  |  | 4223.232 | Rehabilitate
41 | 2 | D | SSMHT0013528 | SS.MH.T0013528 | X-CNL | X-CNL | NA | 274' US of 02927 |  |  |  | Trees/Woods | Unpaved | [23 empty] | 2600 | 2600 | Repair
42 | 2 | D | SSMHT0014316 | SS.MH.T0014316 | 32.3737 | -95.3146 | M13 | 2400 N. CONFEDERATE AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | 42 | Brick | 6.34 | 85.9104 | 2 | [6 empty] | 650 |  |  |  |  | 2577.312 | [5 empty] | 3227.312 | Rehabilitate
43 | 2 | D | SSMHT0015530 | SS.MH.T0015530 | 32.389 | -95.3351 | L11 | 3802 MINEOLA HWY (69) | Vented | 2 | No | Drainage Ditch | Unpaved | At Grade |  | Std 48 Round | Concrete | 7.26 | 97.4656 | 2 | [11 empty] | 2923.968 |  | 280 |  |  |  | 3203.968 | Rehabilitate
44 | 2 | D | SSMHT0015532 | SS.MH.T0015532 | 32.3827 | -95.324 | L12 | 2202 W. NW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 10.92 | 143.4352 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
45 | 2 | D | SSMHT0015649 | SS.MH.T0015649 | 32.3827 | -95.3246 | L12 | 2202 W. NW LP 323 | Solid |  | No | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 8.26 | 110.0256 | 2 | [6 empty] | 650 |  |  |  |  | 3300.768 | [5 empty] | 3950.768 | Rehabilitate
46 | 3 | D | SSMHT0000263 | SS.MH.T0000263 | 32.3625 | -95.4087 | H14 | 700 SKYWAY BLVD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 25.36 | 324.8016 | [7 empty] | 650 | [10 empty] | 650 | Repair
47 | 3 | D | SSMHT0007483 | SS.MH.T0007483 | 32.355 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 10.32 | 135.8992 | [7 empty] | 650 | [7 empty] | 900 |  |  | 1550 | Repair
48 | 3 | D | SSMHT0007484 | SS.MH.T0007484 | 32.3563 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 13.84 | 180.1104 | 2 | [6 empty] | 650 |  |  |  |  | 5403.312 | [5 empty] | 6053.312 | Rehabilitate
49 | 3 | D | SSMHT0007485 | SS.MH.T0007485 | 32.3575 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 23 | 295.16 | 2 | [11 empty] | 8854.8 | [5 empty] | 8854.8 | Rehabilitate
50 | 3 | D | SSMHT0007486 | SS.MH.T0007486 | 32.3587 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 14 | Std 48 Round | Concrete | 13.6 | 177.096 | 2 | [6 empty] | 650 |  |  |  |  | 5312.88 | [5 empty] | 5962.88 | Rehabilitate
51 | 3 | D | SSMHT0007487 | SS.MH.T0007487 | 32.36 | -95.4074 | H14 | 700 SKYWAY BLVD | Solid |  | No | Field | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 15.05 | 195.308 | 2 | [11 empty] | 5859.24 | [5 empty] | 5859.24 | Rehabilitate
52 | 3 | D | SSMHT0008426 | SS.MH.T0008426 | 32.3614 | -95.401 | H14 | 150 AIRPORT DR | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 19 | Std 48 Round | Concrete | 7.98 | 106.5088 | 2 | [6 empty] | 650 |  |  |  |  | 3195.264 | [5 empty] | 3845.264 | Rehabilitate
53 | 3 | D | SSMHT0008432 | SS.MH.T0008432 | 32.3593 | -95.3987 | H14 | 150 AIRPORT DR | Solid |  |  | Sidewalk | Paved - Concrete | At Grade |  |  |  | 5.34 | 73.3504 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
54 | 3 | D | SSMHT0009747 | SS.MH.T0009747 | 32.3531 | -95.4095 | H14 | 700 SKYWAY BLVD | None |  | No | Parking Lot | Unpaved | Above Grade | 7 | CO 6" | Other |  |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
55 | 3 | D | SSMHT0010483 | SS.MH.T0010483 | 32.3644 | -95.3955 | I13 | 345 PRINCESS PL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
56 | 3 | D | SSMHT0013517 | SS.MH.T0013517 | 32.3659 | -95.3926 | I13 | 13390 OLD DALLAS HWY | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 11.58 | 151.7248 | [7 empty] | 650 | [10 empty] | 650 | Repair
57 | 3 | D | SSMHT0013778 | SS.MH.T0013778 | 32.3648 | -95.396 | I13 | 449 WELLINGTON PL BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
58 | 3 | D | SSMHT0015611 | SS.MH.T0015611 | 32.3658 | -95.3923 | I13 | 13390 OLD DALLAS HWY | Solid |  | No | Field | Unpaved | Above Grade | 16 | Std 48 Round | Concrete | 12.16 | 159.0096 | [7 empty] | 650 | [10 empty] | 650 | Repair
59 | 3 | D | SSMHT0015621 | SS.MH.T0015621 | 32.3644 | -95.3918 | I13 | 13390 OLD DALLAS HWY | Solid |  | No | Field | Unpaved | Above Grade | 34 | CO 6" | PVC | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
60 | 5 | D | SSMHT0001161 | SS.MH.T0001161 | 32.3441 | -95.3513 | NA | 4550STATE HWY 31 W | Vented | 1 | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 13.13 | 171.1928 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
61 | 5 | D | SSMHT0001175 | SS.MH.T0001175 | 32.3421 | -95.3404 | K15 | NONE S. SW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Brick | 10.8 | 141.928 | 2 | [11 empty] | 4257.84 |  | 280 |  |  |  | 4537.84 | Rehabilitate
62 | 5 | D | SSMHT0001178 | SS.MH.T0001178 | 32.3421 | -95.3419 | K15 | 3807 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.88 | 168.0528 | 2 | [11 empty] | 5041.584 | [5 empty] | 5041.584 | Rehabilitate
63 | 5 | D | SSMHT0001179 | SS.MH.T0001179 | 32.3421 | -95.3428 | K15 | 3917 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.2 | 134.392 | 2 | [11 empty] | 4031.76 | [5 empty] | 4031.76 | Rehabilitate
64 | 5 | D | SSMHT0001189 | SS.MH.T0001189 | 32.3216 | -95.3332 | L17 | NONE TOL AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 8.5 | 113.04 | 2 | [6 empty] | 650 |  |  |  |  | 3391.2 | [5 empty] | 4041.2 | Rehabilitate
65 | 5 | D | SSMHT0001190 | SS.MH.T0001190 | 32.3215 | -95.3302 | L17 | 2502 WALTON RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 11 | 144.44 | 2 | [6 empty] | 650 |  |  |  |  | 4333.2 | [5 empty] | 4983.2 | Rehabilitate
66 | 5 | D | SSMHT0001191 | SS.MH.T0001191 | 32.3218 | -95.33 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 10.86 | 142.6816 | 2 | [11 empty] | 4280.448 | [5 empty] | 4280.448 | Rehabilitate
67 | 5 | D | SSMHT0001192 | SS.MH.T0001192 | 32.3208 | -95.3304 | L17 | 2505 WALTON RD | Bolted |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 8.05 | 107.388 | 2 | [6 empty] | 650 |  |  |  |  | 3221.64 | [5 empty] | 3871.64 | Rehabilitate
68 | 5 | D | SSMHT0001193 | SS.MH.T0001193 | 32.3201 | -95.3302 | L17 | 2500 BLK WALTON RD | Bolted |  | No | Field | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 19.28 | 248.4368 | 2 | [6 empty] | 650 |  |  |  |  | 7453.104 | [5 empty] | 8103.104 | Rehabilitate
69 | 5 | D | SSMHT0001217 | SS.MH.T0001217 | 32.316 | -95.331 | L18 | 3000 BLK BUDDIE ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Sealed Concrete | 11.69 | 153.1064 | 2 | [11 empty] | 4593.192 | [5 empty] | 4593.192 | Rehabilitate
70 | 5 | D | SSMHT0001218 | SS.MH.T0001218 | 32.3157 | -95.3298 | L18 | 2516 FRANCHEL ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.18 | 159.2608 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
71 | 5 | D | SSMHT0001219 | SS.MH.T0001219 | 32.3366 | -95.34 | K16 | 1000 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 5.72 | 78.1232 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
72 | 5 | D | SSMHT0001225 | SS.MH.T0001225 | 32.3188 | -95.3311 | L17 | 2800 WALTON RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 8.6 | 114.296 | 2 | [6 empty] | 650 |  |  |  |  | 3428.88 | [5 empty] | 4078.88 | Rehabilitate
73 | 5 | D | SSMHT0001236 | SS.MH.T0001236 | 32.3159 | -95.3323 | L18 | 2835 LUTHER ST | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Fiberglass | 10.83 | 142.3048 | [15 empty] | 900 |  |  | 900 | Repair
74 | 5 | D | SSMHT0001240 | SS.MH.T0001240 | 32.3469 | -95.3436 | K15 | 352 WHITESIDE RD | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 5.06 | 69.8336 | 2 | [10 empty] | 2095.008 | [6 empty] | 2095.008 | Rehabilitate
75 | 5 | D | SSMHT0001313 | SS.MH.T0001313 | 32.3418 | -95.3469 | K15 | 4191 BELLWOOD RD | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 7.6 | 101.736 | 2 | [11 empty] | 3052.08 |  | 280 |  |  |  | 3332.08 | Rehabilitate
76 | 5 | D | SSMHT0001464 | SS.MH.T0001464 | 32.316 | -95.3502 | K18 | BLDG 40 WEXFORD DR | Solid |  | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 8.36 | 111.2816 | 2 | [11 empty] | 3338.448 | [5 empty] | 3338.448 | Rehabilitate
77 | 5 | D | SSMHT0002057 | SS.MH.T0002057 | 32.3441 | -95.3506 | K15 | 4430 STATE HWY 31 W | Vented | 1 | No | Road Shoulder | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 13.46 | 175.3376 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
78 | 5 | D | SSMHT0002074 | SS.MH.T0002074 | 32.3415 | -95.3366 | L15 | 703 DUCKENFIELD AVE | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 31 | Std 48 Round | Brick | 10.04 | 132.3824 | 2 | [11 empty] | 3971.472 | [5 empty] | 3971.472 | Rehabilitate
79 | 5 | D | SSMHT0002075 | SS.MH.T0002075 | 32.3413 | -95.3367 | L15 | 703 DUCKENFIELD AVE | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 30 | Std 48 Round | Brick | 10.04 | 132.3824 | 2 | [11 empty] | 3971.472 | [5 empty] | 3971.472 | Rehabilitate
80 | 5 | D | SSMHT0002077 | SS.MH.T0002077 | 32.3421 | -95.3384 | L15 | 3400 BLK BELLWOOD RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.86 | 142.6816 | 2 | [11 empty] | 4280.448 | [5 empty] | 4280.448 | Rehabilitate
81 | 5 | D | SSMHT0002078 | SS.MH.T0002078 | 32.3411 | -95.3372 | L15 | 726 BOYD AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 1 | Std 48 Round | Brick | 8.63 | 114.6728 | 2 | [11 empty] | 3440.184 | [5 empty] | 3440.184 | Rehabilitate
82 | 5 | D | SSMHT0002090 | SS.MH.T0002090 | 32.3378 | -95.3294 | L16 | 1001 CROSBY ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | 28 | Brick | 3.22 | 46.7232 | 2 | [10 empty] | 1401.696 | [6 empty] | 1401.696 | Rehabilitate
83 | 5 | D | SSMHT0002096 | SS.MH.T0002096 | 32.3399 | -95.328 | L15 | 841 BUCKLEY AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.8 | 104.248 | 2 | [11 empty] | 3127.44 | [5 empty] | 3127.44 | Rehabilitate
84 | 5 | D | SSMHT0002099 | SS.MH.T0002099 | 32.3413 | -95.33 | L15 | 2600 BLK BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.71 | 90.5576 | 2 | [11 empty] | 2716.728 | [5 empty] | 2716.728 | Rehabilitate
85 | 5 | D | SSMHT0002105 | SS.MH.T0002105 | 32.3375 | -95.3337 | L16 | 1108 BRITTON AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.52 | 125.8512 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
86 | 5 | D | SSMHT0002113 | SS.MH.T0002113 | 32.3415 | -95.3361 | L15 | 703 DUCKENFIELD AVE | Solid |  | No | Road Shoulder | Unpaved | At Grade | 3 | Std 48 Round | Brick | 10.96 | 143.9376 | 2 | [6 empty] | 650 |  |  |  |  | 4318.128 | [5 empty] | 4968.128 | Rehabilitate
87 | 5 | D | SSMHT0002114 | SS.MH.T0002114 | 32.3421 | -95.3361 | L15 | 3210 BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 7.1 | 95.456 | 2 | [11 empty] | 2863.68 | [5 empty] | 2863.68 | Rehabilitate
88 | 5 | D | SSMHT0002115 | SS.MH.T0002115 | 32.3422 | -95.3338 | L15 | 700 BRITTON AVE | Solid |  | No | Gutter | Paved - Concrete | At Grade |  | Std 48 Round | Brick | 4.2 | 59.032 | 2 | [10 empty] | 1770.96 | [6 empty] | 1770.96 | Rehabilitate
89 | 5 | D | SSMHT0002119 | SS.MH.T0002119 | 32.3403 | -95.3319 | L15 | 812 S. TURNER AVE | Solid |  | No | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Concrete | 7.96 | 106.2576 | 2 | [11 empty] | 3187.728 |  | 280 |  |  |  | 3467.728 | Rehabilitate
90 | 5 | D | SSMHT0002126 | SS.MH.T0002126 | 32.3391 | -95.3403 | K16 | 915 S. SW LP 323 | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 12.72 | 166.0432 | 2 | [6 empty] | 650 |  |  |  |  | 4981.296 |  | 280 |  |  |  | 5911.296 | Rehabilitate
91 | 5 | D | SSMHT0002134 | SS.MH.T0002134 | 32.3454 | -95.3422 | K15 | 3801 CHANDLER HWY | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 6.1 | 82.896 | 2 | [11 empty] | 2486.88 | [5 empty] | 2486.88 | Rehabilitate
92 | 5 | D | SSMHT0002135 | SS.MH.T0002135 | 32.3451 | -95.3436 | K15 | 3921 CHANDLER HWY | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 13.61 | 177.2216 | 2 | [7 empty] | 1950 |  |  |  | 5316.648 | [5 empty] | 7266.648 | Rehabilitate
93 | 5 | D | SSMHT0002136 | SS.MH.T0002136 | 32.3427 | -95.3435 | K15 | 637 WHITESIDE RD | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 7.23 | 97.0888 | 2 | [11 empty] | 2912.664 |  | 280 |  |  |  | 3192.664 | Rehabilitate
94 | 5 | D | SSMHT0002143 | SS.MH.T0002143 | 32.3406 | -95.3301 | L15 | 805 CLARK ST | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.63 | 114.6728 | 2 | [11 empty] | 3440.184 | [5 empty] | 3440.184 | Rehabilitate
95 | 5 | D | SSMHT0002155 | SS.MH.T0002155 | 32.3465 | -95.3481 | K15 | 4229 OLD CHANDLER RD | Solid |  | No | Street | Paved - Asphalt | Below Grade | 2 | Std 48 Round | Concrete | 9.91 | 130.7496 | [8 empty] | 1950 | [5 empty] | 280 |  |  |  | 2230 | Repair
96 | 5 | D | SSMHT0002157 | SS.MH.T0002157 | 32.3159 | -95.3329 | L18 | 3111 SEATON ST | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.34 | 85.9104 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
97 | 5 | D | SSMHT0002227 | SS.MH.T0002227 | 32.3088 | -95.3383 | L18 | 3021 MC CORMICK LN | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 6.8 | 91.688 | 2 | [6 empty] | 650 |  |  |  |  | 2750.64 | [5 empty] | 3400.64 | Rehabilitate
98 | 5 | D | SSMHT0002228 | SS.MH.T0002228 | 32.3093 | -95.3379 | L18 | 3432 S. SE LP 323 | Solid |  | No | Parking Lot | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 8 | 106.76 | 2 | [6 empty] | 650 |  |  |  |  | 3202.8 | [5 empty] | 3852.8 | Rehabilitate
99 | 5 | D | SSMHT0002235 | SS.MH.T0002235 | 32.3193 | -95.3267 | L17 | 2224 WALTON RD | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | 30 | Brick | 5.17 | 71.2152 | 2 | [10 empty] | 2136.456 | [6 empty] | 2136.456 | Rehabilitate
100 | 5 | D | SSMHT0002253 | SS.MH.T0002253 | 32.3367 | -95.3267 | L16 | 2325 W.SHAW ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.86 | 92.4416 | 2 |  |  |  | 500 | [7 empty] | 2773.248 | [5 empty] | 3273.248 | Rehabilitate
101 | 5 | D | SSMHT0002294 | SS.MH.T0002294 | 32.312 | -95.3371 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 8.5 | 113.04 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
102 | 5 | D | SSMHT0002295 | SS.MH.T0002295 | 32.3117 | -95.3362 | L18 | 3110 (22) TOWNE PARK DR | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 11.42 | 149.7152 | [7 empty] | 650 | [10 empty] | 650 | Repair
103 | 5 | D | SSMHT0002296 | SS.MH.T0002296 | 32.3114 | -95.3365 | L18 | 3110 TOWNE PARK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 6.52 | 88.1712 | [7 empty] | 650 | [7 empty] | 900 |  |  | 1550 | Repair
104 | 5 | D | SSMHT0002315 | SS.MH.T0002315 | 32.3414 | -95.3372 | L15 | 714 BOYD AVE | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 10.68 | 140.4208 | 2 | [11 empty] | 4212.624 | [5 empty] | 4212.624 | Rehabilitate
105 | 5 | D | SSMHT0002320 | SS.MH.T0002320 | 32.3225 | -95.3314 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 26 | Std 48 Round | Concrete | 11 | 144.44 | 2 |  |  |  | 500 |  |  | 650 |  |  |  |  | 4333.2 | [5 empty] | 5483.2 | Rehabilitate
106 | 5 | D | SSMHT0002321 | SS.MH.T0002321 | 32.3231 | -95.3331 | L17 | NONE TOL AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 8.89 | 117.9384 | 2 | [11 empty] | 3538.152 | [5 empty] | 3538.152 | Rehabilitate
107 | 5 | D | SSMHT0002322 | SS.MH.T0002322 | 32.3237 | -95.3312 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 35 | Std 48 Round | Concrete | 11.8 | 154.488 | 2 | [11 empty] | 4634.64 | [5 empty] | 4634.64 | Rehabilitate
108 | 5 | D | SSMHT0002323 | SS.MH.T0002323 | 32.3242 | -95.3324 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 23 | Std 48 Round | Concrete | 7.86 | 105.0016 | [14 empty] | 280 |  |  |  | 280 | Repair
109 | 5 | D | SSMHT0002706 | SS.MH.T0002706 | 32.3187 | -95.3419 | K18 | 2772 S. SE LP 323 | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 9.37 | 123.9672 | 2 | [11 empty] | 3719.016 |  | 280 |  |  |  | 3999.016 | Rehabilitate
110 | 5 | D | SSMHT0003335 | SS.MH.T0003335 | 32.3461 | -95.3389 | K15 | 3501 CHANDLER HWY | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 5.66 | 77.3696 | 2 | [6 empty] | 650 |  |  |  | 2321.088 |  |  | 280 |  |  |  | 3251.088 | Rehabilitate
111 | 5 | D | SSMHT0005672 | SS.MH.T0005672 | 32.3183 | -95.3419 | K18 | 2850 S. SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 9.36 | 123.8416 | 2 | [11 empty] | 3715.248 | [5 empty] | 3715.248 | Rehabilitate
112 | 5 | D | SSMHT0009403 | SS.MH.T0009403 | 32.316 | -95.3287 | L18 | 3020 RHINEHART ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.25 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
113 | 5 | D | SSMHT0009407 | SS.MH.T0009407 | 32.3421 | -95.339 | L15 | 3400 BLK BELLWOOD RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
114 | 5 | D | SSMHT0009483 | SS.MH.T0009483 | 32.3213 | -95.3417 | K17 | 2700 S.SW LP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 4.52 | 63.0512 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
115 | 5 | D | SSMHT0009484 | SS.MH.T0009484 | 32.342 | -95.3526 | K15 | 4550 ST HWY 31 W. | None |  | No | Trees/Woods | Unpaved | Above Grade | 7 | CO 6" | Other | 3 |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
116 | 5 | D | SSMHT0009490 | SS.MH.T0009490 | 32.3406 | -95.3267 | L15 | 2310 BELLWOOD RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
117 | 5 | D | SSMHT0009493 | SS.MH.T0009493 | 32.3366 | -95.329 | L16 | 2515 W. SHAW ST | Vented |  | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 4.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
118 | 5 | D | SSMHT0009494 | SS.MH.T0009494 | 32.339 | -95.3319 | L16 | 902 S. TURNER ST | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other | 6.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
119 | 5 | D | SSMHT0009495 | SS.MH.T0009495 | 32.3389 | -95.3319 | L16 | 902 S. TURNER ST | Vented |  | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 13 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
120 | 5 | D | SSMHT0009496 | SS.MH.T0009496 | 32.3389 | -95.336 | L16 | 930 DUCKENFIELD AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
121 | 5 | D | SSMHT0009497 | SS.MH.T0009497 | 32.3388 | -95.336 | L16 | 936 DUCKENFIELD AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
122 | 5 | D | SSMHT0009635 | SS.MH.T0009635 | 32.3184 | -95.3332 | L17 | 2902 MOOREHEAD ST | Vented | 2 | No | Gutter | Paved - Concrete | At Grade |  | CO 6" | Other | 9.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
123 | 5 | D | SSMHT0009636 | SS.MH.T0009636 | 32.3133 | -95.3362 | L18 | 3110 TOWNE PARK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.8 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
124 | 5 | D | SSMHT0009637 | SS.MH.T0009637 | 32.315 | -95.3406 | K18 | 3120 S. SW LP 323 | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
125 | 5 | D | SSMHT0009695 | SS.MH.T0009695 | 32.3133 | -95.3553 | K18 | 3468 PINE TERRACE DR | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 8" | Other | 8.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
126 | 5 | D | SSMHT0009719 | SS.MH.T0009719 | 32.3301 | -95.3367 | L16 | 1553 BENNETTE AVE | Vented | 2 |  | Street | Paved - Asphalt | At Grade | [11 empty] | 3000 | [11 empty] | 3000 | Repair
127 | 5 | D | SSMHT0009720 | SS.MH.T0009720 | 32.3175 | -95.3528 | K18 | 3837 PUTTING LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
128 | 5 | D | SSMHT0009729 | SS.MH.T0009729 | 32.322 | -95.3607 | J17 | 4463 COUPLES CT | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 14 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
129 | 5 | D | SSMHT0009737 | SS.MH.T0009737 | 32.3133 | -95.3532 | K18 | 3958 SCENIC DR | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 7.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
130 | 5 | D | SSMHT0009995 | SS.MH.T0009995 | 32.3201 | -95.3249 | L17 | 2721 MONROE ST | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 2 | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
131 | 5 | D | SSMHT0009996 | SS.MH.T0009996 | 32.3185 | -95.3258 | L17 | 2214 DAVIS AVE | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
132 | 5 | D | SSMHT0009997 | SS.MH.T0009997 | 32.3184 | -95.3271 | L17 | 2300 BLK HALL ST | Vented | 2 | No | Gutter | Paved - Concrete | Above Grade | 1 | CO 6" | Other | 5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
133 | 5 | D | SSMHT0009999 | SS.MH.T0009999 | 32.3463 | -95.3461 | K15 | 406 MORGAN AVE | Vented | 2 | No | Road Shoulder | Paved - Concrete | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
134 | 5 | D | SSMHT0010000 | SS.MH.T0010000 | 32.3457 | -95.3512 | K15 | NONE OLD CHANDLER RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
135 | 5 | D | SSMHT0010002 | SS.MH.T0010002 | 32.3143 | -95.3329 | L18 | 3117 SEATON ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.52 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
136 | 5 | D | SSMHT0010004 | SS.MH.T0010004 | 32.3418 | -95.3436 | K15 | 703 WHITESIDE RD | Vented | 2 | No | Street | Paved - Asphalt | Above Grade | 1 | CO 6" | Other |  |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
137 | 5 | D | SSMHT0010005 | SS.MH.T0010005 | 32.3437 | -95.3436 | K15 | 603 WHITESIDE RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
138 | 5 | D | SSMHT0010090 | SS.MH.T0010090 | 32.3198 | -95.3346 | L17 | 2736 TOL AVE | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 9.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
139 | 5 | D | SSMHT0010099 | SS.MH.T0010099 | 32.3152 | -95.331 | L18 | 3000 BLK BUDDIE ST | Vented | 2 | No | Gutter | Paved - Concrete | At Grade |  | CO 6" | Other | 3.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
140 | 5 | D | SSMHT0010100 | SS.MH.T0010100 | 32.3144 | -95.3298 | L18 | 2706 LUTHER ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 2.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
141 | 5 | D | SSMHT0010101 | SS.MH.T0010101 | 32.3143 | -95.3305 | L18 | 2708 SARA ST | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 7.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
142 | 5 | D | SSMHT0010268 | SS.MH.T0010268 | 32.3151 | -95.3399 | K18 | 3211 TOWN WAY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
143 | 5 | D | SSMHT0010380 | SS.MH.T0010380 | 32.3134 | -95.354 | K18 | 3438 PINE TERRACE DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
144 | 5 | D | SSMHT0010404 | SS.MH.T0010404 | 32.3201 | -95.3598 | J17 | 4418 CASCADES BLVD | None |  | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
145 | 5 | D | SSMHT0010423 | SS.MH.T0010423 | 32.3137 | -95.3384 | L18 | 3208 PARK CENTER DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
146 | 5 | D | SSMHT0010518 | SS.MH.T0010518 | 32.3215 | -95.3543 | K17 | 4306 CASCADES BLVD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 8.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
147 | 5 | D | SSMHT0010519 | SS.MH.T0010519 | 32.3218 | -95.3562 | K17 | 4350 CASCADES BLVD | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
148 | 5 | D | SSMHT0010903 | SS.MH.T0010903 | 32.3386 | -95.3372 | L16 | 1019 BOYD AVE | Solid |  | No | Street | Unpaved | Above Grade | 21 | Std 48 Round | Concrete | 4.74 | 65.8144 | [7 empty] | 650 | [10 empty] | 650 | Repair
149 | 5 | D | SSMHT0011874 | SS.MH.T0011874 | 32.3461 | -95.338 | L15 | 3450 CHANDLER HWY | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Other | 5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
150 | 5 | D | SSMHT0012271 | SS.MH.T0012271 | 32.3359 | -95.3286 | L16 | 2510 HABITAT CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
151 | 5 | D | SSMHT0012405 | SS.MH.T0012405 | 32.3183 | -95.3358 | L17 | 3106 MOOREHEAD ST | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
152 | 5 | D | SSMHT0012410 | SS.MH.T0012410 | 32.3422 | -95.3497 | K15 | 4420 ST HWY 31 W. | None |  | No | Yard | Paved - Concrete | Above Grade | 4 | CO 8" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
153 | 5 | D | SSMHT0012411 | SS.MH.T0012411 | 32.3365 | -95.3318 | L16 | 2850 W. SHAW ST | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | 42 | Brick | 4.64 | 64.5584 | 2 | [6 empty] | 650 |  |  |  | 1936.752 | [6 empty] | 2586.752 | Rehabilitate
154 | 5 | D | SSMHT0013060 | SS.MH.T0013060 | 32.3421 | -95.3508 | K15 | 4420 ST HWY 31 W. | Solid |  | No | Yard | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 6.93 | 93.3208 | [7 empty] | 650 | [10 empty] | 650 | Repair
155 | 5 | D | SSMHT0013061 | SS.MH.T0013061 | 32.342 | -95.3518 | K15 | 4550 ST HWY 31 W. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 11.66 | 152.7296 | 2 | [11 empty] | 4581.888 | [5 empty] | 4581.888 | Rehabilitate
156 | 5 | D | SSMHT0014475 | SS.MH.T0014475 | 32.3219 | -95.3422 | K17 | 2609 S. SW LP 323 | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 9.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
157 | 5 | D | SSMHT0015540 | SS.MH.T0015540 | 32.3221 | -95.3304 | L17 | NONE DEPRIEST AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 20 | Std 48 Round | Concrete | 12.9 | 168.304 | 2 | [11 empty] | 5049.12 | [5 empty] | 5049.12 | Rehabilitate
158 | 5 | D | SSMHT0015548 | SS.MH.T0015548 | 32.3164 | -95.3398 | L18 | 3211 TOWNE WAY DR | Solid |  | No | Parking Lot | Unpaved | Above Grade | 5 | CO 4" | Other | 3.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
159 | 5 | D | SSMHT0015590 | SS.MH.T0015590 | 32.3468 | -95.3451 | K15 | 1419 OLD CHANDLER RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.22 | 84.4032 | 2 | [11 empty] | 2532.096 | [5 empty] | 2532.096 | Rehabilitate
160 | 5 | D | SSMHT0015604 | SS.MH.T0015604 | 32.3112 | -95.3405 | K18 | 3210 S. SW LP 323 | Solid |  | No | Drainage Ditch | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 9.46 | 125.0976 | 2 | [11 empty] | 3752.928 | [5 empty] | 3752.928 | Rehabilitate
161 | 5 | D | SSMHT0015608 | SS.MH.T0015608 | 32.3123 | -95.3362 | L18 | 3110 (16) TOWNE PARK DR | Vented | 2 | No | Parking Lot | Paved - Asphalt | At Grade |  | CO 6" | Other | 12 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
162 | 13 | D | SSMHT0000783 | SS.MH.T0000783 | 32.3463 | -95.2917 | N15 | 903 E. FRONT ST. | Vented | 4 | No | Creek | Unpaved | Above Grade | 5 | 36 | Brick | 3.56 | 50.9936 | 2 |  | 1000 | [8 empty] | 1529.808 |  |  | 280 |  |  |  | 2809.808 | Rehabilitate
163 | 14 | D | SSMHT0004659 | SS.MH.T0004659 | 32.3419 | -95.2769 | O15 | 800 BLK. S. PORTER ST. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | 32 | Brick | 3.78 | 53.7568 | 2 | [10 empty] | 1612.704 | [6 empty] | 1612.704 | Rehabilitate
164 | 17 | D | SSMHT0014669 | SS.MH.T0014669 | 32.2893 | -95.3223 | L20 | 1600 RICE RD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 2 | Std 48 Round | Concrete | 3.89 | 55.1384 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair
165 | 18 | D | SSMHT0005213 | SS.MH.T0005213 | 32.2948 | -95.301 | N20 | 200 BLK SHILOH RD. | Vented | 2 | Yes | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Brick | 11.1 | 145.696 | 2 | [11 empty] | 4370.88 | [5 empty] | 4370.88 | Rehabilitate
166 | 18 | D | SSMHT0009296 | SS.MH.T0009296 | 32.2869 | -95.3008 | N20 | 5610 S BROADWAY AVE | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.24 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
167 | 18 | D | SSMHT0009311 | SS.MH.T0009311 | 32.2869 | -95.2855 | N20 | 1129 GARDEN PARK CIR. | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 3 | CO 6" | Other | 9.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
168 | 18 | D | SSMHT0009543 | SS.MH.T0009543 | 32.308 | -95.272 | N20 | 5400 CARMEL CT | Solid |  |  | Yard | Unpaved | Below Grade | 2 | CO 6" | Other | 1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
169 | 18 | D | SSMHT0015549 | SS.MH.T0015549 | 32.3054 | -95.2793 | O19 | 1826 SYBIL LN | Solid |  | No | Yard | Unpaved | Above Grade | 1 | Std 48 Round | Concrete | 12.64 | 165.0384 | 2 | [6 empty] | 650 |  |  |  |  | 4951.152 |  | 280 |  |  |  | 5881.152 | Rehabilitate
170 | 20 | D | SSMHT0000536 | SS.MH.T0000536 | 32.237 | -95.2977 | N25 | 9245 QUIET WATER | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.3 | 135.648 | [10 empty] | 725 | [7 empty] | 725 | Repair
171 | 20 | D | SSMHT0000591 | SS.MH.T0000591 | 32.259 | -95.316 | M23 | 2401 W CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 7.76 | 103.7456 | [7 empty] | 650 | [10 empty] | 650 | Repair
172 | 20 | D | SSMHT0001354 | SS.MH.T0001354 | 32.2441 | -95.2948 | N24 | NONE COVENTRY RD | Solid |  | No | Creek | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 6.64 | 89.6784 | [7 empty] | 650 | [10 empty] | 650 | Repair
173 | 20 | D | SSMHT0001427 | SS.MH.T0001427 | 32.2448 | -95.2915 | N24 | 1242 COLT LN | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 20 | Std 48 Round | Concrete | 16.24 | 210.2544 | 2 | [6 empty] | 650 |  |  |  |  | 6307.632 | [5 empty] | 6957.632 | Rehabilitate
174 | 20 | D | SSMHT0002452 | SS.MH.T0002452 | 32.2591 | -95.3102 | M23 | 8310 CROOKED TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 21.57 | 277.1992 | 2 | [11 empty] | 8315.976 | [5 empty] | 8315.976 | Rehabilitate
175 | 20 | D | SSMHT0002454 | SS.MH.T0002454 | 32.2591 | -95.3096 | M23 | 8225 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 13.54 | 176.3424 | 2 | [11 empty] | 5290.272 | [5 empty] | 5290.272 | Rehabilitate
176 | 20 | D | SSMHT0002456 | SS.MH.T0002456 | 32.2585 | -95.3097 | M23 | 8205 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 19.4 | 249.944 | 2 | [6 empty] | 650 |  | 1000 |  |  | 7498.32 |  | 280 |  |  |  | 9428.32 | Rehabilitate
177 | 20 | D | SSMHT0002460 | SS.MH.T0002460 | 32.2572 | -95.3094 | M23 | 8389 S BROADWAY AVE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 10.83 | 142.3048 | [7 empty] | 650 | [10 empty] | 650 | Repair
178 | 20 | D | SSMHT0002463 | SS.MH.T0002463 | 32.2591 | -95.3118 | M23 | 8402 LAKEWAY DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 21 | Std 48 Round | Concrete | 13.67 | 177.9752 | 2 | [6 empty] | 650 |  |  |  |  | 5339.256 | [5 empty] | 5989.256 | Rehabilitate
179 | 20 | D | SSMHT0002467 | SS.MH.T0002467 | 32.2591 | -95.3132 | M23 | 8402 LAKEWAY DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 7.9 | 105.504 | 2 | [6 empty] | 650 |  |  |  |  | 3165.12 | [5 empty] | 3815.12 | Rehabilitate
180 | 20 | D | SSMHT0005502 | SS.MH.T0005502 | 32.2699 | -95.2994 | N22 | 600 OXFORD DR | Vented | 2 | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Brick | 6.7 | 90.432 | 2 | [11 empty] | 2712.96 | [5 empty] | 2712.96 | Rehabilitate
181 | 20 | D | SSMHT0005504 | SS.MH.T0005504 | 32.2687 | -95.2999 | N22 | 8237 CLEMSON DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 6.4 | 86.664 | 2 | [11 empty] | 2599.92 | [5 empty] | 2599.92 | Rehabilitate
182 | 20 | D | SSMHT0005516 | SS.MH.T0005516 | 32.268 | -95.2998 | N22 | 513 HARVARD DR. | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 11.56 | 151.4736 | 2 | [11 empty] | 4544.208 | [5 empty] | 4544.208 | Rehabilitate
183 | 20 | D | SSMHT0005519 | SS.MH.T0005519 | 32.2669 | -95.3011 | N22 | 520 PRINCETON DR | Solid |  | No | Creek | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.44 | 74.6064 |  |  |  |  | 500 |  |  | 650 | [10 empty] | 1150 | Repair
184 | 20 | D | SSMHT0005607 | SS.MH.T0005607 | 32.2677 | -95.2951 | N22 | 1917 CAMBRIDGE RD. | Solid |  | No | Road Shoulder | Paved - Asphalt | Above Grade | 5 | Std 48 Round | Concrete | 10.36 | 136.4016 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
185 | 20 | D | SSMHT0006270 | SS.MH.T0006270 | 32.2691 | -95.2961 | N22 | 720 MCCLENNY DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.82 | 154.7392 | [15 empty] | 900 |  |  | 900 | Repair
186 | 20 | D | SSMHT0007045 | SS.MH.T0007045 | 32.2694 | -95.2634 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 16.96 | 219.2976 | 2 | [6 empty] | 650 |  |  |  |  | 6578.928 |  | 280 |  |  |  | 7508.928 | Rehabilitate
187 | 20 | D | SSMHT0007054 | SS.MH.T0007054 | 32.2708 | -95.2667 | O22 | 6033 MORNING MIST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 12.03 | 157.3768 | 2 | [11 empty] | 4721.304 | [5 empty] | 4721.304 | Rehabilitate
188 | 20 | D | SSMHT0007055 | SS.MH.T0007055 | 32.2704 | -95.2668 | O22 | 6041 MORNING MIST DR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.04 | 144.9424 | 2 | [11 empty] | 4348.272 | [5 empty] | 4348.272 | Rehabilitate
189 | 20 | D | SSMHT0007372 | SS.MH.T0007372 | 32.2586 | -95.3077 | M23 | 8288 S BROADWAY AVE | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 9.44 | 124.8464 | [7 empty] | 650 |  |  | 725 |  |  |  |  | 900 |  |  | 2275 | Repair
190 | 20 | D | SSMHT0007380 | SS.MH.T0007380 | 32.2623 | -95.3015 | N23 | 8450 SOUTHLAND DR | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 13.3 | 173.328 | 2 | [11 empty] | 5199.84 | [5 empty] | 5199.84 | Rehabilitate
191 | 20 | D | SSMHT0007390 | SS.MH.T0007390 | 32.262 | -95.2955 | N23 | 8429 CASTLETON WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 8.34 | 111.0304 | 2 | [6 empty] | 650 |  |  |  |  | 3330.912 | [5 empty] | 3980.912 | Rehabilitate
192 | 20 | D | SSMHT0007403 | SS.MH.T0007403 | 32.26 | -95.295 | N23 | 816 WILDER WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 8.38 | 111.5328 | 2 | [6 empty] | 650 |  |  |  |  | 3345.984 | [5 empty] | 3995.984 | Rehabilitate
193 | 20 | D | SSMHT0007431 | SS.MH.T0007431 | 32.259 | -95.2986 | N23 | 683 WILDER WAY | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.1 | 108.016 | 2 | [11 empty] | 3240.48 | [5 empty] | 3240.48 | Rehabilitate
194 | 20 | D | SSMHT0007434 | SS.MH.T0007434 | 32.2597 | -95.3076 | M23 | 7934 S BROADWAY AVE | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.4 | 124.344 | 2 | [6 empty] | 650 |  |  |  |  | 3730.32 | [5 empty] | 4380.32 | Rehabilitate
195 | 20 | D | SSMHT0007436 | SS.MH.T0007436 | 32.2595 | -95.2973 | N23 | 8643 RADCLIFFE DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 9.34 | 123.5904 | 2 | [11 empty] | 3707.712 | [5 empty] | 3707.712 | Rehabilitate
196 | 20 | D | SSMHT0007621 | SS.MH.T0007621 | 32.2543 | -95.2911 | N23 | 1111 CUMBERLNAD RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 7.24 | 97.2144 | [7 empty] | 650 | [10 empty] | 650 | Repair
197 | 20 | D | SSMHT0007684 | SS.MH.T0007684 | 32.2535 | -95.2929 | N23 | 9116 CHEROKEE TRL | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 6.94 | 93.4464 | 2 | [6 empty] | 650 |  |  |  |  | 2803.392 | [5 empty] | 3453.392 | Rehabilitate
198 | 20 | D | SSMHT0007713 | SS.MH.T0007713 | 32.2405 | -95.2984 | N24 | 602 WINDING BROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.91 | 118.1896 | 2 | [11 empty] | 3545.688 | [5 empty] | 3545.688 | Rehabilitate
199 | 20 | D | SSMHT0007717 | SS.MH.T0007717 | 32.2407 | -95.2982 | N24 | 605 WINDING BROOK LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.08 | 120.3248 | 2 | [11 empty] | 3609.744 | [5 empty] | 3609.744 | Rehabilitate
200 | 20 | D | SSMHT0007736 | SS.MH.T0007736 | 32.2546 | -95.2897 | N23 | 1223 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.22 | 84.4032 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
201 | 20 | D | SSMHT0008056 | SS.MH.T0008056 | 32.2782 | -95.2838 | N21 | 1502 E GRANDE BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 9.07 | 120.1992 | 2 | [11 empty] | 3605.976 | [5 empty] | 3605.976 | Rehabilitate
202 | 20 | D | SSMHT0008071 | SS.MH.T0008071 | 32.2767 | -95.2827 | N21 | 1525 E GRANDE BLVD | Solid |  | No | Parking Lot | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 9.56 | 126.3536 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
203 | 20 | D | SSMHT0008072 | SS.MH.T0008072 | 32.2771 | -95.2873 | N21 | 1343 E GRANDE BLVD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 13.36 | 174.0816 | 2 | [11 empty] | 5222.448 |  | 280 |  |  |  | 5502.448 | Rehabilitate
204 | 20 | D | SSMHT0008210 | SS.MH.T0008210 | 32.2731 | -95.2879 | N22 | 1306 JEB STUART DR | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Other | 6.17 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
205 | 20 | D | SSMHT0008211 | SS.MH.T0008211 | 32.2738 | -95.2728 | O21 | 2211 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.92 | 130.8752 | [15 empty] | 900 |  |  | 900 | Repair
206 | 20 | D | SSMHT0008218 | SS.MH.T0008218 | 32.2738 | -95.2699 | O21 | 2448 ROY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 14.38 | 186.8928 | [15 empty] | 900 |  |  | 900 | Repair
207 | 20 | D | SSMHT0008353 | SS.MH.T0008353 | 32.2723 | -95.2787 | O22 | 6928 PALUXY DR | Solid |  | No | Creek | Unpaved | Above Grade | 38 | Std 48 Round | Concrete | 8.9 | 118.064 | 2 | [6 empty] | 650 |  |  |  |  | 3541.92 | [5 empty] | 4191.92 | Rehabilitate
208 | 20 | D | SSMHT0008384 | SS.MH.T0008384 | 32.2629 | -95.2957 | N22 | 8425 CASTLETON WAY. | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Concrete | 10.7 | 140.672 | 2 | [11 empty] | 4220.16 | [5 empty] | 4220.16 | Rehabilitate
209 | 20 | D | SSMHT0008463 | SS.MH.T0008463 | 32.2533 | -95.2858 | N23 | NONE OLD HICKORY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 8.2 | 109.272 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair
210 | 20 | D | SSMHT0008732 | SS.MH.T0008732 | 32.25 | -95.2885 | N24 | 9218 CHISHOLM TRL | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 14.44 | 187.6464 | [10 empty] | 725 | [7 empty] | 725 | Repair
211 | 20 | D | SSMHT0008743 | SS.MH.T0008743 | 32.2469 | -95.2861 | N24 | 1504 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.4 | 149.464 | [8 empty] | 1950 |  | 725 |  |  |  |  | 900 |  |  | 3575 | Repair
212 | 20 | D | SSMHT0008760 | SS.MH.T0008760 | 32.251 | -95.2806 | O24 | 9094 STONE CREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 7.02 | 94.4512 | 2 | [11 empty] | 2833.536 | [5 empty] | 2833.536 | Rehabilitate
213 | 20 | D | SSMHT0008761 | SS.MH.T0008761 | 32.251 | -95.2804 | O24 | 9094 STONE CREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 7.1 | 95.456 | [7 empty] | 650 | [10 empty] | 650 | Repair
214 | 20 | D | SSMHT0008762 | SS.MH.T0008762 | 32.2507 | -95.2794 | O24 | 9141 PALUXY DR | Solid |  | No | Field | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 6.4 | 86.664 | [10 empty] | 725 |  |  | 700 |  |  |  |  | 1425 | Repair
215 | 20 | D | SSMHT0008764 | SS.MH.T0008764 | 32.25 | -95.2804 | O24 | 1628 WILLOW BEND | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 6.9 | 92.944 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
216 | 20 | D | SSMHT0008782 | SS.MH.T0008782 | 32.2535 | -95.2857 | N23 | 1502 CUMBERLAND RD | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 11 | Std 48 Round | Concrete | 6.88 | 92.6928 | [7 empty] | 650 |  | 1000 | 725 |  |  |  | 280 |  |  |  | 2655 | Repair
217 | 20 | D | SSMHT0008796 | SS.MH.T0008796 | 32.2587 | -95.2892 | N23 | NONE WILDER TRL | Solid |  | No | Yard | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 9.91 | 130.7496 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
218 | 20 | D | SSMHT0008928 | SS.MH.T0008928 | 32.2586 | -95.3054 | M23 | 100 CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 7.36 | 98.7216 | 2 | [11 empty] | 2961.648 | [5 empty] | 2961.648 | Rehabilitate
219 | 20 | D | SSMHT0009535 | SS.MH.T0009535 | 32.2728 | -95.2902 | N22 | 1009 JEFFERY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.94 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
220 | 20 | D | SSMHT0009536 | SS.MH.T0009536 | 32.2735 | -95.2903 | N21 | 1017 DAVID DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
221 | 20 | D | SSMHT0009537 | SS.MH.T0009537 | 32.2765 | -95.2905 | N21 | 1009 ELAINE DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
222 | 20 | D | SSMHT0009687 | SS.MH.T0009687 | 32.2458 | -95.2918 | N24 | 1227 RAINMAKER | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
223 | 20 | D | SSMHT0009740 | SS.MH.T0009740 | 32.2467 | -95.292 | N24 | 1234 DREAMCATCHER | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.21 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
224 | 20 | D | SSMHT0009742 | SS.MH.T0009742 | 32.2637 | -95.299 | N22 | 615 POTOMAC DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.28 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
225 | 20 | D | SSMHT0009748 | SS.MH.T0009748 | 32.271 | -95.2651 | O22 | 2744 GUINN FARMS RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
226 | 20 | D | SSMHT0009750 | SS.MH.T0009750 | 32.2728 | -95.2661 | O21 | 7252 MORNING MIST DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.24 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
227 | 20 | D | SSMHT0009760 | SS.MH.T0009760 | 32.2401 | -95.2984 | N25 | 525 WINDING BROOK LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.94 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
228 | 20 | D | SSMHT0009761 | SS.MH.T0009761 | 32.2402 | -95.2997 | N25 | 533 SKIPPING STONE LN | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.76 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
229 | 20 | D | SSMHT0009764 | SS.MH.T0009764 | 32.2538 | -95.2871 | N23 | 1401 CUMBERLAND RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 6.2 | 84.152 | [14 empty] | 280 |  |  |  | 280 | Repair
230 | 20 | D | SSMHT0009805 | SS.MH.T0009805 | 32.2753 | -95.2798 | O21 | 1821 ANGY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.46 | [15 empty] | 280 |  |  |  | 280 | Repair
231 | 20 | D | SSMHT0009806 | SS.MH.T0009806 | 32.2744 | -95.2797 | O21 | 1820 CIRCLE DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.16 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
232 | 20 | D | SSMHT0009812 | SS.MH.T0009812 | 32.2662 | -95.2919 | N22 | 930 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.68 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
233 | 20 | D | SSMHT0009814 | SS.MH.T0009814 | 32.2649 | -95.2928 | N22 | 6363 OBERLIN CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.02 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
234 | 20 | D | SSMHT0009815 | SS.MH.T0009815 | 32.2661 | -95.2939 | N22 | 836 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
235 | 20 | D | SSMHT0009816 | SS.MH.T0009816 | 32.2621 | -95.2947 | N23 | 6510 ROCHESTER WAY | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
236 | 20 | D | SSMHT0009818 | SS.MH.T0009818 | 32.2641 | -95.2932 | N22 | 6547 WHEATON CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.66 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
237 | 20 | D | SSMHT0009819 | SS.MH.T0009819 | 32.2628 | -95.2931 | N22 | 8523 CASTLETON WAY. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.28 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
238 | 20 | D | SSMHT0009835 | SS.MH.T0009835 | 32.2459 | -95.2845 | N24 | 1535 LUANN LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
239 | 20 | D | SSMHT0009843 | SS.MH.T0009843 | 32.2548 | -95.2902 | N23 | 1111 CUMBERLAND RD | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other | 16.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
240 | 20 | D | SSMHT0009873 | SS.MH.T0009873 | 32.2384 | -95.2977 | N25 | 9873 STONEBANK CROSSING | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.98 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
241 | 20 | D | SSMHT0009973 | SS.MH.T0009973 | 32.2583 | -95.3177 | M23 | 704 W CUMBERLAND RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
242 | 20 | D | SSMHT0010336 | SS.MH.T0010336 | 32.2566 | -95.3151 | M23 | 8436 LAKEWAY DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
243 | 20 | D | SSMHT0010354 | SS.MH.T0010354 | 32.258 | -95.3104 | M23 | 8411 CROOKED TRL | Vented | 2 |  | Driveway | Paved - Concrete | At Grade |  | CO 6" | Other | 5.25 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
244 | 20 | D | SSMHT0010357 | SS.MH.T0010357 | 32.2568 | -95.3094 | M23 | 8389 S BROADWAY AVE | Vented | 2 |  | Trees/Woods | Unpaved | Above Grade | 1 | CO 6" | Other | 5.76 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
245 | 20 | D | SSMHT0010364 | SS.MH.T0010364 | 32.2736 | -95.2681 | O21 | 5847 GRACE AVE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.22 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
246 | 20 | D | SSMHT0010370 | SS.MH.T0010370 | 32.2703 | -95.2677 | O22 | 2559 MEADOWLAND CT | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.79 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
247 | 20 | D | SSMHT0010377 | SS.MH.T0010377 | 32.2755 | -95.2697 | O21 | 2448 ROY RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.72 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
248 | 20 | D | SSMHT0010394 | SS.MH.T0010394 | 32.2567 | -95.3046 | M23 | 501 CUMBERLAND RD | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | CO 6" | Other | 20.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
249 | 20 | D | SSMHT0010395 | SS.MH.T0010395 | 32.2582 | -95.2923 | N23 | 1127 WILDER WAY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
250 | 20 | D | SSMHT0010399 | SS.MH.T0010399 | 32.2618 | -95.2998 | N23 | 8524 RADCLIFFE DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other | 7.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
251 | 20 | D | SSMHT0010442 | SS.MH.T0010442 | 32.2662 | -95.2952 | N22 | 819 MARQUETTE LANE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
252 | 20 | D | SSMHT0010443 | SS.MH.T0010443 | 32.2661 | -95.2964 | N22 | 803 MARQUETTE LANE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.98 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
253 | 20 | D | SSMHT0010444 | SS.MH.T0010444 | 32.2644 | -95.2952 | N22 | 820 NEWBURY CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.46 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
254 | 20 | D | SSMHT0010445 | SS.MH.T0010445 | 32.2609 | -95.2946 | N23 | 6527 ROCHESTER WAY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.34 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
255 | 20 | D | SSMHT0010446 | SS.MH.T0010446 | 32.2641 | -95.2921 | N22 | 6522 EMORY CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.18 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
256 | 20 | D | SSMHT0010456 | SS.MH.T0010456 | 32.2764 | -95.2613 | P21 | 6525 RHONES QUARTER RD | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 2.86 | 42.2016 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
257 | 20 | D | SSMHT0010464 | SS.MH.T0010464 | 32.2711 | -95.297 | N22 | 707 JEFF DAVIS DR | Vented |  | No | Road Shoulder | Unpaved | Below Grade | 4 | CO 6" | Other | 13.82 |  |  | 140 |  |  |  | 1250 | [12 empty] | 1390 | Replace/Install Cleanout
258 | 20 | D | SSMHT0010467 | SS.MH.T0010467 | 32.273 | -95.2819 | O22 | 1616 JEB STUART DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade |  | CO 6" | Other | 7.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
259 | 20 | D | SSMHT0010468 | SS.MH.T0010468 | 32.2727 | -95.2817 | O22 | 1630 JEB STUART DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 5 | CO 6" | Other | 11.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
260 | 20 | D | SSMHT0010471 | SS.MH.T0010471 | 32.2738 | -95.2736 | O21 | 2211 ROY RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Other | 7.92 | [15 empty] | 280 |  |  |  | 280 | Repair
261 | 20 | D | SSMHT0010476 | SS.MH.T0010476 | 32.2642 | -95.2909 | N22 | 1197 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
262 | 20 | D | SSMHT0010477 | SS.MH.T0010477 | 32.2627 | -95.2903 | N22 | 6596 FURMAN CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.82 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
263 | 20 | D | SSMHT0010478 | SS.MH.T0010478 | 32.2645 | -95.2908 | N22 | 1190 CAMBRIDGE BEND. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 16.96 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
264 | 20 | D | SSMHT0010479 | SS.MH.T0010479 | 32.2649 | -95.2917 | N22 | 6368 MANCHESTER CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
265 | 20 | D | SSMHT0010486 | SS.MH.T0010486 | 32.25 | -95.281 | O24 | 9102 STONE CREEK TRL | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.7 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
266 | 20 | D | SSMHT0010488 | SS.MH.T0010488 | 32.2488 | -95.2813 | O24 | 1625 WILLOW BEND | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.74 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
267 | 20 | D | SSMHT0010503 | SS.MH.T0010503 | 32.2469 | -95.2901 | N24 | 1221 LUANN LN | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 13.36 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
268 | 20 | D | SSMHT0010515 | SS.MH.T0010515 | 32.2477 | -95.3035 | M24 | 8966 S BROADWAY AVE | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 6.84 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
269 | 20 | D | SSMHT0010516 | SS.MH.T0010516 | 32.2576 | -95.3053 | M23 | NONE WILDER WAY | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | CO 6" | Other | 6.03 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
270 | 20 | D | SSMHT0013349 | SS.MH.T0013349 | 32.2397 | -95.2966 | N25 | 9210 STONEBANK CROSSING | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 8.96 | 118.8176 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair
271 | 20 | D | SSMHT0013489 | SS.MH.T0013489 | 32.2518 | -95.2841 | N23 | 9010 OLD HICKORY RD | Solid |  | No | Creek | Unpaved | Below Grade | 1 | Std 48 Round | Concrete | 5.3 | 72.848 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 | 900 |  |  | 2555 | Repair
272 | 20 | D | SSMHT0013779 | SS.MH.T0013779 | 32.2367 | -95.2997 | N25 | 9374 STONEBANK CROSSING | Solid |  | Yes | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 9.84 | 129.8704 | [10 empty] | 725 |  |  |  |  | 900 |  |  | 1625 | Repair
273 | 20 | D | SSMHT0013805 | SS.MH.T0013805 | 32.2704 | -95.2974 | N22 | 739 CAMBRIDGE BEND CIR | Vented | 2 | No | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 5.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
274 | 20 | D | SSMHT0013806 | SS.MH.T0013806 | 32.2708 | -95.2987 | N22 | 627 CAMBRIDGE BEND CIR | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
275 | 20 | D | SSMHT0013807 | SS.MH.T0013807 | 32.2712 | -95.2981 | N22 | 617 CAMBRIDGE BEND CIR | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other | 2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
276 | 20 | D | SSMHT0014469 | SS.MH.T0014469 | 32.2471 | -95.2813 | O24 | 1653 LEGACY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.73 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
277 | 20 | D | SSMHT0014470 | SS.MH.T0014470 | 32.2471 | -95.2815 | O24 | 1649 LEGACY DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.24 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
278 | 20 | D | SSMHT0014482 | SS.MH.T0014482 | 32.2568 | -95.3199 | M23 | 620 W CUMBERLAND RD | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 60 Round | Concrete | 16.06 | 207.9936 | 2 | [11 empty] | 6239.808 | [5 empty] | 6239.808 | Rehabilitate
279 | 20 | D | SSMHT0014586 | SS.MH.T0014586 | 32.2687 | -95.2632 | O22 | 14600 COUNTY RD 2191 | Solid |  | Yes | Yard | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 19.24 | 247.9344 | 2 | [11 empty] | 7438.032 | [5 empty] | 7438.032 | Rehabilitate
280 | 20 | D | SSMHT0014589 | SS.MH.T0014589 | 32.2688 | -95.2682 | O22 | NONE BARBEE RD | Solid |  | No | Field | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 9.94 | 131.1264 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
281 | 20 | D | SSMHT0014596 | SS.MH.T0014596 | 32.2773 | -95.2902 | N21 | 3203 E GRANDE BLVD | Vented | 2 |  | Street | Paved - Concrete | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
282 | 20 | D | SSMHT0014617 | SS.MH.T0014617 | 32.2786 | -95.2705 | O21 | NONE GRANDE BLVD | Solid |  | No | Sidewalk | Paved - Concrete | At Grade |  | Std 48 Round | Concrete | 16.1 | 208.496 | [10 empty] | 725 | [7 empty] | 725 | Repair
283 | 20 | D | SSMHT0015235 | SS.MH.T0015235 | 32.2441 | -95.2914 | N24 | NONE COVENTRY PKWY | Solid |  | No | Yard | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 13.51 | 175.9656 | [7 empty] | 650 | [10 empty] | 650 | Repair
284 | 20 | D | SSMHT0015489 | SS.MH.T0015489 | 32.2621 | -95.3172 | M23 | 7920 CROOKED TRL | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 18 | Std 48 Round | Concrete | 9.86 | 130.1216 |  |  |  |  | 500 |  |  | 650 | [10 empty] | 1150 | Repair
285 | 20 | D | SSMHT0015508 | SS.MH.T0015508 | 32.2588 | -95.3175 | M23 | 1502 W CUMBERLAND RD | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
286 | 20 | D | SSMHT0015525 | SS.MH.T0015525 | 32.2573 | -95.317 | M23 | 413 CUMBERLAND DR | Solid |  | Yes | Road Shoulder | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 8.24 | 109.7744 | [7 empty] | 650 | [10 empty] | 650 | Repair
287 | 20 | D | SSMHT0015528 | SS.MH.T0015528 | 32.2618 | -95.2955 | N23 | 8429 CASTLETON WAY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 8.3 | 110.528 | 2 | [6 empty] | 650 |  |  |  |  | 3315.84 |  | 280 |  |  |  | 4245.84 | Rehabilitate
288 | 20 | D | SSMHT0015626 | SS.MH.T0015626 | 32.2538 | -95.2923 | N23 | 9116 CHEROKEE TRL | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 7.44 | 99.7264 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 | 900 |  |  | 2555 | Repair
289 | 21 | D | SSMHT0000275 | SS.MH.T0000275 | 32.3076 | -95.2509 | P18 | 3627 RIVER OAKS CT. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 20.14 | 259.2384 | 2 | [11 empty] | 7777.152 | [5 empty] | 7777.152 | Rehabilitate
290 | 21 | D | SSMHT0005563 | SS.MH.T0005563 | 32.3034 | -95.2493 | P19 | 3388 BRIDGEWOOD TRAIL | Vented | 2 | No | Trees/Woods | Unpaved | Below Grade | 7 | Std 48 Round | Brick | 5.94 | 80.8864 | 2 | [6 empty] | 650 |  | 1000 |  | 2426.592 |  |  | 280 |  |  |  | 4356.592 | Rehabilitate
291 | 21 | D | SSMHT0006051 | SS.MH.T0006051 | 32.3064 | -95.2664 | NA | 2500 CALLOWAY RD | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 6.94 | 93.4464 | [7 empty] | 650 | [10 empty] | 650 | Repair
292 | 21 | D | SSMHT0006055 | SS.MH.T0006055 | 32.3064 | -95.2648 | O18 | 2605 CALLOWAY RD | Solid |  | No | Yard | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 10.44 | 137.4064 | 2 | [6 empty] | 650 |  |  |  |  | 4122.192 | [5 empty] | 4772.192 | Rehabilitate
293 | 21 | D | SSMHT0006066 | SS.MH.T0006066 | 32.299 | -95.2613 | P19 | 5050 TROUP HWY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 12.11 | 158.3816 | 2 | [6 empty] | 650 |  |  |  |  | 4751.448 | [5 empty] | 5401.448 | Rehabilitate
294 | 21 | D | SSMHT0006075 | SS.MH.T0006075 | 32.2985 | -95.2542 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 25 | Std 48 Round | Concrete | 17.65 | 227.964 | 2 | [6 empty] | 650 |  |  |  |  | 6838.92 | [5 empty] | 7488.92 | Rehabilitate
295 | 21 | D | SSMHT0006076 | SS.MH.T0006076 | 32.2983 | -95.2545 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.08 | 132.8848 | 2 | [6 empty] | 650 |  |  |  |  | 3986.544 | [5 empty] | 4636.544 | Rehabilitate
296 | 21 | D | SSMHT0006078 | SS.MH.T0006078 | 32.2976 | -95.2532 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 12.75 | 166.42 | 2 | [6 empty] | 650 |  |  |  |  | 4992.6 | [5 empty] | 5642.6 | Rehabilitate
297 | 21 | E | SSMHT0006079 | SS.MH.T0006079 | 32.2971 | -95.2524 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 31 | Std 48 Round | Concrete | 11.06 | 145.1936 | [16 empty] | 7012 |  | 7012 | Replace
298 | 21 | D | SSMHT0006158 | SS.MH.T0006158 | 32.3012 | -95.2674 | O19 | 4610 TROUP HWY | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 2 | Std 48 Round | Concrete | 6.68 | 90.1808 | 2 | [6 empty] | 650 |  |  |  |  | 2705.424 | [5 empty] | 3355.424 | Rehabilitate
299 | 21 | D | SSMHT0006315 | SS.MH.T0006315 | 32.3053 | -95.2589 | P19 | 3839 LAZY CREEK DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 6 | Std 48 Round | Concrete | 8.07 | 107.6392 | 2 | [8 empty] | 1000 |  |  | 3229.176 |  | 280 |  |  |  | 4509.176 | Rehabilitate
300 | 21 | D | SSMHT0006797 | SS.MH.T0006797 | 32.318 | -95.257 | P17 | 3333 VARSITY DR | Bolted | 4 BOLTS | No | Yard | Unpaved | Above Grade | 17 | Std 48 Round | Concrete | 7.35 | 98.596 | [7 empty] | 650 | [10 empty] | 650 | Repair
301 | 21 | D | SSMHT0006859 | SS.MH.T0006859 | 32.299 | -95.2536 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 15.62 | 202.4672 | 2 | [11 empty] | 6074.016 | [5 empty] | 6074.016 | Rehabilitate
302 | 21 | D | SSMHT0006860 | SS.MH.T0006860 | 32.2994 | -95.2533 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 9.58 | 126.6048 | 2 | [6 empty] | 650 |  |  |  |  | 3798.144 | [5 empty] | 4448.144 | Rehabilitate
303 | 21 | D | SSMHT0006862 | SS.MH.T0006862 | 32.3027 | -95.2465 | P19 | 3885 BRIGHTEN CREEK CIR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 7 | Std 48 Round | Concrete | 8.6 | 114.296 | [7 empty] | 650 | [10 empty] | 650 | Repair
304 | 21 | D | SSMHT0006876 | SS.MH.T0006876 | 32.3028 | -95.2426 | Q19 | 3831 BRIGHTON CREEK CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 8.69 | 115.4264 | [10 empty] | 725 | [7 empty] | 725 | Repair
305 | 21 | D | SSMHT0006910 | SS.MH.T0006910 | 32.3004 | -95.2516 | P19 | 4211 LAZYCREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 9.6 | 126.856 | 2 | [6 empty] | 650 |  |  |  |  | 3805.68 | [5 empty] | 4455.68 | Rehabilitate
306 | 21 | D | SSMHT0006914 | SS.MH.T0006914 | 32.3012 | -95.2492 | P19 | 4128 PINECREEK DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 11 | Std 48 Round | Concrete | 13.57 | 176.7192 | 2 | [11 empty] | 5301.576 | [5 empty] | 5301.576 | Rehabilitate
307 | 21 | D | SSMHT0006925 | SS.MH.T0006925 | 32.2992 | -95.255 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 13 | Std 48 Round | Concrete | 15.64 | 202.7184 | 2 | [6 empty] | 650 |  |  |  |  | 6081.552 | [5 empty] | 6731.552 | Rehabilitate
308 | 21 | D | SSMHT0006927 | SS.MH.T0006927 | 32.2996 | -95.2563 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 11.51 | 150.8456 | 2 | [11 empty] | 4525.368 | [5 empty] | 4525.368 | Rehabilitate
309 | 21 | D | SSMHT0006928 | SS.MH.T0006928 | 32.2996 | -95.2567 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 36 | Std 48 Round | Concrete | 13.62 | 177.3472 | 2 | [6 empty] | 650 |  |  |  |  | 5320.416 | [5 empty] | 5970.416 | Rehabilitate
310 | 21 | D | SSMHT0006929 | SS.MH.T0006929 | 32.2997 | -95.2572 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 27 | Std 48 Round | Concrete | 13.91 | 180.9896 | 2 | [11 empty] | 5429.688 | [5 empty] | 5429.688 | Rehabilitate
311 | 21 | D | SSMHT0007008 | SS.MH.T0007008 | 32.3049 | -95.2433 | P19 | 3802 BRIGHTON CREEK CIR | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 11.42 | 149.7152 | [7 empty] | 650 | [10 empty] | 650 | Repair
312 | 21 | D | SSMHT0007677 | SS.MH.T0007677 | 32.3181 | -95.2435 | Q17 | 4016 HANOVER PL | Solid |  | No | Yard | Unpaved | Above Grade | 22 | Std 48 Round | Concrete | 10.18 | 134.1408 | [7 empty] | 650 | [10 empty] | 650 | Repair
313 | 21 | D | SSMHT0007893 | SS.MH.T0007893 | 32.3114 | -95.2421 | Q18 | 3402 PICKENS DR. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.16 | 133.8896 | [10 empty] | 725 | [7 empty] | 725 | Repair
314 | 21 | D | SSMHT0008606 | SS.MH.T0008606 | 32.3011 | -95.2397 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 8.38 | 111.5328 | [7 empty] | 650 | [10 empty] | 650 | Repair
315 | 21 | D | SSMHT0008618 | SS.MH.T0008618 | 32.3036 | -95.2409 | NA | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 22 | Std 48 Round | Concrete | 14.8 | 192.168 | 2 | [11 empty] | 5765.04 | [5 empty] | 5765.04 | Rehabilitate
316 | 21 | D | SSMHT0008637 | SS.MH.T0008637 | 32.3063 | -95.2356 | Q18 | 3521 CLARION LANE | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 7.88 | 105.2528 | [10 empty] | 725 | [7 empty] | 725 | Repair
317 | 21 | D | SSMHT0008651 | SS.MH.T0008651 | 32.3051 | -95.2385 | Q19 | 4001 STONEBROOK LN | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 8 | Std 48 Round | Concrete | 9.84 | 129.8704 | [7 empty] | 650 |  |  | 725 | [7 empty] | 1375 | Repair
318 | 21 | D | SSMHT0008653 | SS.MH.T0008653 | 32.3043 | -95.2396 | Q19 | 3963 CHAPEL WOODS BLVD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 10 | Std 48 Round | Concrete | 19.24 | 247.9344 | 2 | [6 empty] | 650 |  |  |  |  | 7438.032 | [5 empty] | 8088.032 | Rehabilitate
319 | 21 | D | SSMHT0008670 | SS.MH.T0008670 | 32.2985 | -95.2478 | P19 | 3417 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 10.64 | 139.9184 | [10 empty] | 725 | [7 empty] | 725 | Repair
320 | 21 | D | SSMHT0008671 | SS.MH.T0008671 | 32.2988 | -95.2477 | P19 | 3410 RIDGE BLUFF CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 11.33 | 148.5848 | [10 empty] | 725 | [7 empty] | 725 | Repair
321 | 21 | D | SSMHT0009306 | SS.MH.T0009306 | 32.3087 | -95.2534 | P18 | 3312 SHADY COVE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
322 | 21 | D | SSMHT0009325 | SS.MH.T0009325 | 32.3049 | -95.2586 | P19 | 3903 LAZY CREEK DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 14 | CO 6" | Other | 6.64 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
323 | 21 | D | SSMHT0009326 | SS.MH.T0009326 | 32.3051 | -95.2585 | P19 | 3902 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 11.24 | 147.4544 |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
324 | 21 | D | SSMHT0009327 | SS.MH.T0009327 | 32.305 | -95.2582 | P19 | 3904 LAZYCREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.33 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
325 | 21 | D | SSMHT0009328 | SS.MH.T0009328 | 32.3055 | -95.2573 | P19 | 3109 LAKEPINE CIR. | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 5.4 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
326 | 21 | D | SSMHT0009366 | SS.MH.T0009366 | 32.3003 | -95.2666 | O19 | 2701 WILLARD DR | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 10.88 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
327 | 21 | D | SSMHT0009423 | SS.MH.T0009423 | 32.3182 | -95.2599 | P17 | 2902 SHERNANDOAH DR | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
328 | 21 | D | SSMHT0009424 | SS.MH.T0009424 | 32.3163 | -95.2622 | O18 | 2901 ROCKBRIDGE RD. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.2 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
329 | 21 | D | SSMHT0009457 | SS.MH.T0009457 | 32.3078 | -95.2448 | P18 | 3819 BROADMOORE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
330 | 21 | D | SSMHT0009519 | SS.MH.T0009519 | 32.3087 | -95.2579 | P18 | 3101 LAKE FOREST DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Concrete | 10.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
331 | 21 | D | SSMHT0009523 | SS.MH.T0009523 | 32.2958 | -95.2508 | P19 | 3708 SHILOH RD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.03 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
332 | 21 | D | SSMHT0009524 | SS.MH.T0009524 | 32.2954 | -95.2498 | P19 | 3734 SHILOH RD | Vented | 2 | No | Driveway | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.94 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
333 | 21 | D | SSMHT0009539 | SS.MH.T0009539 | 32.3056 | -95.2575 | P19 | 3107 LAKEPINE CIR | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.8 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
334 | 21 | D | SSMHT0009546 | SS.MH.T0009546 | 32.3011 | -95.252 | P19 | 3303 CRIPPLE CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.92 | [15 empty] | 280 |  |  |  | 280 | Repair
335 | 21 | D | SSMHT0009606 | SS.MH.T0009606 | 32.3083 | -95.2564 | P18 | 3702 LAKE VISTA CIR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.42 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
336 | 21 | D | SSMHT0009641 | SS.MH.T0009641 | 32.321 | -95.2531 | P17 | 3428 LEXINGTON DR | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 1 | CO 6" | Other | 4.54 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
337 | 21 | D | SSMHT0009646 | SS.MH.T0009646 | 32.3192 | -95.2581 | P17 | 3101 CAMPUS CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.01 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
338 | 21 | D | SSMHT0009709 | SS.MH.T0009709 | 32.3098 | -95.2445 | P18 | 3709 3709 WINDING WAY. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
339 | 21 | D | SSMHT0009711 | SS.MH.T0009711 | 32.3063 | -95.2433 | P18 | 3788 WOODS BLVD. | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | Other | 11.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
340 | 21 | D | SSMHT0009715 | SS.MH.T0009715 | 32.3016 | -95.2425 | Q19 | 3838 BRIGHTON CREEK CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 12.41 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
341 | 21 | D | SSMHT0009820 | SS.MH.T0009820 | 32.3062 | -95.2527 | P18 | 3505 RICHMOND | Solid |  |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.58 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
342 | 21 | D | SSMHT0009821 | SS.MH.T0009821 | 32.3062 | -95.2521 | P18 | 3513 LALEMONT | Vented |  |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.65 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
343 | 21 | D | SSMHT0009822 | SS.MH.T0009822 | 32.3061 | -95.2516 | P18 | 3519 LAKEMONT | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.42 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
344 | 21 | D | SSMHT0009823 | SS.MH.T0009823 | 32.3071 | -95.2388 | Q18 | 3934 CHAPEL QUARTERS. | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.18 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
345 | 21 | D | SSMHT0009825 | SS.MH.T0009825 | 32.3062 | -95.2366 | Q18 | 4014 CHAPEL RIDGE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 0 | 6.28 |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
346 | 21 | D | SSMHT0009826 | SS.MH.T0009826 | 32.3048 | -95.2371 | O18 | 3992 OLD OMEN RD | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 1 | CO 6" | Concrete | 12.56 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
347 | 21 | D | SSMHT0009827 | SS.MH.T0009827 | 32.3001 | -95.2368 | Q19 | 4310 STONEBROOK LN | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
348 | 21 | D | SSMHT0009828 | SS.MH.T0009828 | 32.2986 | -95.2504 | P19 | 4222 LAZY CREEK DR | Vented |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.01 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
349 | 21 | D | SSMHT0009829 | SS.MH.T0009829 | 32.2992 | -95.2502 | M20 | 3308 RIDGE BLUFF CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.76 | [15 empty] | 280 |  |  |  | 280 | Repair
350 | 21 | D | SSMHT0009830 | SS.MH.T0009830 | 32.2982 | -95.2501 | P19 | 4230 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.36 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
351 | 21 | D | SSMHT0009832 | SS.MH.T0009832 | 32.3006 | -95.2372 | Q19 | 4232 STONEBROOK LN | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 8.48 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
352 | 21 | D | SSMHT0009853 | SS.MH.T0009853 | 32.3176 | -95.2475 | P17 | 3921 HANOVER PL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 5.3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
353 | 21 | D | SSMHT0009876 | SS.MH.T0009876 | 32.3015 | -95.2529 | P19 | 4117 BIG OAK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.62 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
354 | 21 | D | SSMHT0009877 | SS.MH.T0009877 | 32.3011 | -95.2525 | P19 | 4119 LAZY CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.12 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
355 | 21 | D | SSMHT0009878 | SS.MH.T0009878 | 32.3004 | -95.2531 | P19 | 3200 CRIPPLE CREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.05 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
356 | 21 | D | SSMHT0009880 | SS.MH.T0009880 | 32.3029 | -95.2509 | P19 | 4113 PINECREEK DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 1.77 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
357 | 21 | D | SSMHT0010064 | SS.MH.T0010064 | 32.3081 | -95.2449 | P18 | 3815 BROADMOORE CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.1 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
358 | 21 | D | SSMHT0010065 | SS.MH.T0010065 | 32.3103 | -95.2534 | P18 | 3313 OAK KNOLL DR. | Vented | 2 | No | Road Shoulder | Unpaved | Above Grade | 2 | CO 6" | Other | 0 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
359 | 21 | D | SSMHT0010069 | SS.MH.T0010069 | 32.3093 | -95.2527 | P18 | 3604 ROCK CREEK DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.7 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
360 | 21 | D | SSMHT0010070 | SS.MH.T0010070 | 32.3092 | -95.2548 | P18 | 3601 OAK KNOLL DR. | Vented | 2 | No | Street | Paved - Asphalt | Above Grade |  | CO 6" | Other | 8.66 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
361 | 21 | D | SSMHT0010125 | SS.MH.T0010125 | 32.3083 | -95.2459 | P18 | 3814 LONG LEAF DR. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 0 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
362 | 21 | D | SSMHT0010130 | SS.MH.T0010130 | 32.3032 | -95.2512 | P19 | 4112 PINECREEK DR | Vented | IRON | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3.69 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
363 | 21 | D | SSMHT0010137 | SS.MH.T0010137 | 32.3074 | -95.25 | P18 | 3636 RIVER OAKS CT. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 0 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
364 | 21 | D | SSMHT0010140 | SS.MH.T0010140 | 32.3083 | -95.2675 | NA | 3900 OLD TROUP HWY | Vented | 2 | No | Street | Paved - Asphalt | Below Grade | 1 | CO 6" | IRON | 6.5 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
365 | 21 | D | SSMHT0010157 | SS.MH.T0010157 | 32.2993 | -95.2642 | O19 | 4764 OLD TROUP HWY | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 11.65 | [15 empty] | 280 |  |  |  | 280 | Repair
366 | 21 | D | SSMHT0010158 | SS.MH.T0010158 | 32.298 | -95.263 | O19 | 4714 PONDEROSA TRAIL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 7.01 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
367 | 21 | D | SSMHT0010159 | SS.MH.T0010159 | 32.298 | -95.263 | O19 | 4720 PONDEROSA TRAIL | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 6.63 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
368 | 21 | D | SSMHT0010279 | SS.MH.T0010279 | 32.3202 | -95.252 | P17 | 3516 OMEGA DR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.21 | [15 empty] | 280 |  |  |  | 280 | Repair
369 | 21 | D | SSMHT0010325 | SS.MH.T0010325 | 32.3031 | -95.239 | Q19 | 4101 STONEBROOK LN | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other |  |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
370 | 21 | D | SSMHT0010326 | SS.MH.T0010326 | 32.3024 | -95.2424 | Q19 | 3831 BRIGHTON CREEK CIR | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 3 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
371 | 21 | D | SSMHT0010327 | SS.MH.T0010327 | 32.302 | -95.2362 | Q19 | 4002 CHAPEL CT | Solid |  | No | Street | Paved - Asphalt | At Grade |  | CO 6" | IRON | 9.28 |  |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
372 | 21 | D | SSMHT0010328 | SS.MH.T0010328 | 32.3013 | -95.2356 | Q19 | 4017 CHAPEL WOODS BLVD | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 7.78 | 103.9968 |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
373 | 21 | D | SSMHT0010329 | SS.MH.T0010329 | 32.3008 | -95.2364 | Q19 | 4001 CHAPEL WOODS BLVD | Other | 0 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Concrete | 6.6 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
374 | 21 | D | SSMHT0010376 | SS.MH.T0010376 | 32.3061 | -95.2365 | Q18 | 4020 CHAPEL RIDGE. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Other | 0 | 6.28 |  | 140 |  |  |  |  | 3000 | [11 empty] | 3140 | Replace/Install Cleanout
375 | 21 | D | SSMHT0013919 | SS.MH.T0013919 | 32.2966 | -95.2482 | P19 | 4320 LAZY CREEK DR | Vented | 2 |  | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 9.44 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
376 | 21 | D | SSMHT0014500 | SS.MH.T0014500 | X-CNL | X-CNL | P18 | 255' DS of 14500 & 266' US of 06048 | X-CNL |  |  | Yard | Unpaved | Below Grade | [22 empty] | 2600 | 2600 | Repair
377 | 21 | D | SSMHT0014693 | SS.MH.T0014693 | 32.2998 | -95.2574 | P19 | 3706 SHILOH RD | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 15 | Std 48 Round | Concrete | 15.4 | 199.704 | 2 | [11 empty] | 5991.12 | [5 empty] | 5991.12 | Rehabilitate
378 | 21 | D | SSMHT0014730 | SS.MH.T0014730 | 32.311 | -95.2514 | P18 | 3807 UNIVERSITY BLVD. | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Concrete | 5.16 | 71.0896 | 2 | [6 empty] | 650 |  |  |  | 2132.688 | [6 empty] | 2782.688 | Rehabilitate
379 | 21 | D | SSMHT0015223 | SS.MH.T0015223 | 32.3045 | -95.2392 | P19 | NONE OLD OMEN RD | Solid |  | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Concrete | 10.99 | 144.3144 | 2 | [6 empty] | 650 |  |  |  |  | 4329.432 | [5 empty] | 4979.432 | Rehabilitate
380 | 21 | D | SSMHT0015234 | SS.MH.T0015234 | 32.3017 | -95.2648 | O19 | 4580 OLD TROUP HWY | Solid |  | No | Yard | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 3.12 | 45.4672 | [7 empty] | 650 | [10 empty] | 650 | Repair
381 | 7 | D | SSMHT0014387 | SS.MH.T0014387 | X-CNL | X-CNL | K14 | 257' DS of 02017 | X-CNL |  |  | Field | [24 empty] | 2600 | 2600 | Repair
382 | 8 | D | SSMHT0015647 | SS.MH.T0015647 | X-CNL | X-CNL | K14 | 11' DS of 01084 & 107' US of 13042 | X-CNL |  |  | Trees/Woods | [24 empty] | 2600 | 2600 | Repair
383 | 17 | D | SSMHT0014322 | SS.MH.T0014322 | X-CNL | X-CNL | M21 | 408' DS of 03676 & 99' US of 03674 | X-CNL |  |  | Road Shoulder | [24 empty] | 2600 | 2600 | Repair
384 | 17 | D | SSMHT0014368 | SS.MH.T0014368 | X-CNL | X-CNL | M20 | 138' DS of 14368 & 157' of 03514 | X-CNL |  |  | Yard | [24 empty] | 2600 | 2600 | Repair
385 | 17 | D | SSMHT0014397 | SS.MH.T0014397 | X-CNL | X-CNL | L18 | 158' DS of 14396 & 155' US of 14398 | X-CNL |  |  | Street | [24 empty] | 2600 | 2600 | Repair
386 | 17 | D | SSMHT0015243 | SS.MH.T0015243 | X-CNL | X-CNL | L20 | 13' DS of 15244 & 57' US 15243 | X-CNL |  |  | Parking Lot | [24 empty] | 2600 | 2600 | Repair
387 | 17 | D | SSMHT0015244 | SS.MH.T0015244 | X-CNL | X-CNL | L20 | 187' DS of 01546 & 13' 15243 | X-CNL |  |  | Parking Lot | [24 empty] | 2600 | 2600 | Repair
388 | 17 | D | SSMHT0015253 | SS.MH.T0015253 | X-CNL | X-CNL | M20 | 48' DS of 02439 & 149' US of 02440. | X-CNL |  |  | Yard | [24 empty] | 2600 | 2600 | Repair
389 | 17 | D | SSMHT0015300 | SS.MH.T0015300 | X-CNL | X-CNL | L20 | 301' DS of 00542 & 234' US of 00541 | X-CNL |  |  | Trees/Woods | [24 empty] | 2600 | 2600 | Repair
390 | 18 | D | SSMHT0014502 | SS.MH.T0014502 | X-CNL | X-CNL | N20 | 105' DS 05308 & 80' US of 05307 | X-CNL |  |  | Street | [24 empty] | 2600 | 2600 | Repair
391 | 18 | D | SSMHT0014505 | SS.MH.T0014505 | X-CNL | X-CNL | N20 | 255' DS of 05398 & 301 US of 00363 | X-CNL |  |  | Yard | [24 empty] | 2600 | 2600 | Repair
392 | 5 | D | SSMHT0001171 | SS.MH.T0001171 | 32.3319 | -95.3405 | K16 | 1530 SSW LOOP 323 | Solid |  | No | Road Shoulder | Unpaved | Above Grade | 10 | Std 48 Round | Brick | 4.64 | 64.5584 | 2 | [11 empty] | 1936.752 | [5 empty] | 1936.752 | Rehabilitate
393 | 5 | D | SSMHT0002144 | SS.MH.T0002144 | 32.3401 | -95.3303 | L16 | 823 CLARK ST | Solid |  | No | Street | Paved - Asphalt | Above Grade | 1 | Std 48 Round | Brick | 8.08 | 107.7648 | 2 | [11 empty] | 3232.944 |  | 280 |  |  |  | 3512.944 | Rehabilitate
394 | 6 | D | SSMHT0015677 | SS.MH.T0015677 | 32.3439 | -95.3553 | K15 | 4707 STATE HWY 31 W | Solid |  | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Concrete | 5.58 | 76.3648 | [7 empty] | 650 |  |  | 725 |  |  |  | 280 |  |  |  | 1655 | Repair
395 | 7 | D | SSMHT0001013 | SS.MH.T0001013 | 32.3564 | -95.349 | K14 | 104 JORDAN PLAZA BLVD | Solid |  | No | Yard | Unpaved | Below Grade | 12 | Std 48 Round | Concrete | 8.94 | 118.5664 | 2 | [8 empty] | 1000 |  |  | 3556.992 |  | 280 |  |  |  | 4836.992 | Rehabilitate
396 | 7 | D | SSMHT0001016 | SS.MH.T0001016 | 32.3558 | -95.3482 | K14 | 115 JORDAN PLAZA BLVD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 6.08 | 82.6448 | [9 empty] | 1000 | [8 empty] | 1000 | Repair
397 | 7 | D | SSMHT0001052 | SS.MH.T0001052 | 32.3726 | -95.3409 | K13 | 3330 COPE ST | Solid |  | Yes | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Brick | 7.32 | 98.2192 | 2 | [11 empty] | 2946.576 | [5 empty] | 2946.576 | Rehabilitate
398 | 7 | D | SSMHT0015269 | SS.MH.T0015269 | 32.3561 | -95.3484 | K14 | 115 JORDAN PLAZA BLVD | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 3 | Std 48 Round | Concrete | 5.8 | 79.128 |  |  |  |  | 500 |  |  |  |  | 1000 |  |  |  |  | 280 |  |  |  | 1780 | Repair
399 | 8 | D | SSMHT0002019 | SS.MH.T0002019 | 32.3585 | -95.3375 | L14 | 3205 W ERWIN ST | Solid |  | Yes | Yard | Unpaved | Above Grade | 2 | Std 48 Round | Brick | 10.84 | 142.4304 | 2 | [11 empty] | 4272.912 | [5 empty] | 4272.912 | Rehabilitate
400 | 8 | D | SSMHT0012920 | SS.MH.T0012920 | 32.3528 | -95.3192 | M14 | 202 GLENWOOD BLVD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 4.54 | 63.3024 | 2 | [10 empty] | 1899.072 |  |  | 280 |  |  |  | 2179.072 | Rehabilitate
401 | 13 | D | SSMHT0005855 | SS.MH.T0005855 | 32.3424 | -95.2855 | N15 | 643 BAXTER | Vented | 1 | No | Street | Paved - Concrete | At Grade |  | Std 48 Round | Brick | 5.04 | 69.5824 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
402 | 13 | D | SSMHT0005952 | SS.MH.T0005952 | 32.3466 | -95.2743 | O18 | 2117 E FRONT ST | Solid |  | Yes | Street | Paved - Asphalt | Below Grade | 1 | Std 48 Round | Brick | 12.73 | 166.1688 | 2 | [11 empty] | 4985.064 |  | 280 |  |  |  | 5265.064 | Rehabilitate
403 | 13 | D | SSMHT0014136 | SS.MH.T0014136 | 32.3628 | -95.2928 | N13 | 1224 N WINONA AVE | Solid |  | No | Trees/Woods | Unpaved | Below Grade | 10 | Std 48 Round | Brick | 9.65 | 127.484 | 2 | [11 empty] | 3824.52 |  | 280 |  |  |  | 4104.52 | Rehabilitate
404 | 13 | D | SSMHT0015685 | SS.MH.T0015685 | 32.3393 | -95.2974 | N16 | 400BLK FRAZIER ST | Solid |  | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.68 | 77.6208 | 2 | [10 empty] | 2328.624 | [6 empty] | 2328.624 | Rehabilitate
405 | 13 | D | SSMHT0015686 | SS.MH.T0015686 | 32.3392 | -95.2974 | N16 | 400 BLK FRAZIER ST | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 6.1 | 82.896 | 2 | [11 empty] | 2486.88 |  | 280 |  |  |  | 2766.88 | Rehabilitate
406 | 13 | D | SSMHT0015689 | SS.MH.T0015689 | 32.36 | -95.2957 | N14 | 1002 N. NORMANDY AVE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 5.3 | 72.848 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
407 | 13 | D | SSMHT0015696 | SS.MH.T0015696 | 32.3444 | -95.2881 | N15 | 512 S. FLEISHEL AVE. | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 4.37 | 61.1672 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
408 | 13 | D | SSMHT0015837 | SS.MH.T0015837 | 32.3378 | -95.2971 | N16 | 409 E. DODGE ST. | Vented | 2 | No | Yard | Unpaved | At Grade |  | CO 6" | Other | 1.9 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
409 | 13 | D | SSMHT0015838 | SS.MH.T0015838 | 32.3383 | -95.2972 | N16 | 403 E. DODGE ST. | Vented | 2 | No | Street | Paved - Asphalt | At Grade |  | CO 6" | Other | 4.1 |  |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
410 | 13 | D | SSMHT0015839 | SS.MH.T0015839 | 32.3564 | -95.3141 | M14 | 516 N. ROSS AVE. | Solid |  | No | Street | Paved - Asphalt | Above Grade | 2 | Std 48 Round | Concrete | 4.6 | 64.056 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
411 | 14 | D | SSMHT0006577 | SS.MH.T0006577 | 32.3186 | -95.2638 | O17 | 2729 WILLIAMSBURG DR | Solid |  | No | Creek | Unpaved | Above Grade | 9 | Std 48 Round | Concrete | 7 | 94.2 | 2 |  | 1000 | [9 empty] | 2826 |  | 280 |  |  |  | 4106 | Rehabilitate
412 | 16 | D | SSMHT0001620 | SS.MH.T0001620 | 32.2691 | -95.3309 | L22 | 2010 PINEHURST ST | Solid |  | No | Yard | Unpaved | At Grade |  | Std 48 Round | Concrete | 9 | 119.32 | 2 | [11 empty] | 3579.6 | [5 empty] | 3579.6 | Rehabilitate
413 | 16 | D | SSMHT0014318 | SS.MH.T0014318 | 32.2696 | -95.3358 | L22 | 2311 MIRABEAU DR | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 5 | Std 48 Round | Concrete | 11.3 | 148.208 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
414 | 16 | D | SSMHT0014320 | SS.MH.T0014320 | 32.269 | -95.3345 | L22 | 6938 PARK SLOPE | Solid |  | No | Trees/Woods | Unpaved | Above Grade | 3 | Std 48 Round | Concrete | 9.54 | 126.1024 | [7 empty] | 650 | [6 empty] | 280 |  |  |  | 930 | Repair
415 | 17 | D | SSMHT0002397 | SS.MH.T0002397 | 32.3146 | -95.3225 | L18 | 1743 ALAMO CROSSING RD | Vented | 2 | No | Trees/Woods | Unpaved | Above Grade | 12 | Std 48 Round | Brick | 7.98 | 106.5088 | 2 | [11 empty] | 3195.264 |  | 280 |  |  |  | 3475.264 | Rehabilitate
416 | 17 | D | SSMHT0003386 | SS.MH.T0003386 | 32.2998 | -95.3192 | M19 | 1500 WSW LOOP 323 | Solid |  | No | Creek | Unpaved | Below Grade | 23 | Std 48 Round | Concrete | 6.14 | 83.3984 | 2 |  |  |  | 500 |  |  |  |  | 1000 |  |  | 2501.952 |  | 280 |  |  |  | 4281.952 | Rehabilitate
417 | 17 | D | SSMHT0014362 | SS.MH.T0014362 | 32.3084 | -95.3197 | M18 | 1537 WOODLAND HILLS DR | Vented | 2 | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Brick | 5.2 | 71.592 | 2 | [6 empty] | 650 |  |  |  | 2147.76 |  |  | 280 |  |  |  | 3077.76 | Rehabilitate
418 | 17 | D | SSMHT0014367 | SS.MH.T0014367 | 32.2941 | -95.3131 | M20 | 5109 KATIE DR | Solid |  | No | Yard | Unpaved | Above Grade | 6 | Std 48 Round | Concrete | 8.1 | 108.016 | [7 empty] | 650 | [10 empty] | 650 | Repair
419 | 17 | D | SSMHT0015251 | SS.MH.T0015251 | 32.3033 | -95.3201 | L19 | 3000 WSW LOOP 323 | Solid |  | Yes | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 6.34 | 85.9104 | 2 | [11 empty] | 2577.312 |  | 280 |  |  |  | 2857.312 | Rehabilitate
420 | 17 | D | SSMHT0015275 | SS.MH.T0015275 | 32.3026 | -95.3243 | L19 | 4334 DC DR | Solid |  | No | Road Shoulder | Unpaved | Below Grade | 1 | Std 48 Round | Brick | 9.86 | 130.1216 | 2 | [11 empty] | 3903.648 |  | 280 |  |  |  | 4183.648 | Rehabilitate
421 | 18 | D | SSMHT0006192 | SS.MH.T0006192 | 32.2922 | -95.2442 | P20 | 5401 KENT DR | Solid |  | No | Trees/Woods | Unpaved | At Grade |  | Std 48 Round | Brick | 4.62 | 64.3072 | 2 | [6 empty] | 650 |  |  |  | 1929.216 |  |  | 280 |  |  |  | 2859.216 | Rehabilitate
422 | 18 | D | SSMHT0006377 | SS.MH.T0006377 | 32.3159 | -95.2813 | N18 | 1700 DENNIS DR | Vented | 2 | Yes | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Brick | 8.41 | 111.9096 | 2 | [11 empty] | 3357.288 | [5 empty] | 3357.288 | Rehabilitate
423 | 18 | D | SSMHT0009955 | SS.MH.T0009955 | 32.308 | -95.272 | O19 | 3830 TROUP HWY | Vented | 2 | No | Road Shoulder | Unpaved | Below Grade | 2 | CO 8" | Other | 9.11 | 120.7016 |  | 140 | [16 empty] | 140 | Replace/Install Cleanout
424 | 18 | D | SSMHT0013013 | SS.MH.T0013013 | 32.3147 | -95.2743 | O18 | 3110 GOLDEN RD | Solid |  | No | Street | Paved - Asphalt | At Grade |  | Std 48 Round | Concrete | 16.1 | 208.496 | [10 empty] | 725 |  |  |  | 280 |  |  |  | 1005 | Repair
425 | 18 | D | SSMHT0013192 | SS.MH.T0013192 | 32.3077 | -95.2813 | O18 | 1600 BLK E SOUTH EAST LOOP 323 | Bolted |  | No | Drainage Ditch | Paved - Concrete | Below Grade | 2 | Std 48 Round | Concrete | 5.84 | 79.6304 | see note 1 |  |  | 2800 | [7 empty] | 2388.912 | [6 empty] | 5188.912 | Rehabilitate
426 | 18 | D | SSMHT0015197 | SS.MH.T0015197 | 32.2952 | -95.2748 | O19 | 2101 SHILOH RD | Solid |  | No | Gutter | Paved - Concrete | Below Grade | 1 | Std 48 Round | Concrete | 11.64 | 152.4784 | [14 empty] | 280 |  |  |  | 280 | Repair
427 | 20 | D | SSMHT0015673 | SS.MH.T0015673 | 32.2669 | -95.2801 | O22 | 8331 PALUXY DR | Bolted |  | No | Yard | Unpaved | Above Grade | 4 | Std 48 Round | Concrete | 8.5 | 113.04 | 2 | [6 empty] | 650 |  |  |  |  | 3391.2 |  | 280 |  |  |  | 4321.2 | Rehabilitate
428 | 21 | D | SSMHT0015736 | SS.MH.T0015736 | 32.3125 | -95.2509 | P18 | 3905 UNIVERSITY BLVD | Vented | 2 | No | Road Shoulder | Unpaved | At Grade |  | Std 48 Round | Brick | 4.3 | 60.288 | [14 empty] | 280 |  |  |  | 280 | Repair
[21 empty] | 22960 | 2000 | 2800 | 4000 | 6250 | 72000 | 62400 | 9750 | 9000 | 31900 | 36881.184 | 555395.664 | 1400 | 22120 | 16200 | 7012 | 33800 | 895868.848
[21 empty] | 164 | 2 | 1 | 8 | 5 | 24 | 96 | 5 | 9 | 44 | 18 | 136 | 2 | 79 | 18 | 1 | 13
[34 empty] | 89 vf | 1406 vf | Contingency 15% |  | 134380.3272
[34 empty] | 1229 sq.ft. | 18513 sq.ft. | Total |  | 1030249.1752
[24 empty] | Rehabilitation Methods: | [6 empty] | Quantity | Unit Price | Total |  | Condition Code | Occurrences | Total
[24 empty] | Rehab 1001: Raise Manhole to Grade $1000 ea. | [6 empty] | 9 | 1000 | 9000 |  | A | 191 | 0
[24 empty] | Rehab.1010: Install Inflow Protector Insert $280 ea. | [6 empty] | 79 | 280 | 22120 |  | B | 986 | 0
[24 empty] | Rehab 1012: Install/Replace Missing or Defective Mainline Cleanout Cap or T-cone stopper $140 ea. | [6 empty] | 164 | 140 | 22960 |  | C | 543 | 0
|  |  | Condition Code | Occurrences | Total | [18 empty] | Rehab 1015: Mechanical Seal Chimney $1500 ea. | [6 empty] | 0 | 1500 | 0 |  | D | 427 | 888856.848
|  |  | A | 191 | 0 | [18 empty] | Rehab 1020: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Unpaved $650 ea. | [6 empty] | 96 | 650 | 62400 |  | E | 1 | 7012
|  |  | B | 986 | 0 | [18 empty] | Rehab 1021: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Paved $1950 ea. | [6 empty] | 5 | 1950 | 9750 |  | X | 229 | 0
|  |  | C | 543 | 0 | [18 empty] | Rehab 1022: Replace Manhole Ring & Cover (Rebuild Chimney as required) - Unpaved $1000 ea. | [6 empty] | 2 | 1000 | 2000 |  | Total | 2377 | 895868.848
|  |  | D | 426 | 888857 | [18 empty] | Rehab 1024: Replace Manhole Lid $500 ea. | [6 empty] | 8 | 500 | 4000 |  | Design and Contingency -15% |  | 134380.3272
|  |  | E | 1 | 7012 | [18 empty] | Rehab 1023WT: Watertight Bolt Down Ring and Cover - $2800 (See Note 1) | [6 empty] | 1 | 2800 | 2800 |  | Total Estimated Cost |  | 1030249.1752
|  |  | X | 230 | 0 | [18 empty] | Rehab 1026: Replace Cleanout Casting and Cover (Unpaved) $1250 ea. | [6 empty] | 5 | 1250 | 6250
|  |  | Total | 2377 | 895869 | [18 empty] | Rehab 1028: Replace Cleanout Casting and Cover (Paved) $3000 ea. | [6 empty] | 24 | 3000 | 72000
|  |  | Design and Contingency -15% |  | 134380.35 | [18 empty] | Rehab 1040: Clean Manhole, Remove any Roots, Repair as Needed and Coat , including bench (sq.ft.) | [6 empty] | 1229 | 30 | 36881
|  |  | Total Estimated Cost |  | 1030249.35 | [18 empty] | Rehab 1041: Clean Manhole, Remove any Roots, Repair as Needed and Coat , including bench (sq.ft.) | [6 empty] | 18513 | 30 | 555396
[24 empty] | Rehab 1047: Seal Manhole Pipe Connection $900 ea. | [6 empty] | 18 | 900 | 16200
[24 empty] | Rehab 1110: Reconstruct 4 ft. diameter Manhole Bench & Invert $700 ea. | [6 empty] | 2 | 700 | 1400
[24 empty] | Rehab 1205: Repair Chimney and Seal with Elastomeric $725 ea. | [6 empty] | 44 | 725 | 31900
[24 empty] | Rehab 1505: Replace Manhole (>6 feet deep) Unpaved $6000+$200/vf > 6 feet | [6 empty] | 1 | 7012 | 7012
[24 empty] | Rehab 1600: Rehab 1600: Locate and Raise Manhole to Grade $2600 ea. | [6 empty] | 13 | 2600 | 33800
[30 empty] | Sub-total |  |  | 895869
[30 empty] | Design and Contingency -15% |  |  | 134380.35
[30 empty] | Total Estimated Cost |  |  | 1030249.35
Preliminary Repair Methods:
Rehabilitation Methods:
Rehab 1001: Raise Manhole to Grade $1000 ea.
Rehab 1002: Raise Manhole to Grade - Paved $1850
Rehab 1003: Locate and Raise Cleanout to Pavement Grade and Install T-Cone Stopper $1500 ea.
Rehab 1004: Locate and Raise Cleanout to Grade and Install T-Cone Stopper $600 ea.
Rehab.1010: Install Inflow Protector Insert $280 ea.
Rehab 1012: Install/Replace Missing or Defective Mainline Cleanout Cap or T-cone stopper $140 ea.
Rehab 1015: Mechanical Seal Chimney $1500 ea.
Rehab 1020: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Unpaved $650 ea.
Rehab 1021: Realign and Seal Manhole Ring & Cover (Rebuild Chimney as required)-Paved $1950 ea.
Rehab 1022: Replace Manhole Ring & Cover (Rebuild Chimney as required) - Unpaved $1000 ea.
Rehab 1022WT: Same as 1022 except use Bolt Down Ring and Cover - $1500
Rehab 1023: Replace Manhole Ring & Cover (Rebuild Chimney as required) -Paved $1220 ea.
Rehab 1023WT: Same as 1023 except use Watertight Bolt Down Ring and Cover - $2800 (See Note 1)
Rehab 1024: Replace Manhole Lid $500 ea.
Rehab 1026: Replace Cleanout Casting and Cover (Unpaved) $1250 ea.
Rehab 1028: Replace Cleanout Casting and Cover (Paved) $3000 ea.
Rehab 1040/1041: Clean Manhole, Remove any Roots, Repair as Needed and Coat , including bench
Condition 1 - $21/sq.ft.
Condition 2 - $30/sq.ft.
Condition 3 - $40/sq.ft.
Rehab 1043: Repair/Plug Manhole Lift Holes $700 ea. Manhole (all holes)
Rehab 1047: Seal Manhole Pipe Connection $900 ea.
Rehab 1055: Remove Steps, Stop I/I and Repair as needed $700 ea.
Rehab 1110: Reconstruct 4 ft. diameter Manhole Bench & Invert $700 ea.
Rehab 1205: Repair Chimney and Seal with Elastomeric $725 ea.
Rehab 1215: Reconstruct Chimney/Cone $1000 ea.
Rehab 1502: Replace Manhole (< 6 feet deep) Paved $8400 ea.
Rehab 1503: Replace Manhole (>6 feet deep) Paved $8400+$250/vf>6 feet
Rehab 1504: Replace Manhole (< 6 feet deep) Unpaved $6000 ea.
Rehab 1505: Replace Manhole (>6 feet deep) Unpaved $6000+$200/vf > 6 feet
Rehab 1600: Locate and Raise Manhole to Grade $2600 ea.
Wall Condition 1
Condition Standard: An Existing structure that is considered structurally sound with no indications of settlement, cracking or other signs of fatigue. Infiltration or exfiltration through pre-cast joints, mortar joints, or around the pipe connections may exist and structure may be experiencing mild corrosion or deterioration.
Wall Condition 2
Condition Standard: An existing structure that is exhibiting early signs of structural fatigue evidenced by minor cracks, loss of mortar or brick, moderate to moderately severe corrosion (less ½ inch in depth), minor cross sectional distortion (less than 10 %); however, it is currently supporting the soil and live load.
Wall Condition 3
Condition Standard: An existing structure that is exhibiting severe structural fatigue and collapse is eminent. Conditions indicating this degree of deterioration may include very severe corrosion (loss of original profile of one inch or greater), cross sectional distortion beyond 10 percent, exposed reinforcing steel, loose or missing bricks, missing mortar, or large sections of the structure that are gone completely.
Note: Standard 48 inch diameter manhole used for estimating repair costs. Some brick manhole diameters are smaller and range from 24 inch to 48 inch diameter.
Condition Assessment Rating
A = Very Good
Minor defects are mostly cosmetic in nature and do not impact system hydraulics nor contribute to significant infiltration/inflow. No active infiltration.
B = Good
Manhole has no significant structural defects. Minor defects do not impact system hydraulics nor contribute to significant infiltration/inflow. No active infiltration. Minor defects may include slightly loose casting, minor corrosion of metal surfaces, minor deterioration of concrete mortar between bricks, minor cracks, etc. .
C = Fair
Manhole has no significant structural defects although minor defects were noted during inspection. System hydraulics are good and no significant infiltration/inflow sources noted. Light infiltration/inflow may be present. Nominal defects may include loose casting, nominal corrosion of metal surfaces, deterioration of concrete mortar between bricks or concrete walls, minor evidence of infiltration/inflow at precast joint sections, etc.
D = Poor
Manhole has moderate structural defects that may include cracks, loose bricks, separated casting, moderate root intrusion, broken cover and defects that may impact system hydraulics due to structural issues or contribute to significant infiltration/inflow. Some visible staining due to infiltration/inflow may be present. Active infiltration may have been observed. Moderate to severe defects may include loose casting, moderate to severe corrosion of metal surfaces, deterioration of concrete mortar between bricks, moderate to severe deterioration of precast wall sections and precast joint defects, etc. Manhole inspection was completed and the manhole will be addressed in the remediation plan.
E=Very Poor
Manhole may have severe structural defects that may include potential for structural failure, missing bricks, separated/broken casting, severe root intrusion, broken/missing cover and defects that may impact system hydraulics or contribute to significant infiltration/inflow. Visible staining due to infiltration/inflow ma y be present. Active infiltration may have been observed. Severe defects may include separated/broken casting/cover, severe corrosion of metal surfaces, missing mortar between bricks, etc. Manhole inspection was completed and the manhole will be addressed in the remediation plan or immediate repair may be warranted based on condition.
X= Incomplete Data
The asset may not exist, is a end of line segment, or could not be inspected due to being buried, no access, could not open, etc. CCTV results will be used to confirm if the asset exists. Buried and could not open manholes are being raised to grade and/or casting replaced to facilitate inspection. No other remedial measures at this time.
X-CNL (Could Not Locate- awaiting CCTV)
X-CNO (Could Not Open) - On Problem List
X-Buried - On Problem List
X-Access - On Problem List
*Note 1: Rehab 1023WT - Verify waterproof seal condition and and if good replace missing bolts or replace ring and cover with watertight ring and cover.

## Mainline Condition Summary
Group 5 - Mainline Condition Remedial Measures Summary
Basins 2, 7, 8, 10, 13, 16, 17, 18, 19, 20, 21 | [11 empty] | Annual Report
Item | Basin | Condition Rating | City Pipe Asset ID | Upstream Manhole | Downstream Manhole | Pipe Length (GIS) | Pipe Diameter (GIS) | Preliminary Rehabilitation Recommendation | Repair Cost | Recommended | Remediation Plan | Group
1 | 2 | D | SS.GM.T0005934 | SS.MH.T0002926 | SS.MH.T0013422 | 173.9318 | 8 | Point Repair at 92 ft and Grout Joint at 173 ft from 13422 | 5550 | 5550 | Point Repair & Grout Joint | Repair | Condition Code | Occurrances | Est. Cost
2 | 2 | C | SS.GM.T0005935 | SS.MH.T0002925 | SS.MH.T0002926 | 310.6831 | 6 | Grout Joint at 165 ft from 02925 | 800 | 0 | Monitor in CMOM | None | A | 102 | 0
3 | 2 | C | SS.GM.T0005946 | SS.MH.T0002934 | SS.MH.T0007504 | 429.0911 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None | B | 1266 | 0
4 | 2 | C | SS.GM.T0013558 | SS.MH.T0013422 | SS.MH.T0002928 | 283.8564 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None | C | 302 | 0
5 | 7 | B | SS.GM.T0005653 | SS.MH.T0001951 | SS.MH.T0001950 | 36.343 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None | D | 528 | 7123631.3062
6 | 7 | B | SS.GM.T0006459 | SS.MH.T0001119 | SS.MH.T0001117 | 229.1485 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None | E | 5 | 38273.7684
7 | 7 | C | SS.GM.T0006460 | SS.MH.T0010612 | SS.MH.T0001119 | 441.619 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None | Total | 2203 | 7161905.0746
8 | 7 | B | SS.GM.T0006534 | SS.MH.T0012452 | SS.MH.T0001077 | 410.3303 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
9 | 7 | B | SS.GM.T0006584 | SS.MH.T0001111 | SS.MH.T0001113 | 196.6025 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
10 | 7 | B | SS.GM.T0006588 | SS.MH.T0001115 | SS.MH.T0001116 | 196.6102 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
11 | 7 | D | SS.GM.T0006595 | SS.MH.T0001113 | SS.MH.T0001116 | 612.3488 | 8 | Access; Clean and Inspection | 2449.3953 | 0 | Addressed in Capacity Remendiations | Model
12 | 7 | B | SS.GM.T0006596 | SS.MH.T0001109 | SS.MH.T0001113 | 417.1496 | 8 | No Rehabilitation Recommended | 0 | 0 | Addressed in Capacity Remendiations | Model
13 | 7 | C | SS.GM.T0006597 | SS.MH.T0001108 | SS.MH.T0001109 | 373.2547 | 8 | Assign to high frequency cleaning - Grease | 1119.7642 | 0 | Addressed in Capacity Remendiations | Model
14 | 7 | B | SS.GM.T0006936 | SS.MH.T0001012 | SS.MH.T0001011 | 374.9314 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
15 | 7 | B | SS.GM.T0007598 | SS.MH.T0001062 | SS.MH.T0001063 | 81.0725 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
16 | 7 | D | SS.GM.T0007632 | SS.MH.T0001975 | SS.MH.T0001098 | 455.0002 | 6 | Point Repair at 402 ft from 01098 | 4750 | 4750 | Point Repair | Repair
17 | 7 | D | SS.GM.T0007645 | SS.MH.T0001997 | SS.MH.T0001996 | 257.7503 | 6 | Grout Joint at 16 ft from 01996 | 800 | 800 | Grout Joints | Repair
18 | 7 | B | SS.GM.T0007646 | SS.MH.T0010256 | SS.MH.T0001997 | 152.5476 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
19 | 7 | B | SS.GM.T0007651 | SS.MH.T0001116 | SS.MH.T0001117 | 453.455 | 8 | No Rehabilitation Recommended | 0 | 0 | Addressed in Capacity Remendiations | Model
20 | 7 | D | SS.GM.T0007652 | SS.MH.T0001117 | SS.MH.T0001121 | 688.1153 | 8 | Point Repair at 309 and 562 ft from 01117 | 9500 | 0 | Addressed in Capacity Remendiations | Model
21 | 7 | D | SS.GM.T0007656 | SS.MH.T0001122 | SS.MH.T0001123 | 286.8731 | 8 | Burst to 8" - 0 svc | 18646.7526 | 0 | Addressed in Capacity Remendiations | Model
22 | 7 | B | SS.GM.T0009813 | SS.MH.T0001011 | SS.MH.T0000890 | 391.0055 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
23 | 8 | D | SS.GM.T0000397 | SS.MH.T0015262 | SS.MH.T0012830 | 640.2771 | 8 | Point Repair at 179, 183, 256, 440 and 519 ft from 15262 | 23750 | 23750 | Point Repair | Repair
24 | 8 | C | SS.GM.T0006448 | SS.MH.T0001726 | SS.MH.T0001727 | 90.1002 | 8 | 8" CIPP - 0 svc | 4054.5085 | 0 | Monitor in CMOM | None
25 | 8 | C | SS.GM.T0006449 | SS.MH.T0001727 | SS.MH.T0001761 | 181.3 | 8 | 8" CIPP - 0 svc | 8158.5001 | 0 | Monitor in CMOM | None
26 | 8 | D | SS.GM.T0006450 | SS.MH.T0011034 | SS.MH.T0001726 | 687.3138 | 6 | Point Repair at 70 and 309 ft from 01726 | 9500 | 9500 | Point Repair | Repair
27 | 8 | B | SS.GM.T0006644 | SS.MH.T0014497 | SS.MH.T0001036 | 388.6783 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
28 | 8 | D | SS.GM.T0006645 | SS.MH.T0001036 | SS.MH.T0001035 | 529.825 | 21 | Grout Joint at 350 ft from 01036 | 800 | 800 | Grout Joints | Repair
29 | 8 | C | SS.GM.T0006653 | SS.MH.T0013047 | SS.MH.T0001037 | 237.1306 | 12 | Assign to high frequency cleaning | 711.3917 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
30 | 8 | C | SS.GM.T0006654 | SS.MH.T0013516 | SS.MH.T0013047 | 362.3434 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
31 | 8 | D | SS.GM.T0006730 | SS.MH.T0001813 | SS.MH.T0001815 | 235.1892 | 12 | 12" CIPP - 0 svc | 16463.247 | 0 | Addressed in Capacity Remendiations | Model
32 | 8 | B | SS.GM.T0006731 | SS.MH.T0001812 | SS.MH.T0001813 | 333.5859 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
33 | 8 | D | SS.GM.T0006734 | SS.MH.T0002560 | SS.MH.T0002556 | 408.7401 | 8 | Burst to 10" - 1 svc | 31655.5058 | 31655.5058 | Pipe Burst or Replace | Replace
34 | 8 | D | SS.GM.T0006766 | SS.MH.T0011845 | SS.MH.T0001910 | 363.7613 | 6 | Point Repair at 223 ft and Grout Joint at 40 ft from 01910 | 5550 | 5550 | Point Repair & Grout Joint | Repair
35 | 8 | D | SS.GM.T0007150 | SS.MH.T0002617 | SS.MH.T0002616 | 185.7244 | 8 | 8" CIPP - 0 svc | 8357.5965 | 8357.5965 | Cured In Place Pipe Liner | Rehab
36 | 8 | D | SS.GM.T0007168 | SS.MH.T0003162 | SS.MH.T0012907 | 40.0144 | 6 | Grout Joint at 17, 23, 25 and 29 ft from 03162 | 3280.0288 | 3280.0288 | Grout Joints and Add to Root Removal Program in CMOM | Repair
37 | 8 | C | SS.GM.T0007389 | SS.MH.T0001722 | SS.MH.T0012930 | 163.6002 | 6 | Add to Root Removal Schedule | 327.2003 | 0 | Add to Root Removal Program in CMOM | Maintenance
38 | 8 | C | SS.GM.T0007576 | SS.MH.T0001909 | SS.MH.T0001910 | 75.878 | 6 | 6" CIPP - 0 svc | 3414.5082 | 0 | Monitor in CMOM | None
39 | 8 | D | SS.GM.T0007617 | SS.MH.T0015647 | SS.MH.T0013042 | 103.8899 | 12 | 12" CIPP - 0 svc | 7272.2947 | 7272.2947 | Cured In Place Pipe Liner | Rehab
40 | 8 | D | SS.GM.T0007618 | SS.MH.T0013042 | SS.MH.T0001085 | 49.9164 | 12 | 12" CIPP - 0 svc | 3494.1488 | 3494.1488 | Cured In Place Pipe Liner | Rehab
41 | 8 | B | SS.GM.T0007630 | SS.MH.T0001035 | SS.MH.T0013005 | 581.412 | 24 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
42 | 8 | B | SS.GM.T0007669 | SS.MH.T0012488 | SS.MH.T0001718 | 528 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
43 | 8 | B | SS.GM.T0007687 | SS.MH.T0001903 | SS.MH.T0002025 | 135.7681 | 21 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
44 | 8 | D | SS.GM.T0007988 | SS.MH.T0001937 | SS.MH.T0012877 | 226.5739 | 8 | Point Repair at 23, 36 and 59 ft from 01937 | 14250 | 14250 | Point Repair | Repair
45 | 8 | D | SS.GM.T0013189 | SS.MH.T0001983 | SS.MH.T0015276 | 329.0679 | 12 | Replace - 0 svc | 47714.8432 | 47714.8432 | Replace | Replace
46 | 8 | C | SS.GM.T0013190 | SS.MH.T0013045 | SS.MH.T0001036 | 375.738 | 8 | Assign to high frequency cleaning - Grease | 1127.2141 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
47 | 8 | C | SS.GM.T0013831 | SS.MH.T0013048 | SS.MH.T0013516 | 216.5882 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
48 | 8 | D | SS.GM.T0013937 | SS.MH.T0013727 | SS.MH.T0001909 | 627.9981 | 6 | Burst to 8" - 8 svc | 48819.8784 | 48819.8784 | Pipe Burst or Replace | Replace
49 | 8 | B | SS.GM.T0014741 | SS.MH.T0001037 | SS.MH.T0014497 | 174.0279 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
50 | 8 | B | SS.GM.T0015269 | SS.MH.T0015276 | SS.MH.T0013048 | 102 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
51 | 8 | B | SS.GM.T0015327 | SS.MH.T0001084 | SS.MH.T0015647 | 10.3613 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
52 | 10 | B | SS.GM.T0004091 | SS.MH.T0002979 | SS.MH.T0012986 | 318.932 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
53 | 10 | B | SS.GM.T0004092 | SS.MH.T0002980 | SS.MH.T0002979 | 356.2737 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
54 | 10 | D | SS.GM.T0004093 | SS.MH.T0002981 | SS.MH.T0002980 | 475.7 | 8 | Point Repair at 165 ft from 02981 | 4750 | 4750 | Point Repair | Repair
55 | 10 | D | SS.GM.T0004132 | SS.MH.T0004468 | SS.MH.T0004469 | 87.0829 | 6 | Point Repair at 85 ft from 04468 | 4750 | 4750 | Point Repair | Repair
56 | 10 | D | SS.GM.T0007032 | SS.MH.T0000671 | SS.MH.T0002811 | 336.718 | 8 | Point Repair at 85 and 185 ft and Grout Joint at 8 ft from 02811 | 10300 | 10300 | Point Repair & Grout Joint | Repair
57 | 13 | D | SS.GM.T0004865 | SS.MH.T0010949 | SS.MH.T0005106 | 320.0106 | 6 | Replace section 0 to 80 ft from 05106. Point Repair at 128 ft from 05106 | 14350 | 14350 | Replace Section & Point Repair | Repair
58 | 13 | D | SS.GM.T0005511 | SS.MH.T0011758 | SS.MH.T0012797 | 129.8203 | 6 | Point Repair at 109 ft from 12797 | 4750 | 4750 | Point Repair | Repair
59 | 13 | B | SS.GM.T0006092 | SS.MH.T0012914 | SS.MH.T0012911 | 196.5879 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
60 | 13 | D | SS.GM.T0006117 | SS.MH.T0012077 | SS.MH.T0014073 | 66.13 | 6 | Point Repair at 13 ft from 14073 | 4750 | 4750 | Point Repair | Repair
61 | 13 | D | SS.GM.T0006132 | SS.MH.T0004928 | SS.MH.T0004925 | 381.8625 | 18 | Point Repair at 100 ft from 04925 | 4750 | 4750 | Point Repair | Repair
62 | 13 | D | SS.GM.T0006316 | SS.MH.T0011441 | SS.MH.T0012853 | 350.9693 | 6 | Point Repair at 28 ft from 12853 | 4750 | 4750 | Point Repair | Repair
63 | 13 | D | SS.GM.T0006487 | SS.MH.T0012269 | SS.MH.T0003078 | 157.8799 | 6 | Burst to 8" - 4 svc | 14262.1931 | 14262.1931 | Pipe Burst or Replace | Replace
64 | 13 | B | SS.GM.T0007105 | SS.MH.T0011076 | SS.MH.T0012856 | 15.8103 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
65 | 13 | D | SS.GM.T0007113 | SS.MH.T0011444 | SS.MH.T0012855 | 192.3337 | 6 | Point Repair at 111 ft from 12855 | 4750 | 4750 | Point Repair | Repair
66 | 13 | B | SS.GM.T0007123 | SS.MH.T0012719 | SS.MH.T0003289 | 194.95 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
67 | 13 | B | SS.GM.T0008327 | SS.MH.T0010593 | SS.MH.T0012798 | 132.0631 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
68 | 13 | B | SS.GM.T0008455 | SS.MH.T0004623 | SS.MH.T0003118 | 9.7579 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
69 | 13 | B | SS.GM.T0009011 | SS.MH.T0013599 | SS.MH.T0004752 | 104.0432 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
70 | 13 | D | SS.GM.T0009043 | SS.MH.T0004809 | SS.MH.T0004808 | 39.0774 | 6 | Burst to 8" - 0 svc | 2540.0335 | 2540.0335 | Pipe Burst or Replace | Replace
71 | 13 | D | SS.GM.T0009046 | SS.MH.T0004835 | SS.MH.T0004830 | 405.9375 | 8 | Point Repair at 355 ft from 04835 | 4750 | 4750 | Point Repair | Repair
72 | 13 | C | SS.GM.T0009073 | SS.MH.T0004841 | SS.MH.T0004842 | 27.8098 | 8 | No Rehabilitation Recommended | 0 | 0 | Addressed in Capacity Remendiations | Model
73 | 13 | B | SS.GM.T0009254 | SS.MH.T0005057 | SS.MH.T0005017 | 399.2268 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
74 | 13 | A | SS.GM.T0009271 | SS.MH.T0005017 | SS.MH.T0005009 | 70.4523 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
75 | 13 | D | SS.GM.T0009716 | SS.MH.T0005035 | SS.MH.T0005043 | 179.8539 | 12 | Access; Clean and Inspection | 719.4155 | 0 | Addressed in Capacity Remendiations | Model
76 | 13 | D | SS.GM.T0009719 | SS.MH.T0005860 | SS.MH.T0003208 | 537.6248 | 6 | Point Repair at 37 ft from 05860(Cross bore) & Replace section 80 to 30 ft from 03208 | 10750 | 10750 | Replace Section & Point Repair | Repair
77 | 13 | B | SS.GM.T0014772 | SS.MH.T0014748 | SS.MH.T0004756 | 181.1892 | 0 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
78 | 16 | B | SS.GM.T0010350 | SS.MH.T0001704 | SS.MH.T0001478 | 23.8042 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
79 | 16 | A | SS.GM.T0014594 | SS.MH.T0014706 | SS.MH.T0014705 | 228.7196 | 0 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
80 | 17 | C | SS.GM.T0000630 | SS.MH.T0003434 | SS.MH.T0003433 | 246.5132 | 6 | Add to Root Removal Schedule | 493.0263 | 0 | Add to Root Removal Program in CMOM | Maintenance
81 | 17 | C | SS.GM.T0000631 | SS.MH.T0003436 | SS.MH.T0003434 | 447.6767 | 6 | Add to Root Removal Schedule | 895.3533 | 0 | Add to Root Removal Program in CMOM | Maintenance
82 | 17 | D | SS.GM.T0000909 | SS.MH.T0013508 | SS.MH.T0003539 | 62.2033 | 15 | Burst to 18" - 0 svc | 5909.3138 | 5909.3138 | Pipe Burst or Replace | Replace
83 | 17 | B | SS.GM.T0000911 | SS.MH.T0003385 | SS.MH.T0007096 | 426.9005 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
84 | 17 | D | SS.GM.T0000926 | SS.MH.T0002397 | SS.MH.T0002398 | 348.9197 | 8 | Burst to 10" - 2 svc | 28168.9742 | 28168.9742 | Pipe Burst or Replace | Replace
85 | 17 | D | SS.GM.T0000927 | SS.MH.T0014133 | SS.MH.T0002397 | 307.3874 | 6 | Point Repair at 10, 158 and 211 ft from 14133 | 14250 | 14250 | Point Repair | Repair
86 | 17 | D | SS.GM.T0000928 | SS.MH.T0002395 | SS.MH.T0002396 | 326.9398 | 6 | Point Repair at 58, 60, 104, 135 & 152 ft from 02395 | 23750 | 23750 | Point Repair | Repair
87 | 17 | D | SS.GM.T0000929 | SS.MH.T0002394 | SS.MH.T0002395 | 360.3383 | 6 | Burst to 8" - 0 svc | 23421.9877 | 23421.9877 | Pipe Burst or Replace | Replace
88 | 17 | C | SS.GM.T0000933 | SS.MH.T0001491 | SS.MH.T0001490 | 188.6615 | 6 | Add to Root Removal Schedule | 377.323 | 0 | Add to Root Removal Program in CMOM | Maintenance
89 | 17 | B | SS.GM.T0001088 | SS.MH.T0003533 | SS.MH.T0003535 | 212.2591 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
90 | 17 | D | SS.GM.T0001108 | SS.MH.T0003528 | SS.MH.T0015638 | 294.6784 | 12 | Point Repair at 44 and Grout Joint at 218 and 220 ft from 03528 | 6350 | 6350 | Point Repair & Grout Joint | Repair
91 | 17 | D | SS.GM.T0001118 | SS.MH.T0003597 | SS.MH.T0003598 | 272.1908 | 18 | 18" CIPP - 0 svc | 32662.9011 | 32662.9011 | Cured In Place Pipe Liner | Rehab
92 | 17 | C | SS.GM.T0001132 | SS.MH.T0014669 | SS.MH.T0001560 | 277.521 | 8 | Point Repair at 14 ft from 01560 | 4750 | 0 | Monitor in CMOM | None
93 | 17 | D | SS.GM.T0001133 | SS.MH.T0001557 | SS.MH.T0014669 | 38.8154 | 6 | Point Repair at 10 and 34 ft from 01557 | 9500 | 9500 | Point Repair | Repair
94 | 17 | B | SS.GM.T0001276 | SS.MH.T0011006 | SS.MH.T0003485 | 35.6489 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
95 | 17 | D | SS.GM.T0001594 | SS.MH.T0003598 | SS.MH.T0003599 | 91.4484 | 18 | 18" CIPP - 0 svc | 10973.8074 | 10973.8074 | Cured In Place Pipe Liner | Rehab
96 | 17 | D | SS.GM.T0001595 | SS.MH.T0003599 | SS.MH.T0014697 | 84.0401 | 18 | 18" CIPP - 0 svc | 10084.8154 | 10084.8154 | Cured In Place Pipe Liner | Rehab
97 | 17 | D | SS.GM.T0001596 | SS.MH.T0003549 | SS.MH.T0015480 | 284.3269 | 6 | Point Repair at 82 and 110 ft from 03549 | 9500 | 9500 | Point Repair | Repair
98 | 17 | C | SS.GM.T0001597 | SS.MH.T0003547 | SS.MH.T0003652 | 196.1832 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
99 | 17 | B | SS.GM.T0001600 | SS.MH.T0003708 | SS.MH.T0015672 | 179.5919 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
100 | 17 | B | SS.GM.T0001621 | SS.MH.T0015648 | SS.MH.T0005482 | 118.3833 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
101 | 17 | B | SS.GM.T0001815 | SS.MH.T0010724 | SS.MH.T0003664 | 50.6942 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
102 | 17 | B | SS.GM.T0001891 | SS.MH.T0002448 | SS.MH.T0003756 | 216.5064 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
103 | 17 | B | SS.GM.T0001892 | SS.MH.T0003756 | SS.MH.T0003755 | 35.6245 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
104 | 17 | D | SS.GM.T0001923 | SS.MH.T0001700 | SS.MH.T0003557 | 71.1175 | 6 | Burst to 8" - 0 svc | 4622.6378 | 4622.6378 | Pipe Burst or Replace | Replace
105 | 17 | B | SS.GM.T0001945 | SS.MH.T0003751 | SS.MH.T0007357 | 154.8983 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
106 | 17 | B | SS.GM.T0001946 | SS.MH.T0003752 | SS.MH.T0003753 | 130.786 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
107 | 17 | B | SS.GM.T0001947 | SS.MH.T0003753 | SS.MH.T0003754 | 100.1126 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
108 | 17 | B | SS.GM.T0001948 | SS.MH.T0003754 | SS.MH.T0003755 | 281.498 | 8 | Assign to high frequency cleaning - Grease | 844.4939 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
109 | 17 | B | SS.GM.T0002197 | SS.MH.T0010205 | SS.MH.T0003821 | 124.2906 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
110 | 17 | B | SS.GM.T0002212 | SS.MH.T0007031 | SS.MH.T0002448 | 326.5578 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
111 | 17 | B | SS.GM.T0002216 | SS.MH.T0010886 | SS.MH.T0004153 | 291.8002 | 6 | Assign to high frequency cleaning - Grease | 875.4006 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
112 | 17 | D | SS.GM.T0002217 | SS.MH.T0011979 | SS.MH.T0005592 | 136.8958 | 6 | Point Repair at 110 ft from 05592 | 4750 | 4750 | Point Repair | Repair
113 | 17 | B | SS.GM.T0002218 | SS.MH.T0000365 | SS.MH.T0011985 | 223.4927 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
114 | 17 | B | SS.GM.T0002224 | SS.MH.T0010712 | SS.MH.T0003560 | 23.7005 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
115 | 17 | B | SS.GM.T0002234 | SS.MH.T0011708 | SS.MH.T0003751 | 100.961 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
116 | 17 | B | SS.GM.T0002288 | SS.MH.T0003759 | SS.MH.T0003758 | 163.1443 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
117 | 17 | D | SS.GM.T0002290 | SS.MH.T0003755 | SS.MH.T0003757 | 330.4925 | 10 | 10" CIPP - 0 svc | 16524.6254 | 16524.6254 | Cured In Place Pipe Liner | Rehab
118 | 17 | B | SS.GM.T0002371 | SS.MH.T0010195 | SS.MH.T0003706 | 220.5001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
119 | 17 | B | SS.GM.T0002375 | SS.MH.T0003543 | SS.MH.T0003542 | 327.92 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
120 | 17 | C | SS.GM.T0002399 | SS.MH.T0003658 | SS.MH.T0003660 | 286.8091 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
121 | 17 | B | SS.GM.T0002451 | SS.MH.T0001547 | SS.MH.T0003763 | 52.068 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
122 | 17 | B | SS.GM.T0002461 | SS.MH.T0003530 | SS.MH.T0015638 | 133.479 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
123 | 17 | D | SS.GM.T0002489 | SS.MH.T0003435 | SS.MH.T0003433 | 143.9372 | 6 | Point Repair at 36 ft from 03435 | 4750 | 4750 | Point Repair | Repair
124 | 17 | B | SS.GM.T0002490 | SS.MH.T0003433 | SS.MH.T0003432 | 26.8712 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
125 | 17 | B | SS.GM.T0002493 | SS.MH.T0003425 | SS.MH.T0003429 | 423.0176 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
126 | 17 | B | SS.GM.T0002520 | SS.MH.T0001524 | SS.MH.T0001526 | 298.6057 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
127 | 17 | D | SS.GM.T0002529 | SS.MH.T0001503 | SS.MH.T0015278 | 364.9959 | 6 | Point Repair at 298 ft from 01503 | 4750 | 4750 | Point Repair | Repair
128 | 17 | D | SS.GM.T0002653 | SS.MH.T0009895 | SS.MH.T0000318 | 158.5893 | 6 | Point Repair at 54 ft from 00318 | 4750 | 4750 | Point Repair | Repair
129 | 17 | D | SS.GM.T0002656 | SS.MH.T0009892 | SS.MH.T0005479 | 311.8233 | 6 | Point Repair at 29 ft from 05479 | 4750 | 4750 | Point Repair | Repair
130 | 17 | B | SS.GM.T0002657 | SS.MH.T0000316 | SS.MH.T0005478 | 236.0879 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
131 | 17 | B | SS.GM.T0002658 | SS.MH.T0005477 | SS.MH.T0000316 | 77.9659 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
132 | 17 | B | SS.GM.T0002659 | SS.MH.T0000309 | SS.MH.T0005477 | 219.4481 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
133 | 17 | B | SS.GM.T0002955 | SS.MH.T0005593 | SS.MH.T0005592 | 69.7677 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
134 | 17 | B | SS.GM.T0002957 | SS.MH.T0010245 | SS.MH.T0000365 | 170.3468 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
135 | 17 | B | SS.GM.T0002964 | SS.MH.T0003472 | SS.MH.T0003473 | 55.122 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
136 | 17 | B | SS.GM.T0003129 | SS.MH.T0011986 | SS.MH.T0003543 | 181.2998 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
137 | 17 | D | SS.GM.T0003161 | SS.MH.T0011220 | SS.MH.T0002436 | 486.9999 | 6 | Point Repair at 21 and 58 ft from 02436 | 9500 | 9500 | Point Repair | Repair
138 | 17 | B | SS.GM.T0003185 | SS.MH.T0003935 | SS.MH.T0003901 | 98.4913 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
139 | 17 | B | SS.GM.T0003235 | SS.MH.T0003758 | SS.MH.T0003756 | 117.0495 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
140 | 17 | C | SS.GM.T0003245 | SS.MH.T0003720 | SS.MH.T0003557 | 474.0747 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
141 | 17 | B | SS.GM.T0003282 | SS.MH.T0003706 | SS.MH.T0000342 | 53.5482 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
142 | 17 | C | SS.GM.T0003283 | SS.MH.T0003542 | SS.MH.T0003544 | 288.5674 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
143 | 17 | B | SS.GM.T0003320 | SS.MH.T0003600 | SS.MH.T0014697 | 171.4064 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
144 | 17 | D | SS.GM.T0003383 | SS.MH.T0001526 | SS.MH.T0001525 | 282.93 | 8 | Access; Clean and Inspection | 1131.72 | 1131.72 | Access; Clean and Inspection | Inspect
145 | 17 | C | SS.GM.T0003388 | SS.MH.T0001490 | SS.MH.T0002398 | 290.4977 | 6 | Add to Root Removal Schedule | 580.9953 | 0 | Add to Root Removal Program in CMOM | Maintenance
146 | 17 | B | SS.GM.T0003389 | SS.MH.T0002401 | SS.MH.T0002402 | 69.8793 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
147 | 17 | B | SS.GM.T0003518 | SS.MH.T0010711 | SS.MH.T0003560 | 3.0137 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
148 | 17 | C | SS.GM.T0003698 | SS.MH.T0006193 | SS.MH.T0003771 | 593.6918 | 6 | Add to Root Removal Schedule | 1187.3835 | 0 | Add to Root Removal Program in CMOM | Maintenance
149 | 17 | B | SS.GM.T0003704 | SS.MH.T0005480 | SS.MH.T0000318 | 257.583 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
150 | 17 | B | SS.GM.T0003705 | SS.MH.T0000318 | SS.MH.T0005481 | 232.4252 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
151 | 17 | C | SS.GM.T0007796 | SS.MH.T0009626 | SS.MH.T0002270 | 350.1147 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
152 | 17 | B | SS.GM.T0009995 | SS.MH.T0003799 | SS.MH.T0003800 | 365.6069 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
153 | 17 | B | SS.GM.T0010265 | SS.MH.T0009101 | SS.MH.T0001440 | 107.6188 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
154 | 17 | D | SS.GM.T0010267 | SS.MH.T0009099 | SS.MH.T0001440 | 339.9034 | 8 | Replace section from 270 ft from 01440 to 09099. | 9100 | 9100 | Replace Section | Repair
155 | 17 | B | SS.GM.T0010278 | SS.MH.T0007890 | SS.MH.T0014681 | 130.5983 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
156 | 17 | B | SS.GM.T0010472 | SS.MH.T0007359 | SS.MH.T0007357 | 260.5929 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
157 | 17 | B | SS.GM.T0012619 | SS.MH.T0001635 | SS.MH.T0007354 | 350.6882 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
158 | 17 | B | SS.GM.T0012620 | SS.MH.T0007354 | SS.MH.T0007356 | 77.5162 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
159 | 17 | B | SS.GM.T0012804 | SS.MH.T0009156 | SS.MH.T0003560 | 81.8071 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
160 | 17 | B | SS.GM.T0013447 | SS.MH.T0013952 | SS.MH.T0003542 | 150.0997 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
161 | 17 | B | SS.GM.T0013600 | SS.MH.T0001369 | SS.MH.T0013562 | 178.5797 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
162 | 17 | B | SS.GM.T0013601 | SS.MH.T0013562 | SS.MH.T0013563 | 66.5636 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
163 | 17 | D | SS.GM.T0014106 | SS.MH.T0002396 | SS.MH.T0014133 | 47.6917 | 6 | Point Repair at 24 ft from 02396 | 4750 | 4750 | Point Repair | Repair
164 | 17 | D | SS.GM.T0014577 | SS.MH.T0014697 | SS.MH.T0003548 | 49.8733 | 18 | 18" CIPP - 0 svc | 5984.7989 | 5984.7989 | Cured In Place Pipe Liner | Rehab
165 | 17 | B | SS.GM.T0014616 | SS.MH.T0014196 | SS.MH.T0014195 | 54.159 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
166 | 17 | B | SS.GM.T0014617 | SS.MH.T0014195 | SS.MH.T0014194 | 110.5289 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
167 | 17 | A | SS.GM.T0014618 | SS.MH.T0014187 | SS.MH.T0014195 | 233.2721 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
168 | 17 | B | SS.GM.T0014619 | SS.MH.T0014216 | SS.MH.T0014196 | 241.8685 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
169 | 17 | B | SS.GM.T0014881 | SS.MH.T0002388 | SS.MH.T0014361 | 59.8336 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
170 | 17 | B | SS.GM.T0015273 | SS.MH.T0007357 | SS.MH.T0003752 | 137.0102 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
171 | 17 | B | SS.GM.T0015276 | SS.MH.T0015278 | SS.MH.T0002395 | 207.8157 | 6 | Assign to high frequency cleaning - Grease | 623.4471 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
172 | 17 | B | SS.GM.T0015287 | SS.MH.T0015638 | SS.MH.T0015639 | 31.3919 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
173 | 17 | B | SS.GM.T0015288 | SS.MH.T0015639 | SS.MH.T0003584 | 3.7439 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
174 | 17 | B | SS.GM.T0015342 | SS.MH.T0005481 | SS.MH.T0015648 | 71.2637 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
175 | 18 | C | SS.GM.T0000344 | SS.MH.T0004298 | SS.MH.T0004297 | 182.7898 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
176 | 18 | D | SS.GM.T0000345 | SS.MH.T0002531 | SS.MH.T0004298 | 519.3676 | 6 | Burst to 8" - 0 svc | 33758.8935 | 33758.8935 | Pipe Burst or Replace | Replace
177 | 18 | D | SS.GM.T0000346 | SS.MH.T0004296 | SS.MH.T0004297 | 378.6413 | 6 | Point Repair at 227 ft from 04296 | 4750 | 4750 | Point Repair | Repair
178 | 18 | C | SS.GM.T0000347 | SS.MH.T0004297 | SS.MH.T0004294 | 513.1363 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
179 | 18 | D | SS.GM.T0000348 | SS.MH.T0004291 | SS.MH.T0004290 | 339.0912 | 6 | Burst to 8" - 2 svc | 24040.9296 | 24040.9296 | Pipe Burst or Replace | Replace
180 | 18 | D | SS.GM.T0000349 | SS.MH.T0004299 | SS.MH.T0004291 | 339.2652 | 6 | Burst to 8" - 3 svc | 25052.237 | 25052.237 | Pipe Burst or Replace | Replace
181 | 18 | B | SS.GM.T0000350 | SS.MH.T0009906 | SS.MH.T0004251 | 374.1745 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
182 | 18 | B | SS.GM.T0000352 | SS.MH.T0004279 | SS.MH.T0004278 | 27.2696 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
183 | 18 | C | SS.GM.T0000353 | SS.MH.T0004289 | SS.MH.T0004279 | 209.8551 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
184 | 18 | C | SS.GM.T0000354 | SS.MH.T0004266 | SS.MH.T0004277 | 297.306 | 6 | Add to Root Removal Schedule | 594.612 | 0 | Add to Root Removal Program in CMOM | Maintenance
185 | 18 | C | SS.GM.T0000355 | SS.MH.T0010168 | SS.MH.T0004266 | 969.3369 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
186 | 18 | D | SS.GM.T0000356 | SS.MH.T0004275 | SS.MH.T0004274 | 662.2967 | 6 | Burst to 8" - 7 svc | 50049.2873 | 50049.2873 | Pipe Burst or Replace | Replace
187 | 18 | D | SS.GM.T0000357 | SS.MH.T0004276 | SS.MH.T0004275 | 319.5469 | 6 | Burst to 8" - 5 svc | 25770.5471 | 25770.5471 | Pipe Burst or Replace | Replace
188 | 18 | B | SS.GM.T0000382 | SS.MH.T0015120 | SS.MH.T0013137 | 300.5133 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
189 | 18 | D | SS.GM.T0000383 | SS.MH.T0012301 | SS.MH.T0002531 | 357.2506 | 6 | Point Repair at 35 and 181 ft from 02531 | 9500 | 9500 | Point Repair | Repair
190 | 18 | D | SS.GM.T0000384 | SS.MH.T0012313 | SS.MH.T0004296 | 542.3684 | 6 | Burst to 8" - 7 svc | 42253.9465 | 42253.9465 | Pipe Burst or Replace | Replace
191 | 18 | D | SS.GM.T0000385 | SS.MH.T0010685 | SS.MH.T0004296 | 361.5027 | 6 | Point Repair at 89 ft from 04296 | 4750 | 4750 | Point Repair | Repair
192 | 18 | D | SS.GM.T0000386 | SS.MH.T0012305 | SS.MH.T0004297 | 264.6486 | 6 | Point Repair at 22 ft from 04297 | 4750 | 4750 | Point Repair | Repair
193 | 18 | D | SS.GM.T0000387 | SS.MH.T0011183 | SS.MH.T0004295 | 274.5288 | 6 | Point Repair at 102 ft from 04295 | 4750 | 4750 | Point Repair | Repair
194 | 18 | D | SS.GM.T0000388 | SS.MH.T0011518 | SS.MH.T0004291 | 441.8862 | 6 | Point Repair at 7, 102 and 130 ft from 04291 and Add to Root Removal Schedule | 15133.7725 | 15133.7725 | Point Repair and Add to Root Removal Program in CMOM | Repair
195 | 18 | D | SS.GM.T0000389 | SS.MH.T0010683 | SS.MH.T0004299 | 401.5293 | 6 | Burst to 8" - 0 svc | 26099.4056 | 26099.4056 | Pipe Burst or Replace | Replace
196 | 18 | D | SS.GM.T0000390 | SS.MH.T0011939 | SS.MH.T0004275 | 606.0698 | 6 | Burst to 8" - 10 svc | 49394.5355 | 49394.5355 | Pipe Burst or Replace | Replace
197 | 18 | D | SS.GM.T0000391 | SS.MH.T0012317 | SS.MH.T0004276 | 644.5432 | 6 | Burst to 8" - 4 svc | 45895.31 | 45895.31 | Pipe Burst or Replace | Replace
198 | 18 | D | SS.GM.T0000392 | SS.MH.T0011193 | SS.MH.T0004276 | 243.6771 | 6 | Burst to 8" - 4 svc | 19839.0088 | 19839.0088 | Pipe Burst or Replace | Replace
199 | 18 | D | SS.GM.T0000393 | SS.MH.T0010697 | SS.MH.T0004287 | 270.9627 | 6 | Burst to 8" - 2 svc | 19612.5761 | 19612.5761 | Pipe Burst or Replace | Replace
200 | 18 | D | SS.GM.T0000394 | SS.MH.T0010846 | SS.MH.T0004248 | 312.3522 | 6 | Burst to 8" - 1 svc | 21302.896 | 21302.896 | Pipe Burst or Replace | Replace
201 | 18 | D | SS.GM.T0000395 | SS.MH.T0010851 | SS.MH.T0004249 | 259.3462 | 6 | Point Repair at 191 ft from 04249 | 4750 | 4750 | Point Repair | Repair
202 | 18 | C | SS.GM.T0000396 | SS.MH.T0012330 | SS.MH.T0005148 | 60.0016 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
203 | 18 | D | SS.GM.T0000399 | SS.MH.T0004317 | SS.MH.T0004316 | 396.8171 | 6 | Burst to 8" - 10 svc | 35793.1102 | 35793.1102 | Pipe Burst or Replace | Replace
204 | 18 | C | SS.GM.T0000400 | SS.MH.T0004316 | SS.MH.T0004307 | 189.3423 | 8 | Add to Root Removal Schedule | 378.6846 | 0 | Add to Root Removal Program in CMOM | Maintenance
205 | 18 | D | SS.GM.T0000402 | SS.MH.T0006330 | SS.MH.T0006336 | 1053.6361 | 6 | Burst to 8" - 10 svc | 78486.3491 | 78486.3491 | Pipe Burst or Replace | Replace
206 | 18 | B | SS.GM.T0000403 | SS.MH.T0006329 | SS.MH.T0006330 | 21.6301 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
207 | 18 | B | SS.GM.T0000404 | SS.MH.T0006326 | SS.MH.T0006327 | 100.2677 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
208 | 18 | B | SS.GM.T0000405 | SS.MH.T0004327 | SS.MH.T0006326 | 33.7387 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
209 | 18 | D | SS.GM.T0000406 | SS.MH.T0000334 | SS.MH.T0006326 | 303.3219 | 6 | Burst to 8" - 2 svc | 21715.9204 | 21715.9204 | Pipe Burst or Replace | Replace
210 | 18 | B | SS.GM.T0000407 | SS.MH.T0004305 | SS.MH.T0004304 | 39.1004 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
211 | 18 | C | SS.GM.T0000408 | SS.MH.T0004306 | SS.MH.T0004304 | 313.0233 | 8 | Point Repair at 45, 147 and 239 ft from 04304 | 14250 | 0 | Monitor in CMOM | None
212 | 18 | B | SS.GM.T0000409 | SS.MH.T0004307 | SS.MH.T0004306 | 69.732 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
213 | 18 | D | SS.GM.T0000410 | SS.MH.T0005999 | SS.MH.T0004307 | 226.5813 | 6 | Burst to 8" - 2 svc | 16727.7861 | 16727.7861 | Pipe Burst or Replace | Replace
214 | 18 | C | SS.GM.T0000411 | SS.MH.T0004304 | SS.MH.T0004303 | 155.6746 | 8 | Point Repair at 126 ft from 04304 | 4750 | 0 | Monitor in CMOM | None
215 | 18 | B | SS.GM.T0000412 | SS.MH.T0004303 | SS.MH.T0004302 | 209.3216 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
216 | 18 | B | SS.GM.T0000413 | SS.MH.T0004302 | SS.MH.T0004301 | 49.6556 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
217 | 18 | C | SS.GM.T0000414 | SS.MH.T0004301 | SS.MH.T0004312 | 347.1852 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
218 | 18 | D | SS.GM.T0000415 | SS.MH.T0004312 | SS.MH.T0004313 | 323.5381 | 8 | Point Repair at 320 ft from 04213 and Add to Root Removal Schedule | 5397.0761 | 5397.0761 | Point Repair and Add to Root Removal Program in CMOM | Repair
219 | 18 | B | SS.GM.T0000416 | SS.MH.T0011186 | SS.MH.T0004293 | 595.3902 | 6 | Assign to high frequency cleaning - Grease | 1786.1707 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
220 | 18 | C | SS.GM.T0000417 | SS.MH.T0004314 | SS.MH.T0004315 | 307.5484 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
221 | 18 | C | SS.GM.T0000419 | SS.MH.T0000746 | SS.MH.T0005231 | 283.1487 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
222 | 18 | C | SS.GM.T0000420 | SS.MH.T0004285 | SS.MH.T0000746 | 732.4057 | 8 | Point Repair at 423 ft from 04285 | 4750 | 0 | Monitor in CMOM | None
223 | 18 | B | SS.GM.T0000421 | SS.MH.T0005231 | SS.MH.T0005230 | 90.0105 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
224 | 18 | B | SS.GM.T0000423 | SS.MH.T0005237 | SS.MH.T0005236 | 321.8382 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
225 | 18 | D | SS.GM.T0000424 | SS.MH.T0005241 | SS.MH.T0005239 | 363.6878 | 6 | Burst to 8" - 0 svc | 23639.7056 | 23639.7056 | Pipe Burst or Replace | Replace
226 | 18 | D | SS.GM.T0000425 | SS.MH.T0005236 | SS.MH.T0005235 | 356.8407 | 6 | Burst to 8" - 0 svc | 23194.6435 | 23194.6435 | Pipe Burst or Replace | Replace
227 | 18 | C | SS.GM.T0000426 | SS.MH.T0004330 | SS.MH.T0004329 | 297.5108 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
228 | 18 | D | SS.GM.T0000427 | SS.MH.T0004331 | SS.MH.T0004330 | 300.0123 | 6 | Point Repair at 71 and 219 ft from 04331 | 9500 | 9500 | Point Repair | Repair
229 | 18 | C | SS.GM.T0000428 | SS.MH.T0004334 | SS.MH.T0004333 | 638.0028 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
230 | 18 | C | SS.GM.T0000429 | SS.MH.T0004328 | SS.MH.T0004330 | 641.1589 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
231 | 18 | D | SS.GM.T0000430 | SS.MH.T0004332 | SS.MH.T0000749 | 238.5659 | 6 | Grout Joint at 26 ft from 04332 | 800 | 800 | Grout Joints | Repair
232 | 18 | C | SS.GM.T0000431 | SS.MH.T0000749 | SS.MH.T0005222 | 199.6447 | 8 | Add to Root Removal Schedule - Performed by the City | 399.2894 | 0 | Add to Root Removal Program in CMOM | Maintenance
233 | 18 | D | SS.GM.T0000432 | SS.MH.T0005147 | SS.MH.T0005142 | 324.7356 | 6 | Point Repair at 7 and 161 ft from 05147 | 9500 | 9500 | Point Repair | Repair
234 | 18 | D | SS.GM.T0000433 | SS.MH.T0004311 | SS.MH.T0005147 | 521.8404 | 6 | Point Repair at 119, 188 and 195 ft from 04310 and 115 ft from 04311 | 14250 | 14250 | Point Repair | Repair
235 | 18 | C | SS.GM.T0000434 | SS.MH.T0005143 | SS.MH.T0005142 | 142.5117 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
236 | 18 | B | SS.GM.T0000436 | SS.MH.T0005155 | SS.MH.T0000265 | 9.9468 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
237 | 18 | B | SS.GM.T0000437 | SS.MH.T0005153 | SS.MH.T0013309 | 163.7635 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
238 | 18 | B | SS.GM.T0000438 | SS.MH.T0005152 | SS.MH.T0005153 | 193.963 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
239 | 18 | B | SS.GM.T0000439 | SS.MH.T0005151 | SS.MH.T0005152 | 216.1769 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
240 | 18 | C | SS.GM.T0000440 | SS.MH.T0010073 | SS.MH.T0005151 | 444.6803 | 6 | Add to Root Removal Schedule | 889.3606 | 0 | Add to Root Removal Program in CMOM | Maintenance
241 | 18 | B | SS.GM.T0000443 | SS.MH.T0000265 | SS.MH.T0005177 | 20.7766 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
242 | 18 | C | SS.GM.T0000445 | SS.MH.T0000266 | SS.MH.T0005156 | 245.7898 | 6 | Point Repair at 238 and 261 ft from 00266 | 9500 | 0 | Monitor in CMOM | None
243 | 18 | C | SS.GM.T0000446 | SS.MH.T0005150 | SS.MH.T0000266 | 649.8396 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
244 | 18 | D | SS.GM.T0000447 | SS.MH.T0005149 | SS.MH.T0005150 | 328.8734 | 6 | Point Repair at 90, 100 and 174 ft from 05149 and 54 ft from 05150 | 19000 | 19000 | Point Repair | Repair
245 | 18 | C | SS.GM.T0000448 | SS.MH.T0010129 | SS.MH.T0005149 | 177.3628 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
246 | 18 | D | SS.GM.T0000449 | SS.MH.T0005226 | SS.MH.T0005227 | 185.8646 | 6 | Burst to 8" - 0 svc | 12081.1976 | 12081.1976 | Pipe Burst or Replace | Replace
247 | 18 | D | SS.GM.T0000450 | SS.MH.T0005225 | SS.MH.T0005226 | 477.5496 | 6 | Burst to 8" - 7 svc | 38040.7259 | 38040.7259 | Pipe Burst or Replace | Replace
248 | 18 | D | SS.GM.T0000451 | SS.MH.T0005232 | SS.MH.T0005226 | 532.418 | 6 | Point Repair at 46 ft from 05232 and 50 ft from 05226 | 9500 | 9500 | Point Repair | Repair
249 | 18 | D | SS.GM.T0000452 | SS.MH.T0005233 | SS.MH.T0005232 | 349.9201 | 6 | Point Repair at 164 ft from 05232 and 148 ft from 05233 and Add to Root Removal Schedule | 10199.8402 | 10199.8402 | Point Repair and Add to Root Removal Program in CMOM | Repair
250 | 18 | B | SS.GM.T0000453 | SS.MH.T0005234 | SS.MH.T0005233 | 57.623 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
251 | 18 | B | SS.GM.T0000544 | SS.MH.T0005171 | SS.MH.T0005172 | 115.9762 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
252 | 18 | B | SS.GM.T0000545 | SS.MH.T0005172 | SS.MH.T0005173 | 28.6581 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
253 | 18 | D | SS.GM.T0000546 | SS.MH.T0005178 | SS.MH.T0005179 | 462.9796 | 6 | Point Repair at 135, 136 and 176 ft from 05178 | 14250 | 14250 | Point Repair | Repair
254 | 18 | D | SS.GM.T0000547 | SS.MH.T0005179 | SS.MH.T0000271 | 150.0166 | 6 | Burst to 8" - 0 svc | 9751.0822 | 9751.0822 | Pipe Burst or Replace | Replace
255 | 18 | C | SS.GM.T0000550 | SS.MH.T0005174 | SS.MH.T0005998 | 99.6795 | 6 | Point Repair at 94 ft from 05174 | 4750 | 0 | Monitor in CMOM | None
256 | 18 | D | SS.GM.T0000552 | SS.MH.T0005169 | SS.MH.T0005170 | 249.5457 | 6 | Replace section 190 to 245 ft from 05170. | 6600 | 6600 | Replace Section | Repair
257 | 18 | C | SS.GM.T0000647 | SS.MH.T0010866 | SS.MH.T0005148 | 192.5426 | 6 | Point Repair at 97 ft from 05148 | 4750 | 0 | Monitor in CMOM | None
258 | 18 | C | SS.GM.T0000648 | SS.MH.T0011210 | SS.MH.T0004281 | 304.9496 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
259 | 18 | D | SS.GM.T0000649 | SS.MH.T0004345 | SS.MH.T0004344 | 72.9197 | 8 | Point Repair at 20 ft from 04344 and 36 ft from 04345 | 9500 | 9500 | Point Repair | Repair
260 | 18 | D | SS.GM.T0000650 | SS.MH.T0013994 | SS.MH.T0015434 | 648.504 | 8 | Point Repair at 43 ft from 15434 and Grout Joint at 28, 106, 127 and 275 ft from 13994 | 7950 | 7950 | Point Repair & Grout Joint | Repair
261 | 18 | B | SS.GM.T0000651 | SS.MH.T0006122 | SS.MH.T0006121 | 42.5541 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
262 | 18 | B | SS.GM.T0000652 | SS.MH.T0013191 | SS.MH.T0006124 | 189.1117 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
263 | 18 | B | SS.GM.T0000653 | SS.MH.T0006124 | SS.MH.T0006125 | 161.4705 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
264 | 18 | B | SS.GM.T0000654 | SS.MH.T0006125 | SS.MH.T0006122 | 299.4282 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
265 | 18 | C | SS.GM.T0000655 | SS.MH.T0004338 | SS.MH.T0004345 | 531.0324 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
266 | 18 | D | SS.GM.T0000656 | SS.MH.T0014963 | SS.MH.T0004335 | 656.831 | 6 | Burst to 8" - 10 svc | 52694.0148 | 52694.0148 | Pipe Burst or Replace | Replace
267 | 18 | D | SS.GM.T0000657 | SS.MH.T0004340 | SS.MH.T0004338 | 181.0587 | 6 | Point Repair at 160 and 163 ft from 04340 | 9500 | 9500 | Point Repair | Repair
268 | 18 | C | SS.GM.T0000658 | SS.MH.T0012331 | SS.MH.T0004340 | 696.7941 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
269 | 18 | D | SS.GM.T0000659 | SS.MH.T0006399 | SS.MH.T0004338 | 490.8842 | 8 | Burst to 8" - 6 svc | 37907.4706 | 37907.4706 | Pipe Burst or Replace | Replace
270 | 18 | D | SS.GM.T0000660 | SS.MH.T0006379 | SS.MH.T0006399 | 900.0069 | 6 | Point Repair at 52 and 75 ft from 06399 and Add to Root Removal Schedule | 11300.0138 | 11300.0138 | Point Repair and Add to Root Removal Program in CMOM | Repair
271 | 18 | C | SS.GM.T0000661 | SS.MH.T0006372 | SS.MH.T0006379 | 920.2171 | 6 | Burst to 8" - 12 svc | 71814.112 | 0 | Monitor in CMOM | None
272 | 18 | C | SS.GM.T0000662 | SS.MH.T0011748 | SS.MH.T0006372 | 183.3249 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
273 | 18 | E | SS.GM.T0000663 | SS.MH.T0010862 | SS.MH.T0006399 | 334.3977 | 6 | Point Repair at 16 and 83 ft from 10862. Crossbore @ 83. Telephone pole | 9500 | 9500 | Point Repair | Repair
274 | 18 | B | SS.GM.T0000664 | SS.MH.T0005359 | SS.MH.T0006128 | 152.0688 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
275 | 18 | B | SS.GM.T0000665 | SS.MH.T0006364 | SS.MH.T0005359 | 293.427 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
276 | 18 | D | SS.GM.T0000666 | SS.MH.T0004341 | SS.MH.T0004342 | 662.8009 | 6 | Point Repair at 9 and 28 ft from 04341 and 155 and crossbore 227 ft from 04342 | 19000 | 19000 | Point Repair | Repair
277 | 18 | D | SS.GM.T0000667 | SS.MH.T0011208 | SS.MH.T0004341 | 156.7598 | 6 | Point Repair at 71 and 81 ft from 04341 | 9500 | 9500 | Point Repair | Repair
278 | 18 | B | SS.GM.T0000669 | SS.MH.T0005362 | SS.MH.T0005363 | 297.8785 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
279 | 18 | C | SS.GM.T0000670 | SS.MH.T0012186 | SS.MH.T0005361 | 415.5175 | 6 | Add to Root Removal Schedule | 831.035 | 0 | Add to Root Removal Program in CMOM | Maintenance
280 | 18 | B | SS.GM.T0000671 | SS.MH.T0011204 | SS.MH.T0005362 | 223.8 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
281 | 18 | C | SS.GM.T0000672 | SS.MH.T0005361 | SS.MH.T0005362 | 302.9197 | 6 | Point Repair at 38 and 248 ft from 05361 | 9500 | 0 | Monitor in CMOM | None
282 | 18 | D | SS.GM.T0000673 | SS.MH.T0011109 | SS.MH.T0005362 | 793.9355 | 6 | Point Repair at 47, 210, 224 and 239 ft from 05362 | 19000 | 19000 | Point Repair | Repair
283 | 18 | B | SS.GM.T0000674 | SS.MH.T0005357 | SS.MH.T0005266 | 320.8778 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
284 | 18 | D | SS.GM.T0000675 | SS.MH.T0010702 | SS.MH.T0005358 | 202.2603 | 6 | Point Repair at 92 and 95 ft from 05358 | 9500 | 9500 | Point Repair | Repair
285 | 18 | D | SS.GM.T0000676 | SS.MH.T0005358 | SS.MH.T0005357 | 246.3239 | 6 | Burst to 8" - 3 svc | 19011.052 | 19011.052 | Pipe Burst or Replace | Replace
286 | 18 | B | SS.GM.T0000677 | SS.MH.T0011953 | SS.MH.T0005266 | 146.1425 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
287 | 18 | D | SS.GM.T0000678 | SS.MH.T0012306 | SS.MH.T0004317 | 463.5231 | 6 | Burst to 8" - 4 svc | 34129.003 | 34129.003 | Pipe Burst or Replace | Replace
288 | 18 | C | SS.GM.T0000679 | SS.MH.T0010847 | SS.MH.T0006329 | 322.7524 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
289 | 18 | B | SS.GM.T0000680 | SS.MH.T0012299 | SS.MH.T0004327 | 96.4677 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
290 | 18 | C | SS.GM.T0000682 | SS.MH.T0011941 | SS.MH.T0005999 | 218.2623 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
291 | 18 | D | SS.GM.T0000683 | SS.MH.T0012319 | SS.MH.T0004304 | 144.7359 | 6 | Point Repair at 107 ft from 04304 and Add to Root Removal Schedule | 5039.4717 | 5039.4717 | Point Repair and Add to Root Removal Program in CMOM | Repair
292 | 18 | D | SS.GM.T0000684 | SS.MH.T0012320 | SS.MH.T0004300 | 180.533 | 6 | Point Repair at 127 ft from 04300 | 4750 | 4750 | Point Repair | Repair
293 | 18 | D | SS.GM.T0000685 | SS.MH.T0012318 | SS.MH.T0004300 | 147.028 | 6 | Point Repair at 11 ft from 04300 | 4750 | 4750 | Point Repair | Repair
294 | 18 | C | SS.GM.T0000687 | SS.MH.T0011218 | SS.MH.T0005144 | 349.2423 | 6 | Point Repair at 284 ft from 05144 | 4750 | 0 | Monitor in CMOM | None
295 | 18 | D | SS.GM.T0000688 | SS.MH.T0011206 | SS.MH.T0005240 | 429.2313 | 6 | Point Repair at 49, 174 and 276 ft from 05240 | 14250 | 14250 | Point Repair | Repair
296 | 18 | D | SS.GM.T0000689 | SS.MH.T0010997 | SS.MH.T0005241 | 595.7888 | 6 | Burst to 8" - 4 svc | 42726.275 | 42726.275 | Pipe Burst or Replace | Replace
297 | 18 | D | SS.GM.T0000690 | SS.MH.T0011963 | SS.MH.T0005237 | 151.3225 | 6 | Point Repair at 63 ft from 05237 | 4750 | 4750 | Point Repair | Repair
298 | 18 | D | SS.GM.T0000691 | SS.MH.T0011964 | SS.MH.T0005224 | 360.1646 | 6 | Point Repair at 136 ft from 05224 and Add to Root Removal Schedule | 5470.3293 | 5470.3293 | Point Repair and Add to Root Removal Program in CMOM | Repair
299 | 18 | B | SS.GM.T0000692 | SS.MH.T0012344 | SS.MH.T0005223 | 145.4619 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
300 | 18 | D | SS.GM.T0000693 | SS.MH.T0012343 | SS.MH.T0005235 | 112.8237 | 6 | Point Repair at 23 and 112 ft from 05235 | 9500 | 9500 | Point Repair | Repair
301 | 18 | D | SS.GM.T0000694 | SS.MH.T0011959 | SS.MH.T0005236 | 244.5745 | 6 | Burst to 8" - 2 svc | 17897.3455 | 17897.3455 | Pipe Burst or Replace | Replace
302 | 18 | D | SS.GM.T0000695 | SS.MH.T0011213 | SS.MH.T0004329 | 213.1631 | 6 | Burst to 8" - 7 svc | 20855.5983 | 20855.5983 | Pipe Burst or Replace | Replace
303 | 18 | B | SS.GM.T0000696 | SS.MH.T0011111 | SS.MH.T0004331 | 51.2096 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
304 | 18 | D | SS.GM.T0000697 | SS.MH.T0010690 | SS.MH.T0004334 | 301.1655 | 6 | Point Repair at 58 ft from 04334 | 4750 | 4750 | Point Repair | Repair
305 | 18 | D | SS.GM.T0000698 | SS.MH.T0010689 | SS.MH.T0004331 | 617.594 | 6 | Point Repair at 237 ft from 04331 | 4750 | 4750 | Point Repair | Repair
306 | 18 | B | SS.GM.T0000699 | SS.MH.T0012336 | SS.MH.T0004328 | 406.7298 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
307 | 18 | C | SS.GM.T0000700 | SS.MH.T0011945 | SS.MH.T0004311 | 743.6837 | 6 | Point Repair at 90 ft from 04311 | 4750 | 0 | Monitor in CMOM | None
308 | 18 | D | SS.GM.T0000701 | SS.MH.T0010868 | SS.MH.T0005143 | 376.6786 | 6 | Point Repair at 48, 68, 123 and 254 ft from 05143 | 19000 | 19000 | Point Repair | Repair
309 | 18 | C | SS.GM.T0000702 | SS.MH.T0010694 | SS.MH.T0005143 | 233.3785 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
310 | 18 | C | SS.GM.T0000703 | SS.MH.T0015240 | SS.MH.T0005227 | 259.2084 | 6 | Point Repair at 8 and 22 ft from 15240 | 9500 | 0 | Monitor in CMOM | None
311 | 18 | D | SS.GM.T0000705 | SS.MH.T0006126 | SS.MH.T0013186 | 488.8097 | 6 | Point Repair at 21 ft from 06126 | 4750 | 4750 | Point Repair | Repair
312 | 18 | B | SS.GM.T0000706 | SS.MH.T0011971 | SS.MH.T0006126 | 566.6258 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
313 | 18 | B | SS.GM.T0000708 | SS.MH.T0015100 | SS.MH.T0014938 | 318.4283 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
314 | 18 | C | SS.GM.T0000709 | SS.MH.T0011747 | SS.MH.T0006373 | 354.3595 | 6 | Add to Root Removal Schedule | 708.719 | 0 | Add to Root Removal Program in CMOM | Maintenance
315 | 18 | D | SS.GM.T0000710 | SS.MH.T0006375 | SS.MH.T0006376 | 292.5669 | 6 | Point Repair at 99 and 139 ft from 06375 and 32 ft from 06376 Add to Root Removal Schedule | 14835.1337 | 14835.1337 | Point Repair and Add to Root Removal Program in CMOM | Repair
316 | 18 | D | SS.GM.T0000711 | SS.MH.T0010850 | SS.MH.T0006375 | 426.5562 | 6 | Point Repair at 286 and 318 ft from 06375 | 9500 | 9500 | Point Repair | Repair
317 | 18 | B | SS.GM.T0000712 | SS.MH.T0012310 | SS.MH.T0006375 | 155.7303 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
318 | 18 | D | SS.GM.T0000715 | SS.MH.T0012182 | SS.MH.T0006377 | 296.1481 | 6 | Point Repair at 63 ft from 06377 | 4750 | 4750 | Point Repair | Repair
319 | 18 | B | SS.GM.T0000716 | SS.MH.T0010707 | SS.MH.T0006123 | 552.2375 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
320 | 18 | B | SS.GM.T0000717 | SS.MH.T0005356 | SS.MH.T0015434 | 344.9103 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
321 | 18 | D | SS.GM.T0000718 | SS.MH.T0004343 | SS.MH.T0005356 | 574.5271 | 6 | Point Repair at 18, 217 and 476 ft from 05356 | 14250 | 14250 | Point Repair | Repair
322 | 18 | C | SS.GM.T0000719 | SS.MH.T0004346 | SS.MH.T0004344 | 150.7903 | 6 | Point Repair at 133 ft from 04346 | 4750 | 0 | Monitor in CMOM | None
323 | 18 | D | SS.GM.T0000720 | SS.MH.T0004337 | SS.MH.T0004346 | 752.2692 | 6 | Burst to 8" - 1 svc | 49897.4966 | 49897.4966 | Pipe Burst or Replace | Replace
324 | 18 | C | SS.GM.T0000721 | SS.MH.T0015194 | SS.MH.T0004337 | 408.1718 | 6 | Point Repair at 53 and 109 ft from 04337 and 8 ft from 15194 | 14250 | 0 | Monitor in CMOM | None
325 | 18 | C | SS.GM.T0000722 | SS.MH.T0004351 | SS.MH.T0004337 | 352.6876 | 6 | Point Repair at 211 ft from 04351 | 4750 | 0 | Monitor in CMOM | None
326 | 18 | C | SS.GM.T0000723 | SS.MH.T0011943 | SS.MH.T0004351 | 339.3905 | 6 | Burst to 8" - 2 svc | 24060.3847 | 0 | Monitor in CMOM | None
327 | 18 | B | SS.GM.T0000724 | SS.MH.T0004348 | SS.MH.T0004346 | 376.8399 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
328 | 18 | B | SS.GM.T0000725 | SS.MH.T0006982 | SS.MH.T0004348 | 251.9813 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
329 | 18 | B | SS.GM.T0000726 | SS.MH.T0011207 | SS.MH.T0006982 | 212.0778 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
330 | 18 | B | SS.GM.T0000727 | SS.MH.T0010542 | SS.MH.T0006982 | 136.8842 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
331 | 18 | B | SS.GM.T0000728 | SS.MH.T0012324 | SS.MH.T0004348 | 412.4425 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
332 | 18 | C | SS.GM.T0000729 | SS.MH.T0004350 | SS.MH.T0004349 | 732.8291 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
333 | 18 | B | SS.GM.T0000730 | SS.MH.T0004356 | SS.MH.T0004350 | 50.3797 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
334 | 18 | D | SS.GM.T0000731 | SS.MH.T0011936 | SS.MH.T0004356 | 208.9849 | 6 | Access; Clean and Inspection | 835.9396 | 835.9396 | Access; Clean and Inspection | Inspect
335 | 18 | E | SS.GM.T0000732 | SS.MH.T0004352 | SS.MH.T0004350 | 437.8917 | 6 | Point Repair at 87 and 228 ft from 04352 and Add to Root Removal Schedule | 9773.7684 | 9773.7684 | Point Repair and Add to Root Removal Program in CMOM | Repair
336 | 18 | B | SS.GM.T0000733 | SS.MH.T0011191 | SS.MH.T0004352 | 2.0001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
337 | 18 | C | SS.GM.T0000734 | SS.MH.T0011190 | SS.MH.T0004352 | 38.7964 | 6 | Point Repair at 20 ft from 04352 | 4750 | 0 | Monitor in CMOM | None
338 | 18 | D | SS.GM.T0000735 | SS.MH.T0004349 | SS.MH.T0004367 | 642.797 | 6 | Point Repair at 100, 120 and 226 ft from 04349 | 14250 | 14250 | Point Repair | Repair
339 | 18 | B | SS.GM.T0000736 | SS.MH.T0015050 | SS.MH.T0004361 | 78.5083 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
340 | 18 | B | SS.GM.T0000737 | SS.MH.T0010692 | SS.MH.T0013193 | 64.4299 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
341 | 18 | B | SS.GM.T0000738 | SS.MH.T0006386 | SS.MH.T0006387 | 42.1651 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
342 | 18 | B | SS.GM.T0000739 | SS.MH.T0006385 | SS.MH.T0006386 | 299.4137 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
343 | 18 | C | SS.GM.T0000740 | SS.MH.T0006798 | SS.MH.T0006387 | 425.4517 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
344 | 18 | B | SS.GM.T0000741 | SS.MH.T0011211 | SS.MH.T0004286 | 192.5396 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
345 | 18 | C | SS.GM.T0000742 | SS.MH.T0011961 | SS.MH.T0005152 | 320.6911 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
346 | 18 | C | SS.GM.T0000743 | SS.MH.T0011962 | SS.MH.T0005152 | 214.7053 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
347 | 18 | D | SS.GM.T0000744 | SS.MH.T0010989 | SS.MH.T0005154 | 149.6191 | 6 | Point Repair at 153 ft from 05154 | 4750 | 4750 | Point Repair | Repair
348 | 18 | C | SS.GM.T0000745 | SS.MH.T0011956 | SS.MH.T0005155 | 167.4395 | 6 | Point Repair at 160 ft from 05155 | 4750 | 0 | Monitor in CMOM | None
349 | 18 | D | SS.GM.T0000746 | SS.MH.T0011968 | SS.MH.T0005150 | 127.1171 | 6 | Point Repair at 50 and 96 ft from 05150 | 9500 | 9500 | Point Repair | Repair
350 | 18 | B | SS.GM.T0000747 | SS.MH.T0010703 | SS.MH.T0005149 | 170.0401 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
351 | 18 | D | SS.GM.T0000748 | SS.MH.T0010704 | SS.MH.T0005225 | 215.7472 | 6 | Point Repair at 106 ft from 05225 | 4750 | 4750 | Point Repair | Repair
352 | 18 | C | SS.GM.T0000749 | SS.MH.T0012350 | SS.MH.T0005234 | 226.3119 | 6 | Point Repair at 8 ft from 05234 | 4750 | 0 | Monitor in CMOM | None
353 | 18 | D | SS.GM.T0000750 | SS.MH.T0012190 | SS.MH.T0005234 | 204.2418 | 6 | Point Repair at 53 ft from 05234 | 4750 | 4750 | Point Repair | Repair
354 | 18 | D | SS.GM.T0000751 | SS.MH.T0010990 | SS.MH.T0005233 | 486.223 | 6 | Burst to 8" - 7 svc | 38604.4969 | 38604.4969 | Pipe Burst or Replace | Replace
355 | 18 | B | SS.GM.T0000828 | SS.MH.T0011978 | SS.MH.T0005174 | 510.7592 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
356 | 18 | D | SS.GM.T0000829 | SS.MH.T0011011 | SS.MH.T0003628 | 120.552 | 6 | Burst to 8" - 0 svc | 7835.8777 | 7835.8777 | Pipe Burst or Replace | Replace
357 | 18 | B | SS.GM.T0000830 | SS.MH.T0011227 | SS.MH.T0003625 | 30.7187 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
358 | 18 | B | SS.GM.T0000831 | SS.MH.T0012359 | SS.MH.T0003423 | 144.1669 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
359 | 18 | D | SS.GM.T0000832 | SS.MH.T0012358 | SS.MH.T0003625 | 60.7508 | 6 | Point Repair at 12358 | 4750 | 4750 | Point Repair | Repair
360 | 18 | B | SS.GM.T0000834 | SS.MH.T0012353 | SS.MH.T0003626 | 305.5645 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
361 | 18 | B | SS.GM.T0000985 | SS.MH.T0005188 | SS.MH.T0005190 | 111.8993 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
362 | 18 | A | SS.GM.T0000986 | SS.MH.T0005189 | SS.MH.T0005188 | 395.9602 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
363 | 18 | A | SS.GM.T0000987 | SS.MH.T0005187 | SS.MH.T0005189 | 399.2351 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
364 | 18 | B | SS.GM.T0000991 | SS.MH.T0005193 | SS.MH.T0003576 | 573.355 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
365 | 18 | A | SS.GM.T0000994 | SS.MH.T0003579 | SS.MH.T0003580 | 152.7028 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
366 | 18 | D | SS.GM.T0000999 | SS.MH.T0010243 | SS.MH.T0003580 | 388.218 | 8 | Burst to 10" - 1 svc | 30116.3527 | 30116.3527 | Pipe Burst or Replace | Replace
367 | 18 | D | SS.GM.T0001000 | SS.MH.T0010244 | SS.MH.T0010243 | 89.6539 | 8 | Burst to 10" - 0 svc | 6724.0409 | 6724.0409 | Pipe Burst or Replace | Replace
368 | 18 | D | SS.GM.T0001001 | SS.MH.T0003637 | SS.MH.T0010244 | 79.9127 | 8 | 8" CIPP - 0 svc | 3596.0735 | 3596.0735 | Cured In Place Pipe Liner | Rehab
369 | 18 | B | SS.GM.T0001002 | SS.MH.T0012904 | SS.MH.T0003637 | 72.7291 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
370 | 18 | B | SS.GM.T0001005 | SS.MH.T0004129 | SS.MH.T0012904 | 159.4226 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
371 | 18 | D | SS.GM.T0001048 | SS.MH.T0003502 | SS.MH.T0014957 | 590.0087 | 6 | Burst to 8" - 12 svc | 50350.5648 | 50350.5648 | Pipe Burst or Replace | Replace
372 | 18 | D | SS.GM.T0001049 | SS.MH.T0003441 | SS.MH.T0003442 | 807.8928 | 6 | Burst to 8" - 5 svc | 57513.03 | 57513.03 | Pipe Burst or Replace | Replace
373 | 18 | D | SS.GM.T0001050 | SS.MH.T0003440 | SS.MH.T0003441 | 352.4237 | 6 | Burst to 8" - 4 svc | 26907.5394 | 26907.5394 | Pipe Burst or Replace | Replace
374 | 18 | D | SS.GM.T0001051 | SS.MH.T0003439 | SS.MH.T0003440 | 292.9135 | 6 | Burst to 8" - 5 svc | 24039.3757 | 24039.3757 | Pipe Burst or Replace | Replace
375 | 18 | D | SS.GM.T0001052 | SS.MH.T0005575 | SS.MH.T0003439 | 400.6804 | 6 | Burst to 8" - 2 svc | 28044.2234 | 28044.2234 | Pipe Burst or Replace | Replace
376 | 18 | B | SS.GM.T0001053 | SS.MH.T0003444 | SS.MH.T0003445 | 142.0173 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
377 | 18 | D | SS.GM.T0001054 | SS.MH.T0000340 | SS.MH.T0003446 | 420.853 | 6 | Point Repair at 357 ft from 00340 | 4750 | 4750 | Point Repair | Repair
378 | 18 | D | SS.GM.T0001055 | SS.MH.T0003442 | SS.MH.T0003447 | 601.6527 | 6 | Burst to 8" - 2 svc | 41107.4231 | 41107.4231 | Pipe Burst or Replace | Replace
379 | 18 | D | SS.GM.T0001056 | SS.MH.T0009338 | SS.MH.T0003442 | 648.913 | 6 | Burst to 8" - 0 svc | 42179.3466 | 42179.3466 | Pipe Burst or Replace | Replace
380 | 18 | C | SS.GM.T0001057 | SS.MH.T0003451 | SS.MH.T0003445 | 359.2092 | 6 | Add to Root Removal Schedule | 718.4184 | 0 | Add to Root Removal Program in CMOM | Maintenance
381 | 18 | B | SS.GM.T0001058 | SS.MH.T0003443 | SS.MH.T0003444 | 92.0529 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
382 | 18 | B | SS.GM.T0001059 | SS.MH.T0004128 | SS.MH.T0003444 | 546.7332 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
383 | 18 | B | SS.GM.T0001060 | SS.MH.T0003454 | SS.MH.T0004128 | 98.374 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
384 | 18 | B | SS.GM.T0001061 | SS.MH.T0003455 | SS.MH.T0003454 | 171.6569 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
385 | 18 | B | SS.GM.T0001062 | SS.MH.T0003456 | SS.MH.T0003455 | 128.1832 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
386 | 18 | B | SS.GM.T0001063 | SS.MH.T0004124 | SS.MH.T0001665 | 96.9684 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
387 | 18 | B | SS.GM.T0001064 | SS.MH.T0004125 | SS.MH.T0004124 | 220.9208 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
388 | 18 | B | SS.GM.T0001065 | SS.MH.T0004126 | SS.MH.T0004125 | 97.7351 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
389 | 18 | B | SS.GM.T0001066 | SS.MH.T0000361 | SS.MH.T0004126 | 27.3732 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
390 | 18 | B | SS.GM.T0001068 | SS.MH.T0003447 | SS.MH.T0003448 | 264.6185 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
391 | 18 | B | SS.GM.T0001069 | SS.MH.T0003448 | SS.MH.T0003449 | 40.8767 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
392 | 18 | D | SS.GM.T0001071 | SS.MH.T0003504 | SS.MH.T0003503 | 256.1777 | 8 | Point Repair at 228 ft from 03504 | 4750 | 4750 | Point Repair | Repair
393 | 18 | B | SS.GM.T0001152 | SS.MH.T0005560 | SS.MH.T0005561 | 136.6185 | 21 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
394 | 18 | D | SS.GM.T0001153 | SS.MH.T0005305 | SS.MH.T0006216 | 343.7041 | 6 | Burst to 8" - 6 svc | 28340.7642 | 28340.7642 | Pipe Burst or Replace | Replace
395 | 18 | D | SS.GM.T0001154 | SS.MH.T0000300 | SS.MH.T0005305 | 575.4202 | 6 | Burst to 8" - 6 svc | 43402.3137 | 43402.3137 | Pipe Burst or Replace | Replace
396 | 18 | D | SS.GM.T0001155 | SS.MH.T0000299 | SS.MH.T0000300 | 316.5467 | 6 | Point Repair at 93 ft from 00299 | 4750 | 4750 | Point Repair | Repair
397 | 18 | B | SS.GM.T0001156 | SS.MH.T0005525 | SS.MH.T0000320 | 56.4133 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
398 | 18 | C | SS.GM.T0001200 | SS.MH.T0000285 | SS.MH.T0005578 | 356.6626 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
399 | 18 | B | SS.GM.T0001201 | SS.MH.T0005578 | SS.MH.T0000286 | 276.6199 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
400 | 18 | C | SS.GM.T0001202 | SS.MH.T0010705 | SS.MH.T0005578 | 83.4854 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
401 | 18 | B | SS.GM.T0001203 | SS.MH.T0011699 | SS.MH.T0006402 | 26.6052 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
402 | 18 | B | SS.GM.T0001204 | SS.MH.T0000286 | SS.MH.T0015105 | 104.4408 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
403 | 18 | D | SS.GM.T0001205 | SS.MH.T0006097 | SS.MH.T0000286 | 418.2852 | 8 | Point Repair at 302 ft and Grout Joint at 19 ft from 00286 | 5550 | 5550 | Point Repair & Grout Joint | Repair
404 | 18 | B | SS.GM.T0001206 | SS.MH.T0006099 | SS.MH.T0006097 | 171.3685 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
405 | 18 | B | SS.GM.T0001207 | SS.MH.T0010127 | SS.MH.T0006099 | 332.0548 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
406 | 18 | B | SS.GM.T0001208 | SS.MH.T0006091 | SS.MH.T0000285 | 90.6228 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
407 | 18 | B | SS.GM.T0001211 | SS.MH.T0012345 | SS.MH.T0006410 | 112.8545 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
408 | 18 | C | SS.GM.T0001212 | SS.MH.T0006410 | SS.MH.T0004175 | 212.3514 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
409 | 18 | B | SS.GM.T0001213 | SS.MH.T0004175 | SS.MH.T0006409 | 202.2869 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
410 | 18 | D | SS.GM.T0001214 | SS.MH.T0006409 | SS.MH.T0006408 | 290.3002 | 6 | Point Repair at 224, 266 and 290 ft from 06409 | 14250 | 14250 | Point Repair | Repair
411 | 18 | D | SS.GM.T0001215 | SS.MH.T0006408 | SS.MH.T0006407 | 437.9128 | 6 | Burst to 8" - 8 svc | 36464.329 | 36464.329 | Pipe Burst or Replace | Replace
412 | 18 | D | SS.GM.T0001216 | SS.MH.T0006407 | SS.MH.T0006104 | 301.5899 | 6 | Replace section 44 ft from 06407 to 222 ft from 06104. | 8400 | 8400 | Replace Section | Repair
413 | 18 | E | SS.GM.T0001217 | SS.MH.T0006104 | SS.MH.T0006105 | 218.8267 | 6 | Point Repair at 40 ft from 06105. Crossbore | 4750 | 4750 | Point Repair | Repair
414 | 18 | D | SS.GM.T0001219 | SS.MH.T0006105 | SS.MH.T0006106 | 100.3932 | 6 | Point Repair at 43 ft from 06105 | 4750 | 4750 | Point Repair | Repair
415 | 18 | D | SS.GM.T0001220 | SS.MH.T0006106 | SS.MH.T0006107 | 244.3824 | 6 | Replace section 20 to 70 ft from 06106. | 6000 | 6000 | Replace Section | Repair
416 | 18 | B | SS.GM.T0001221 | SS.MH.T0006107 | SS.MH.T0006108 | 228.6986 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
417 | 18 | B | SS.GM.T0001222 | SS.MH.T0006108 | SS.MH.T0006109 | 202.5092 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
418 | 18 | B | SS.GM.T0001224 | SS.MH.T0006110 | SS.MH.T0010988 | 357.6978 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
419 | 18 | B | SS.GM.T0001225 | SS.MH.T0006265 | SS.MH.T0011701 | 96.05 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
420 | 18 | D | SS.GM.T0001226 | SS.MH.T0006266 | SS.MH.T0006265 | 512.0593 | 18 | Point Repair at 49, 72, 96 and 213 ft from 06266 | 19000 | 19000 | Point Repair | Repair
421 | 18 | D | SS.GM.T0001227 | SS.MH.T0006267 | SS.MH.T0006266 | 471.9002 | 18 | 18" CIPP - 0 svc | 56628.025 | 56628.025 | Cured In Place Pipe Liner | Rehab
422 | 18 | D | SS.GM.T0001228 | SS.MH.T0006233 | SS.MH.T0006267 | 397.9151 | 18 | Point Repair at 5 ft from 06267 | 4750 | 4750 | Point Repair | Repair
423 | 18 | D | SS.GM.T0001229 | SS.MH.T0005265 | SS.MH.T0005264 | 430.1357 | 18 | Point Repair at 141 and 165 ft from 05265 | 9500 | 9500 | Point Repair | Repair
424 | 18 | B | SS.GM.T0001230 | SS.MH.T0005263 | SS.MH.T0005265 | 115.5943 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
425 | 18 | B | SS.GM.T0001231 | SS.MH.T0006131 | SS.MH.T0005263 | 542.3275 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
426 | 18 | B | SS.GM.T0001232 | SS.MH.T0013186 | SS.MH.T0006131 | 132.7392 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
427 | 18 | B | SS.GM.T0001233 | SS.MH.T0013190 | SS.MH.T0013187 | 218.0356 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
428 | 18 | B | SS.GM.T0001234 | SS.MH.T0013189 | SS.MH.T0013190 | 188.4533 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
429 | 18 | C | SS.GM.T0001235 | SS.MH.T0006101 | SS.MH.T0006981 | 267.7427 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
430 | 18 | C | SS.GM.T0001237 | SS.MH.T0004367 | SS.MH.T0006133 | 117.7298 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
431 | 18 | C | SS.GM.T0001238 | SS.MH.T0004368 | SS.MH.T0004367 | 47.1548 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
432 | 18 | D | SS.GM.T0001239 | SS.MH.T0004366 | SS.MH.T0015309 | 97.0002 | 8 | Point Repair at 80 ft from 04366 | 4750 | 4750 | Point Repair | Repair
433 | 18 | D | SS.GM.T0001240 | SS.MH.T0004365 | SS.MH.T0004366 | 125.6328 | 8 | Burst to 10" - 0 svc | 9422.458 | 9422.458 | Pipe Burst or Replace | Replace
434 | 18 | C | SS.GM.T0001241 | SS.MH.T0004364 | SS.MH.T0004365 | 54.5231 | 6 | Assign to high frequency cleaning - Grease | 163.5692 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
435 | 18 | C | SS.GM.T0001242 | SS.MH.T0004363 | SS.MH.T0004364 | 167.1271 | 6 | Assign to high frequency cleaning - Grease | 501.3812 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
436 | 18 | C | SS.GM.T0001243 | SS.MH.T0004362 | SS.MH.T0004363 | 58.6686 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
437 | 18 | D | SS.GM.T0001244 | SS.MH.T0004369 | SS.MH.T0015720 | 302.399 | 6 | Point Repair at 200 and 298 ft from 04369 | 9500 | 9500 | Point Repair | Repair
438 | 18 | C | SS.GM.T0001245 | SS.MH.T0004371 | SS.MH.T0004369 | 196.1057 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
439 | 18 | D | SS.GM.T0001246 | SS.MH.T0006384 | SS.MH.T0004371 | 402.218 | 6 | Burst to 8" - 0 svc | 26144.1678 | 26144.1678 | Pipe Burst or Replace | Replace
440 | 18 | B | SS.GM.T0001247 | SS.MH.T0006383 | SS.MH.T0006384 | 82.0026 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
441 | 18 | D | SS.GM.T0001248 | SS.MH.T0006382 | SS.MH.T0006383 | 229.0867 | 6 | Burst to 8" - 0 svc | 14890.6344 | 14890.6344 | Pipe Burst or Replace | Replace
442 | 18 | D | SS.GM.T0001249 | SS.MH.T0012333 | SS.MH.T0006381 | 554.6579 | 6 | Point Repair at 120 ft from 06381 and Add to Root Removal Schedule | 5859.3159 | 5859.3159 | Point Repair and Add to Root Removal Program in CMOM | Repair
443 | 18 | D | SS.GM.T0001250 | SS.MH.T0004370 | SS.MH.T0004369 | 111.9751 | 6 | Burst to 8" - 0 svc | 7278.382 | 7278.382 | Pipe Burst or Replace | Replace
444 | 18 | C | SS.GM.T0001251 | SS.MH.T0004172 | SS.MH.T0004370 | 382.6565 | 6 | Point Repair at 129 ft from 04172 | 4750 | 0 | Monitor in CMOM | None
445 | 18 | C | SS.GM.T0001252 | SS.MH.T0010700 | SS.MH.T0004172 | 416.4136 | 6 | Point Repair at 323 ft from 04172 | 4750 | 0 | Monitor in CMOM | None
446 | 18 | C | SS.GM.T0001260 | SS.MH.T0011969 | SS.MH.T0015112 | 250.1687 | 6 | Add to Root Removal Schedule | 500.3375 | 0 | Add to Root Removal Program in CMOM | Maintenance
447 | 18 | D | SS.GM.T0001261 | SS.MH.T0010699 | SS.MH.T0006135 | 264.8111 | 6 | Grout Joint at 211 and 227 ft from 06135 | 1600 | 1600 | Grout Joints | Repair
448 | 18 | A | SS.GM.T0001262 | SS.MH.T0010883 | SS.MH.T0005187 | 250.6964 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
449 | 18 | D | SS.GM.T0001266 | SS.MH.T0014315 | SS.MH.T0015768 | 354.7227 | 8 | Burst to 10" - 0 svc | 26604.1992 | 26604.1992 | Pipe Burst or Replace | Replace
450 | 18 | B | SS.GM.T0001280 | SS.MH.T0011014 | SS.MH.T0005575 | 54.5151 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
451 | 18 | D | SS.GM.T0001281 | SS.MH.T0011017 | SS.MH.T0003440 | 411.7654 | 6 | Burst to 8" - 3 svc | 29764.7491 | 29764.7491 | Pipe Burst or Replace | Replace
452 | 18 | D | SS.GM.T0001282 | SS.MH.T0012365 | SS.MH.T0003441 | 617.5323 | 6 | Burst to 8" - 1 svc | 41139.5971 | 41139.5971 | Pipe Burst or Replace | Replace
453 | 18 | B | SS.GM.T0001284 | SS.MH.T0011013 | SS.MH.T0000340 | 275.0875 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
454 | 18 | B | SS.GM.T0001285 | SS.MH.T0011021 | SS.MH.T0003451 | 314.6583 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
455 | 18 | B | SS.GM.T0001286 | SS.MH.T0001665 | SS.MH.T0003456 | 24.2323 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
456 | 18 | D | SS.GM.T0001287 | SS.MH.T0004161 | SS.MH.T0004127 | 101.6898 | 6 | Access; Clean and Inspection | 406.7591 | 406.7591 | Access; Clean and Inspection | Inspect
457 | 18 | D | SS.GM.T0001289 | SS.MH.T0011228 | SS.MH.T0000361 | 119.7339 | 6 | Point Repair at 3 ft from 00361 | 4750 | 4750 | Point Repair | Repair
458 | 18 | B | SS.GM.T0001290 | SS.MH.T0011232 | SS.MH.T0001665 | 251.0945 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
459 | 18 | B | SS.GM.T0001292 | SS.MH.T0012200 | SS.MH.T0003448 | 411.9306 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
460 | 18 | C | SS.GM.T0001293 | SS.MH.T0003449 | SS.MH.T0003504 | 423.9257 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
461 | 18 | D | SS.GM.T0001298 | SS.MH.T0011241 | SS.MH.T0003500 | 44.2065 | 6 | Point Repair at 33 ft from 03500 to remove blockage | 4750 | 4750 | Point Repair | Repair
462 | 18 | B | SS.GM.T0001322 | SS.MH.T0012378 | SS.MH.T0006143 | 335.5667 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
463 | 18 | D | SS.GM.T0001323 | SS.MH.T0012375 | SS.MH.T0006146 | 178.4477 | 6 | Point Repair at 46, 63 and 102 ft from 06146 | 14250 | 14250 | Point Repair | Repair
464 | 18 | B | SS.GM.T0001324 | SS.MH.T0011234 | SS.MH.T0006144 | 31.1711 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
465 | 18 | B | SS.GM.T0001325 | SS.MH.T0015093 | SS.MH.T0006253 | 442.2995 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
466 | 18 | D | SS.GM.T0001326 | SS.MH.T0000284 | SS.MH.T0006089 | 131.4784 | 6 | Burst to 8" - 0 svc | 8546.094 | 8546.094 | Pipe Burst or Replace | Replace
467 | 18 | D | SS.GM.T0001328 | SS.MH.T0006086 | SS.MH.T0006088 | 318.521 | 6 | Burst to 8" - 5 svc | 25703.8641 | 25703.8641 | Pipe Burst or Replace | Replace
468 | 18 | D | SS.GM.T0001329 | SS.MH.T0006085 | SS.MH.T0006086 | 346.957 | 6 | Point Repair at 203, 271 and 340 ft from 06085 | 14250 | 14250 | Point Repair | Repair
469 | 18 | D | SS.GM.T0001330 | SS.MH.T0000283 | SS.MH.T0006083 | 304.5807 | 6 | Point Repair at 155, 175 and 296 ft from 00283 | 14250 | 14250 | Point Repair | Repair
470 | 18 | D | SS.GM.T0001331 | SS.MH.T0006083 | SS.MH.T0006085 | 299.6218 | 6 | Burst to 8" - 5 svc | 24475.4171 | 24475.4171 | Pipe Burst or Replace | Replace
471 | 18 | B | SS.GM.T0001332 | SS.MH.T0010991 | SS.MH.T0000283 | 184.856 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
472 | 18 | D | SS.GM.T0001333 | SS.MH.T0011954 | SS.MH.T0000283 | 146.8205 | 6 | Point Repair at 69 and 154 ft from 00283 | 9500 | 9500 | Point Repair | Repair
473 | 18 | D | SS.GM.T0001334 | SS.MH.T0006084 | SS.MH.T0006083 | 148.3852 | 6 | Point Repair at 26 and 36 ft from 06083 | 9500 | 9500 | Point Repair | Repair
474 | 18 | D | SS.GM.T0001335 | SS.MH.T0012347 | SS.MH.T0006084 | 149.0586 | 6 | Construct Cleanout at End Of Line | 3000 | 3000 | Point Repair | Repair
475 | 18 | D | SS.GM.T0001336 | SS.MH.T0012196 | SS.MH.T0006085 | 193.6532 | 6 | Burst to 8" - 4 svc | 16587.4604 | 16587.4604 | Pipe Burst or Replace | Replace
476 | 18 | D | SS.GM.T0001337 | SS.MH.T0011955 | SS.MH.T0006086 | 667.1199 | 6 | Burst to 8" - 2 svc | 45362.7948 | 45362.7948 | Pipe Burst or Replace | Replace
477 | 18 | B | SS.GM.T0001338 | SS.MH.T0006087 | SS.MH.T0006088 | 67.1998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
478 | 18 | D | SS.GM.T0001339 | SS.MH.T0012355 | SS.MH.T0006087 | 656.6452 | 6 | Point Repair at 92 and 271 ft from 06087 | 9500 | 9500 | Point Repair | Repair
479 | 18 | B | SS.GM.T0001340 | SS.MH.T0005547 | SS.MH.T0005546 | 125.9227 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
480 | 18 | B | SS.GM.T0001341 | SS.MH.T0010871 | SS.MH.T0005547 | 287.846 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
481 | 18 | B | SS.GM.T0001342 | SS.MH.T0013470 | SS.MH.T0013469 | 55.4988 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
482 | 18 | B | SS.GM.T0001343 | SS.MH.T0006260 | SS.MH.T0006254 | 159.1529 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
483 | 18 | B | SS.GM.T0001344 | SS.MH.T0012374 | SS.MH.T0006259 | 84.3789 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
484 | 18 | B | SS.GM.T0001345 | SS.MH.T0012368 | SS.MH.T0000325 | 232.9762 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
485 | 18 | B | SS.GM.T0001346 | SS.MH.T0000325 | SS.MH.T0006260 | 159.0792 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
486 | 18 | C | SS.GM.T0001347 | SS.MH.T0006262 | SS.MH.T0000325 | 163.5778 | 6 | Grout Joint at 128 ft from 06262 | 800 | 0 | Monitor in CMOM | None
487 | 18 | D | SS.GM.T0001348 | SS.MH.T0006264 | SS.MH.T0006262 | 512.3367 | 6 | Point Repair at 484 and 489 ft from 06264 | 9500 | 9500 | Point Repair | Repair
488 | 18 | C | SS.GM.T0001349 | SS.MH.T0006263 | SS.MH.T0006262 | 307.3046 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
489 | 18 | D | SS.GM.T0001350 | SS.MH.T0011121 | SS.MH.T0006263 | 315.0413 | 6 | Construct Cleanout at End Of Line | 3000 | 3000 | Point Repair | Repair
490 | 18 | D | SS.GM.T0001351 | SS.MH.T0012370 | SS.MH.T0006263 | 348.4588 | 6 | Burst to 8" - 6 svc | 28649.8219 | 28649.8219 | Pipe Burst or Replace | Replace
491 | 18 | D | SS.GM.T0001352 | SS.MH.T0012199 | SS.MH.T0006264 | 353.2997 | 6 | Point Repair at 132 ft from 06264 | 4750 | 4750 | Point Repair | Repair
492 | 18 | B | SS.GM.T0001353 | SS.MH.T0010880 | SS.MH.T0006264 | 212.5188 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
493 | 18 | B | SS.GM.T0001354 | SS.MH.T0005545 | SS.MH.T0015440 | 227.14 | 12 | No Rehabilitation Recommended | 0 | 0 | Addressed in Capacity Remendiations | Model
494 | 18 | C | SS.GM.T0001355 | SS.MH.T0005543 | SS.MH.T0005545 | 354.7936 | 12 | Point Repair at 300 ft from 05543 | 4750 | 0 | Addressed in Capacity Remendiations | Model
495 | 18 | B | SS.GM.T0001356 | SS.MH.T0005540 | SS.MH.T0005543 | 337.288 | 12 | No Rehabilitation Recommended | 0 | 0 | Addressed in Capacity Remendiations | Model
496 | 18 | B | SS.GM.T0001357 | SS.MH.T0010873 | SS.MH.T0005543 | 501.4691 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
497 | 18 | B | SS.GM.T0001358 | SS.MH.T0012362 | SS.MH.T0000324 | 113.0227 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
498 | 18 | D | SS.GM.T0001359 | SS.MH.T0005577 | SS.MH.T0005535 | 944.3114 | 6 | Point Repair at 180, 657 and 893 ft from 05577 | 14250 | 14250 | Point Repair | Repair
499 | 18 | C | SS.GM.T0001360 | SS.MH.T0009367 | SS.MH.T0005577 | 426.0277 | 6 | Add to Root Removal Schedule | 852.0553 | 0 | Add to Root Removal Program in CMOM | Maintenance
500 | 18 | D | SS.GM.T0001361 | SS.MH.T0011122 | SS.MH.T0000300 | 66.1432 | 6 | Point Repair at 39 and 59 ft from 00300 | 9500 | 9500 | Point Repair | Repair
501 | 18 | D | SS.GM.T0001362 | SS.MH.T0011118 | SS.MH.T0000299 | 276.4539 | 6 | Burst to 8" - 4 svc | 21969.5054 | 21969.5054 | Pipe Burst or Replace | Replace
502 | 18 | C | SS.GM.T0001363 | SS.MH.T0012371 | SS.MH.T0000299 | 279.6853 | 6 | Add to Root Removal Schedule | 559.3706 | 0 | Add to Root Removal Program in CMOM | Maintenance
503 | 18 | D | SS.GM.T0001367 | SS.MH.T0005376 | SS.MH.T0005524 | 592.729 | 6 | Point Repair at 13, 175, 221, 269, 270 and 364 ft from 05376 and 25 ft from 05524 | 28500 | 28500 | Point Repair | Repair
504 | 18 | D | SS.GM.T0001369 | SS.MH.T0005379 | SS.MH.T0014964 | 424.0378 | 6 | Point Repair at 58 ft from 14964 | 4750 | 4750 | Point Repair | Repair
505 | 18 | B | SS.GM.T0001370 | SS.MH.T0010132 | SS.MH.T0005379 | 177.418 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
506 | 18 | B | SS.GM.T0001371 | SS.MH.T0000320 | SS.MH.T0005523 | 370.1574 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
507 | 18 | B | SS.GM.T0001372 | SS.MH.T0015482 | SS.MH.T0006974 | 287.2462 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
508 | 18 | C | SS.GM.T0001376 | SS.MH.T0006975 | SS.MH.T0007914 | 339.6687 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
509 | 18 | B | SS.GM.T0001377 | SS.MH.T0006971 | SS.MH.T0006975 | 395.0764 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
510 | 18 | B | SS.GM.T0001378 | SS.MH.T0006970 | SS.MH.T0006971 | 306.7393 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
511 | 18 | C | SS.GM.T0001379 | SS.MH.T0006969 | SS.MH.T0006970 | 322.4474 | 12 | Point Repair at 30 ft from 06969 | 4750 | 0 | Monitor in CMOM | None
512 | 18 | B | SS.GM.T0001380 | SS.MH.T0006968 | SS.MH.T0006969 | 321.734 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
513 | 18 | B | SS.GM.T0001412 | SS.MH.T0005594 | SS.MH.T0006210 | 200.2679 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
514 | 18 | D | SS.GM.T0001413 | SS.MH.T0005595 | SS.MH.T0005594 | 232.286 | 8 | Point Repair at 50 ft from 05595 | 4750 | 4750 | Point Repair | Repair
515 | 18 | B | SS.GM.T0001414 | SS.MH.T0010161 | SS.MH.T0005527 | 89.1834 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
516 | 18 | B | SS.GM.T0001415 | SS.MH.T0005527 | SS.MH.T0005528 | 161.3361 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
517 | 18 | C | SS.GM.T0001416 | SS.MH.T0005528 | SS.MH.T0005529 | 262.76 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
518 | 18 | B | SS.GM.T0001417 | SS.MH.T0005529 | SS.MH.T0005314 | 95.8581 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
519 | 18 | B | SS.GM.T0001418 | SS.MH.T0006214 | SS.MH.T0007919 | 161.2397 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
520 | 18 | C | SS.GM.T0001422 | SS.MH.T0005303 | SS.MH.T0005311 | 353.6498 | 6 | Point Repair at 225 ft from 05303 | 4750 | 0 | Monitor in CMOM | None
521 | 18 | B | SS.GM.T0001423 | SS.MH.T0005302 | SS.MH.T0005303 | 329.9354 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
522 | 18 | D | SS.GM.T0001424 | SS.MH.T0005301 | SS.MH.T0005302 | 612.2766 | 6 | Point Repair at 145, 270 and 337 ft from 05301 | 14250 | 14250 | Point Repair | Repair
523 | 18 | D | SS.GM.T0001425 | SS.MH.T0005304 | SS.MH.T0005303 | 485.7743 | 6 | Point Repair at 275 and 387 ft from 05304 | 9500 | 9500 | Point Repair | Repair
524 | 18 | D | SS.GM.T0001458 | SS.MH.T0004152 | SS.MH.T0000363 | 322.3217 | 6 | Grout Joint at 99 and 193 ft from 04152 | 1600 | 1600 | Grout Joints | Repair
525 | 18 | B | SS.GM.T0001462 | SS.MH.T0006155 | SS.MH.T0006153 | 404.0341 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
526 | 18 | B | SS.GM.T0001463 | SS.MH.T0006156 | SS.MH.T0006155 | 194.619 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
527 | 18 | C | SS.GM.T0001464 | SS.MH.T0006157 | SS.MH.T0006156 | 235.4126 | 6 | Point Repair at 236 ft from 06157 | 4750 | 0 | Monitor in CMOM | None
528 | 18 | C | SS.GM.T0001465 | SS.MH.T0010072 | SS.MH.T0006157 | 401.8337 | 6 | Point Repair at 98 ft from 06157 | 4750 | 0 | Monitor in CMOM | None
529 | 18 | B | SS.GM.T0001466 | SS.MH.T0000306 | SS.MH.T0006171 | 117.1678 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
530 | 18 | B | SS.GM.T0001467 | SS.MH.T0005435 | SS.MH.T0005433 | 183.6179 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
531 | 18 | B | SS.GM.T0001468 | SS.MH.T0000307 | SS.MH.T0005433 | 374.5435 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
532 | 18 | B | SS.GM.T0001469 | SS.MH.T0005433 | SS.MH.T0005434 | 40.8224 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
533 | 18 | D | SS.GM.T0001470 | SS.MH.T0005434 | SS.MH.T0006173 | 322.6411 | 10 | Point Repair at 307 ft from 06173 | 4750 | 4750 | Point Repair | Repair
534 | 18 | B | SS.GM.T0001471 | SS.MH.T0006173 | SS.MH.T0005437 | 188.3315 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
535 | 18 | D | SS.GM.T0001472 | SS.MH.T0005437 | SS.MH.T0005438 | 402.1002 | 10 | Point Repair at 90, 98, 283, 303 and 325 from 05438. | 23750 | 23750 | Point Repair | Repair
536 | 18 | C | SS.GM.T0001473 | SS.MH.T0005438 | SS.MH.T0005440 | 102.2281 | 10 | Point Repair at 32 ft from 05438 | 4750 | 0 | Monitor in CMOM | None
537 | 18 | B | SS.GM.T0001474 | SS.MH.T0005440 | SS.MH.T0007984 | 85 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
538 | 18 | D | SS.GM.T0001475 | SS.MH.T0005444 | SS.MH.T0005443 | 157.7616 | 8 | Point Repair at 210 ft from 05444 | 4750 | 4750 | Point Repair | Repair
539 | 18 | B | SS.GM.T0001476 | SS.MH.T0006422 | SS.MH.T0005444 | 124.0013 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
540 | 18 | D | SS.GM.T0001499 | SS.MH.T0005388 | SS.MH.T0005389 | 153.489 | 6 | Point Repair at 69 ft from 05398 and 20 ft from 05388 | 9500 | 9500 | Point Repair | Repair
541 | 18 | D | SS.GM.T0001572 | SS.MH.T0006080 | SS.MH.T0006184 | 501.4582 | 6 | Replace section 292 to 390 ft from 06184. | 11760 | 11760 | Replace Section | Repair
542 | 18 | C | SS.GM.T0001573 | SS.MH.T0006184 | SS.MH.T0006185 | 503.0614 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
543 | 18 | B | SS.GM.T0001574 | SS.MH.T0006185 | SS.MH.T0006186 | 10.9469 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
544 | 18 | D | SS.GM.T0001575 | SS.MH.T0006186 | SS.MH.T0006189 | 238.1468 | 12 | Replace section 166 ft from 06189 to 06186. | 10730 | 10730 | Replace Section | Repair
545 | 18 | D | SS.GM.T0001576 | SS.MH.T0006189 | SS.MH.T0006190 | 277.2496 | 12 | Point Repair at 144, 153 and 163 ft from 06189 | 14250 | 14250 | Point Repair | Repair
546 | 18 | C | SS.GM.T0001577 | SS.MH.T0006190 | SS.MH.T0006192 | 319.9999 | 12 | Add to Root Removal Schedule | 639.9998 | 0 | Add to Root Removal Program in CMOM | Maintenance
547 | 18 | D | SS.GM.T0001650 | SS.MH.T0009956 | SS.MH.T0006801 | 357.4063 | 6 | Point Repair at 13 and 91 ft from 06801 | 9500 | 9500 | Point Repair | Repair
548 | 18 | C | SS.GM.T0001651 | SS.MH.T0015727 | SS.MH.T0004353 | 170.9536 | 8 | Point Repair at 162 ft from 15727 | 4750 | 0 | Monitor in CMOM | None
549 | 18 | C | SS.GM.T0001652 | SS.MH.T0011256 | SS.MH.T0005525 | 310.1798 | 6 | Point Repair at 135 ft from 05525 | 4750 | 0 | Monitor in CMOM | None
550 | 18 | C | SS.GM.T0001653 | SS.MH.T0005539 | SS.MH.T0005540 | 148.5021 | 12 | Point Repair at 43 ft from 05539 | 4750 | 0 | Addressed in Capacity Remendiations | Model
551 | 18 | B | SS.GM.T0001654 | SS.MH.T0012369 | SS.MH.T0005535 | 155.0771 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
552 | 18 | D | SS.GM.T0001655 | SS.MH.T0005538 | SS.MH.T0015095 | 66.0194 | 12 | Point Repair at 5 and 25 ft from 15095 | 9500 | 9500 | Point Repair | Repair
553 | 18 | C | SS.GM.T0001657 | SS.MH.T0012361 | SS.MH.T0005537 | 174.0133 | 6 | Point Repair at 98 ft from 05537 | 4750 | 0 | Monitor in CMOM | None
554 | 18 | B | SS.GM.T0001659 | SS.MH.T0004178 | SS.MH.T0004179 | 407.2559 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
555 | 18 | D | SS.GM.T0001660 | SS.MH.T0004177 | SS.MH.T0004178 | 425.4342 | 6 | Point Repair at 271 ft and Grout Joint at 51, 82 and 146 ft from 04177 | 7150 | 7150 | Point Repair & Grout Joint | Repair
556 | 18 | B | SS.GM.T0001661 | SS.MH.T0009948 | SS.MH.T0004177 | 110.5131 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
557 | 18 | B | SS.GM.T0001662 | SS.MH.T0006950 | SS.MH.T0006949 | 301.6692 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
558 | 18 | B | SS.GM.T0001663 | SS.MH.T0004171 | SS.MH.T0006950 | 460.7815 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
559 | 18 | C | SS.GM.T0001664 | SS.MH.T0006963 | SS.MH.T0004171 | 319.2272 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
560 | 18 | B | SS.GM.T0001665 | SS.MH.T0010210 | SS.MH.T0006963 | 306.4611 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
561 | 18 | B | SS.GM.T0001666 | SS.MH.T0006949 | SS.MH.T0006948 | 153.2498 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
562 | 18 | B | SS.GM.T0001667 | SS.MH.T0006948 | SS.MH.T0004179 | 331.6034 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
563 | 18 | C | SS.GM.T0001668 | SS.MH.T0006959 | SS.MH.T0006949 | 432.6829 | 6 | Grout Joint at 376 ft from 06959 | 800 | 0 | Monitor in CMOM | None
564 | 18 | D | SS.GM.T0001669 | SS.MH.T0006239 | SS.MH.T0006960 | 551.3878 | 6 | Point Repair at 53 ft from 06239 | 4750 | 4750 | Point Repair | Repair
565 | 18 | B | SS.GM.T0001670 | SS.MH.T0009471 | SS.MH.T0006239 | 226.3006 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
566 | 18 | D | SS.GM.T0001671 | SS.MH.T0006961 | SS.MH.T0006960 | 303.3001 | 6 | Point Repair at 184 and 199 ft from 06961 | 9500 | 9500 | Point Repair | Repair
567 | 18 | C | SS.GM.T0001672 | SS.MH.T0006962 | SS.MH.T0006961 | 392.4199 | 6 | Point Repair at 385 ft from 06962 | 4750 | 0 | Monitor in CMOM | None
568 | 18 | C | SS.GM.T0001673 | SS.MH.T0010212 | SS.MH.T0006962 | 377.8136 | 6 | Point Repair at 169 ft from 06962 | 4750 | 0 | Monitor in CMOM | None
569 | 18 | C | SS.GM.T0001674 | SS.MH.T0006946 | SS.MH.T0004179 | 166.5606 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
570 | 18 | C | SS.GM.T0001675 | SS.MH.T0011224 | SS.MH.T0006946 | 200.2121 | 6 | Add to Root Removal Schedule | 400.4243 | 0 | Add to Root Removal Program in CMOM | Maintenance
571 | 18 | D | SS.GM.T0001676 | SS.MH.T0006945 | SS.MH.T0006946 | 720.7235 | 6 | Burst to 8" - 9 svc | 55847.0282 | 55847.0282 | Pipe Burst or Replace | Replace
572 | 18 | B | SS.GM.T0001677 | SS.MH.T0012352 | SS.MH.T0006945 | 139.8377 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
573 | 18 | B | SS.GM.T0001678 | SS.MH.T0012197 | SS.MH.T0005286 | 200.6278 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
574 | 18 | B | SS.GM.T0001679 | SS.MH.T0011973 | SS.MH.T0005291 | 239.5871 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
575 | 18 | D | SS.GM.T0001680 | SS.MH.T0011018 | SS.MH.T0005367 | 75.4327 | 6 | Point Repair at 15 ft from 05367 | 4750 | 4750 | Point Repair | Repair
576 | 18 | D | SS.GM.T0001681 | SS.MH.T0011022 | SS.MH.T0012863 | 112.4204 | 6 | Burst to 8" - 0 svc | 7307.3279 | 7307.3279 | Pipe Burst or Replace | Replace
577 | 18 | B | SS.GM.T0001682 | SS.MH.T0004180 | SS.MH.T0006231 | 40.4837 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
578 | 18 | B | SS.GM.T0001683 | SS.MH.T0011251 | SS.MH.T0006231 | 6.1939 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
579 | 18 | D | SS.GM.T0001684 | SS.MH.T0006230 | SS.MH.T0006229 | 151.3323 | 8 | Point Repair at 16 and 23 ft from 06229 | 9500 | 9500 | Point Repair | Repair
580 | 18 | B | SS.GM.T0001685 | SS.MH.T0006229 | SS.MH.T0006228 | 37.7 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
581 | 18 | B | SS.GM.T0001686 | SS.MH.T0006231 | SS.MH.T0006230 | 176.7173 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
582 | 18 | B | SS.GM.T0001687 | SS.MH.T0012868 | SS.MH.T0006232 | 32.0366 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
583 | 18 | D | SS.GM.T0001688 | SS.MH.T0012376 | SS.MH.T0006232 | 21.0117 | 6 | Point Repair at 5 ft from 06232 | 4750 | 4750 | Point Repair | Repair
584 | 18 | D | SS.GM.T0001689 | SS.MH.T0006232 | SS.MH.T0006231 | 242.6874 | 8 | Replace section 160 to 200 ft from 06232. | 5200 | 5200 | Replace Section | Repair
585 | 18 | B | SS.GM.T0001690 | SS.MH.T0006235 | SS.MH.T0006232 | 266.0298 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
586 | 18 | D | SS.GM.T0001691 | SS.MH.T0006236 | SS.MH.T0006235 | 332.1335 | 6 | Point Repair at 77 and 116 ft from 06236 | 9500 | 9500 | Point Repair | Repair
587 | 18 | C | SS.GM.T0001692 | SS.MH.T0010211 | SS.MH.T0006236 | 412.4481 | 6 | Point Repair at 189 ft from 06236 | 4750 | 0 | Monitor in CMOM | None
588 | 18 | B | SS.GM.T0001693 | SS.MH.T0010075 | SS.MH.T0006238 | 276.3359 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
589 | 18 | D | SS.GM.T0001694 | SS.MH.T0006238 | SS.MH.T0006237 | 393.2502 | 6 | Point Repair at 348 and 385 ft from 06238 | 9500 | 9500 | Point Repair | Repair
590 | 18 | D | SS.GM.T0001695 | SS.MH.T0006237 | SS.MH.T0015437 | 411.4505 | 6 | Point Repair at 161 and 257 ft from 06237 | 9500 | 9500 | Point Repair | Repair
591 | 18 | B | SS.GM.T0001696 | SS.MH.T0006365 | SS.MH.T0006366 | 266.4826 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
592 | 18 | B | SS.GM.T0001697 | SS.MH.T0006366 | SS.MH.T0006224 | 366.1562 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
593 | 18 | D | SS.GM.T0001701 | SS.MH.T0006228 | SS.MH.T0006977 | 464.0488 | 12 | Replace section 0 to 100 ft from 06228. | 14500 | 14500 | Replace Section | Repair
594 | 18 | C | SS.GM.T0001702 | SS.MH.T0006977 | SS.MH.T0013278 | 130.883 | 12 | Grout Joint at 38 ft from 06977 | 800 | 0 | Monitor in CMOM | None
595 | 18 | B | SS.GM.T0001714 | SS.MH.T0010544 | SS.MH.T0005301 | 576.1906 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
596 | 18 | D | SS.GM.T0001717 | SS.MH.T0011239 | SS.MH.T0005304 | 481.4771 | 6 | Point Repair at 70 ft from 05304 | 4750 | 4750 | Point Repair | Repair
597 | 18 | B | SS.GM.T0001727 | SS.MH.T0012392 | SS.MH.T0006174 | 96.5999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
598 | 18 | B | SS.GM.T0001728 | SS.MH.T0010721 | SS.MH.T0006170 | 42.981 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
599 | 18 | B | SS.GM.T0001729 | SS.MH.T0012396 | SS.MH.T0006171 | 18.5662 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
600 | 18 | B | SS.GM.T0001730 | SS.MH.T0015008 | SS.MH.T0000306 | 107.0321 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
601 | 18 | D | SS.GM.T0001735 | SS.MH.T0012393 | SS.MH.T0005389 | 465.1081 | 6 | Point Repair at 12 ft from 12393 and 232 ft from 05389 | 9500 | 9500 | Point Repair | Repair
602 | 18 | B | SS.GM.T0001746 | SS.MH.T0015851 | SS.MH.T0006361 | 317.3022 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
603 | 18 | D | SS.GM.T0001750 | SS.MH.T0006113 | SS.MH.T0000287 | 539.7058 | 6 | Point Repair at 261 and 504 ft from 06113 | 9500 | 9500 | Point Repair | Repair
604 | 18 | C | SS.GM.T0001751 | SS.MH.T0006114 | SS.MH.T0006113 | 104.6334 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
605 | 18 | C | SS.GM.T0001752 | SS.MH.T0000288 | SS.MH.T0006114 | 47.7614 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
606 | 18 | C | SS.GM.T0001753 | SS.MH.T0006115 | SS.MH.T0015722 | 183.9678 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
607 | 18 | B | SS.GM.T0001754 | SS.MH.T0000289 | SS.MH.T0006115 | 59.246 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
608 | 18 | C | SS.GM.T0001755 | SS.MH.T0006116 | SS.MH.T0000289 | 301.8727 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
609 | 18 | D | SS.GM.T0001756 | SS.MH.T0012356 | SS.MH.T0006115 | 275.2578 | 6 | Burst to 8" - 7 svc | 24891.7588 | 24891.7588 | Pipe Burst or Replace | Replace
610 | 18 | D | SS.GM.T0001757 | SS.MH.T0012357 | SS.MH.T0014965 | 173.7789 | 6 | Point Repair at 146 ft from 14965 | 4750 | 4750 | Point Repair | Repair
611 | 18 | D | SS.GM.T0001758 | SS.MH.T0011958 | SS.MH.T0006112 | 63.0002 | 6 | Burst to 8" - 0 svc | 4095.0106 | 4095.0106 | Pipe Burst or Replace | Replace
612 | 18 | D | SS.GM.T0001759 | SS.MH.T0011225 | SS.MH.T0006249 | 126.4998 | 6 | Point Repair at 88 and 101 ft from 06249 | 9500 | 9500 | Point Repair | Repair
613 | 18 | D | SS.GM.T0001760 | SS.MH.T0006111 | SS.MH.T0015578 | 379.0865 | 8 | Replace section 180 to 252 ft from 06111. | 9360 | 9360 | Replace Section | Repair
614 | 18 | C | SS.GM.T0001761 | SS.MH.T0004176 | SS.MH.T0006139 | 494.1301 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
615 | 18 | D | SS.GM.T0001762 | SS.MH.T0006139 | SS.MH.T0006118 | 320.076 | 8 | Point Repair at 7, 32, 142 and 175 ft from 06139 | 19000 | 19000 | Point Repair | Repair
616 | 18 | B | SS.GM.T0001763 | SS.MH.T0004170 | SS.MH.T0006118 | 206.0546 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
617 | 18 | B | SS.GM.T0001764 | SS.MH.T0013096 | SS.MH.T0004170 | 398.4713 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
618 | 18 | C | SS.GM.T0001765 | SS.MH.T0009584 | SS.MH.T0006139 | 681.1351 | 6 | Point Repair at 146 and 153 ft from 06139 | 9500 | 0 | Monitor in CMOM | None
619 | 18 | B | SS.GM.T0001770 | SS.MH.T0009615 | SS.MH.T0005278 | 183.7156 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
620 | 18 | C | SS.GM.T0001771 | SS.MH.T0005278 | SS.MH.T0005277 | 456.061 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
621 | 18 | B | SS.GM.T0001773 | SS.MH.T0006272 | SS.MH.T0006271 | 343.454 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
622 | 18 | D | SS.GM.T0001774 | SS.MH.T0006278 | SS.MH.T0006279 | 371.1081 | 6 | Point Repair at 178, 182 and 350 ft from 06279 | 14250 | 14250 | Point Repair | Repair
623 | 18 | B | SS.GM.T0001775 | SS.MH.T0006282 | SS.MH.T0006287 | 60.7857 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
624 | 18 | B | SS.GM.T0001776 | SS.MH.T0006986 | SS.MH.T0006987 | 257.3121 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
625 | 18 | B | SS.GM.T0001777 | SS.MH.T0012388 | SS.MH.T0006989 | 149.2308 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
626 | 18 | B | SS.GM.T0001778 | SS.MH.T0006991 | SS.MH.T0000327 | 297.0066 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
627 | 18 | B | SS.GM.T0001779 | SS.MH.T0006992 | SS.MH.T0006991 | 280.6579 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
628 | 18 | B | SS.GM.T0001780 | SS.MH.T0006990 | SS.MH.T0006992 | 240.9869 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
629 | 18 | C | SS.GM.T0001781 | SS.MH.T0012387 | SS.MH.T0006990 | 57.9664 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
630 | 18 | B | SS.GM.T0001782 | SS.MH.T0006988 | SS.MH.T0006990 | 258.2969 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
631 | 18 | D | SS.GM.T0001788 | SS.MH.T0000329 | SS.MH.T0007744 | 228.5176 | 10 | Point Repair at 73, 77 and 87 ft from 07744 | 19000 | 19000 | Point Repair | Repair
632 | 18 | B | SS.GM.T0002004 | SS.MH.T0009889 | SS.MH.T0006423 | 103.2114 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
633 | 18 | B | SS.GM.T0002006 | SS.MH.T0013652 | SS.MH.T0005610 | 276.7233 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
634 | 18 | B | SS.GM.T0002008 | SS.MH.T0005609 | SS.MH.T0005172 | 485.0101 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
635 | 18 | B | SS.GM.T0002024 | SS.MH.T0006328 | SS.MH.T0006330 | 36.3588 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
636 | 18 | D | SS.GM.T0002025 | SS.MH.T0005982 | SS.MH.T0004332 | 344.8335 | 6 | Point Repair at 5 ft from 05982 | 4750 | 4750 | Point Repair | Repair
637 | 18 | D | SS.GM.T0002026 | SS.MH.T0015152 | SS.MH.T0005609 | 285.1612 | 8 | Point Repair at 10 ft from 05609 and Access; Clean and Inspection | 5890.645 | 5890.645 | Point Repair and Access; Clean and Inspection | Repair
638 | 18 | D | SS.GM.T0002033 | SS.MH.T0006146 | SS.MH.T0001687 | 289.3101 | 6 | Point Repair at 68 ft from 01687 and Grout Joint at 19 ft from 06146 | 5550 | 5550 | Point Repair & Grout Joint | Repair
639 | 18 | C | SS.GM.T0002035 | SS.MH.T0001685 | SS.MH.T0005193 | 68.9779 | 6 | Point Repair at 27 ft from 01685 | 4750 | 0 | Monitor in CMOM | None
640 | 18 | D | SS.GM.T0002048 | SS.MH.T0003577 | SS.MH.T0004133 | 39.0228 | 8 | Burst to 10" - 0 svc | 2926.7109 | 2926.7109 | Pipe Burst or Replace | Replace
641 | 18 | B | SS.GM.T0002243 | SS.MH.T0009949 | SS.MH.T0004178 | 106.4176 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
642 | 18 | B | SS.GM.T0002244 | SS.MH.T0009947 | SS.MH.T0004177 | 162.7597 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
643 | 18 | C | SS.GM.T0002247 | SS.MH.T0006951 | SS.MH.T0005291 | 299.9569 | 8 | Grout Joint at 142, 151, 171, 181, 187, 198 and 264 ft from 05291 | 5600 | 0 | Monitor in CMOM | None
644 | 18 | B | SS.GM.T0002249 | SS.MH.T0009470 | SS.MH.T0004180 | 55.5268 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
645 | 18 | D | SS.GM.T0002253 | SS.MH.T0000692 | SS.MH.T0003439 | 288.0697 | 6 | Burst to 8" - 2 svc | 20724.5282 | 20724.5282 | Pipe Burst or Replace | Replace
646 | 18 | D | SS.GM.T0002419 | SS.MH.T0003629 | SS.MH.T0003628 | 157.9327 | 6 | Point Repair at 43 ft from 03629 | 4750 | 4750 | Point Repair | Repair
647 | 18 | D | SS.GM.T0002420 | SS.MH.T0003628 | SS.MH.T0005171 | 392.2822 | 6 | Point Repair at 97 ft from 03628 | 4750 | 4750 | Point Repair | Repair
648 | 18 | B | SS.GM.T0002436 | SS.MH.T0003576 | SS.MH.T0003632 | 18.7345 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
649 | 18 | D | SS.GM.T0002437 | SS.MH.T0003575 | SS.MH.T0003576 | 108.4469 | 8 | Burst to 8" - 0 svc | 7049.047 | 7049.047 | Pipe Burst or Replace | Replace
650 | 18 | D | SS.GM.T0002487 | SS.MH.T0003445 | SS.MH.T0015765 | 233.1963 | 6 | Point Repair at 46 ft from 03445 | 4750 | 4750 | Point Repair | Repair
651 | 18 | D | SS.GM.T0002488 | SS.MH.T0003446 | SS.MH.T0015763 | 394.7996 | 6 | Burst to 8" - 1 svc | 26661.9742 | 26661.9742 | Pipe Burst or Replace | Replace
652 | 18 | B | SS.GM.T0002498 | SS.MH.T0003423 | SS.MH.T0003422 | 82.0292 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
653 | 18 | D | SS.GM.T0002543 | SS.MH.T0004333 | SS.MH.T0005982 | 623.2267 | 6 | Point Repair at 27 and 224 ft and Grout Joint 449 from 04333 and Grout Joint at 92 and 167 ft from 05982 | 15850 | 15850 | Point Repair & Grout Joint | Repair
654 | 18 | B | SS.GM.T0002554 | SS.MH.T0004326 | SS.MH.T0000334 | 36.9486 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
655 | 18 | D | SS.GM.T0002556 | SS.MH.T0004313 | SS.MH.T0004314 | 117.1642 | 8 | Point Repair at 46, 86 and 104 ft from 04314 | 14250 | 14250 | Point Repair | Repair
656 | 18 | D | SS.GM.T0002557 | SS.MH.T0004310 | SS.MH.T0004305 | 238.8002 | 6 | Point Repair at 109, 112 and 219 ft from 04310 | 14250 | 14250 | Point Repair | Repair
657 | 18 | D | SS.GM.T0002558 | SS.MH.T0004309 | SS.MH.T0004307 | 322.0978 | 6 | Burst to 8" - 4 svc | 24936.3585 | 24936.3585 | Pipe Burst or Replace | Replace
658 | 18 | B | SS.GM.T0002559 | SS.MH.T0004300 | SS.MH.T0004301 | 199.0209 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
659 | 18 | D | SS.GM.T0002560 | SS.MH.T0004290 | SS.MH.T0004289 | 584.823 | 6 | Burst to 8" - 5 svc | 43013.4934 | 43013.4934 | Pipe Burst or Replace | Replace
660 | 18 | C | SS.GM.T0002561 | SS.MH.T0004249 | SS.MH.T0004289 | 596.1285 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
661 | 18 | D | SS.GM.T0002562 | SS.MH.T0004288 | SS.MH.T0004281 | 878.1234 | 6 | Point Repair at 33 ft from 04281 | 4750 | 4750 | Point Repair | Repair
662 | 18 | C | SS.GM.T0002563 | SS.MH.T0004284 | SS.MH.T0004285 | 352.7544 | 8 | Point Repair at 212 ft from 04284 | 4750 | 0 | Monitor in CMOM | None
663 | 18 | D | SS.GM.T0002564 | SS.MH.T0004283 | SS.MH.T0004284 | 325.1102 | 8 | Point Repair at 194 ft from 04283 and Add to Root Removal Schedule | 5400.2204 | 5400.2204 | Point Repair and Add to Root Removal Program in CMOM | Repair
664 | 18 | D | SS.GM.T0002565 | SS.MH.T0004251 | SS.MH.T0004280 | 402.921 | 6 | Point Repair at 137, 147 and 210 ft from 04280 | 14250 | 14250 | Point Repair | Repair
665 | 18 | D | SS.GM.T0002566 | SS.MH.T0004277 | SS.MH.T0004278 | 334.0815 | 6 | Point Repair at 14 & 16 and 271 ft from 04278 and 16 ft from 04277 | 19000 | 19000 | Point Repair | Repair
666 | 18 | D | SS.GM.T0002567 | SS.MH.T0004280 | SS.MH.T0004277 | 368.0723 | 6 | Point Repair at 61 ft from 04277 | 4750 | 4750 | Point Repair | Repair
667 | 18 | D | SS.GM.T0002570 | SS.MH.T0010167 | SS.MH.T0004267 | 895.4034 | 6 | Point Repair at 216, 226 and 240 ft from 04267 | 14250 | 14250 | Point Repair | Repair
668 | 18 | B | SS.GM.T0002617 | SS.MH.T0009322 | SS.MH.T0005378 | 277.3609 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
669 | 18 | C | SS.GM.T0002618 | SS.MH.T0005378 | SS.MH.T0005377 | 394.5566 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
670 | 18 | C | SS.GM.T0002619 | SS.MH.T0009323 | SS.MH.T0005375 | 118.1437 | 6 | Point Repair at 100 ft from 05375 | 4750 | 0 | Monitor in CMOM | None
671 | 18 | B | SS.GM.T0002620 | SS.MH.T0005375 | SS.MH.T0005374 | 300.8839 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
672 | 18 | D | SS.GM.T0002621 | SS.MH.T0005374 | SS.MH.T0005373 | 201.7994 | 6 | Point Repair at 58 ft from 05373 | 4750 | 4750 | Point Repair | Repair
673 | 18 | D | SS.GM.T0002622 | SS.MH.T0005373 | SS.MH.T0005372 | 395.1372 | 6 | Point Repair at 240, 280 and 313 ft from 05373 | 14250 | 14250 | Point Repair | Repair
674 | 18 | D | SS.GM.T0002623 | SS.MH.T0005371 | SS.MH.T0005372 | 590.0594 | 6 | Point Repair at 168 ft from 05371 | 4750 | 4750 | Point Repair | Repair
675 | 18 | C | SS.GM.T0002624 | SS.MH.T0005372 | SS.MH.T0006217 | 530.4268 | 6 | Point Repair at 357 ft from 05372 | 4750 | 0 | Monitor in CMOM | None
676 | 18 | D | SS.GM.T0002625 | SS.MH.T0009321 | SS.MH.T0006214 | 297.0986 | 6 | Point Repair at 48, 271, 281 and 290 ft from 06124 | 19000 | 19000 | Point Repair | Repair
677 | 18 | B | SS.GM.T0002626 | SS.MH.T0010162 | SS.MH.T0006213 | 125.2959 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
678 | 18 | B | SS.GM.T0002627 | SS.MH.T0006213 | SS.MH.T0006212 | 301.8387 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
679 | 18 | D | SS.GM.T0002628 | SS.MH.T0006212 | SS.MH.T0015027 | 304.867 | 6 | Grout Joint at 101 ft from 15027 | 800 | 800 | Grout Joints | Repair
680 | 18 | B | SS.GM.T0002629 | SS.MH.T0006210 | SS.MH.T0006209 | 81.7289 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
681 | 18 | C | SS.GM.T0002630 | SS.MH.T0006209 | SS.MH.T0005530 | 165.3568 | 8 | Add to Root Removal Schedule | 330.7136 | 0 | Add to Root Removal Program in CMOM | Maintenance
682 | 18 | B | SS.GM.T0002631 | SS.MH.T0010160 | SS.MH.T0005526 | 139.7032 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
683 | 18 | D | SS.GM.T0002632 | SS.MH.T0005523 | SS.MH.T0005524 | 311.2647 | 6 | Point Repair at 182 ft from 05523 | 4750 | 4750 | Point Repair | Repair
684 | 18 | D | SS.GM.T0002633 | SS.MH.T0005524 | SS.MH.T0005522 | 520.1665 | 6 | Replace section from 05522 to 20 ft from 05522 | 3440.3331 | 3440.3331 | Replace Section & Add to Root Removal Program in CMOM | Repair
685 | 18 | C | SS.GM.T0002642 | SS.MH.T0006187 | SS.MH.T0006185 | 325.8011 | 12 | Assign to high frequency cleaning | 977.4033 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
686 | 18 | B | SS.GM.T0002675 | SS.MH.T0004373 | SS.MH.T0004341 | 303.6908 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
687 | 18 | B | SS.GM.T0002676 | SS.MH.T0013193 | SS.MH.T0013194 | 264.1741 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
688 | 18 | B | SS.GM.T0002677 | SS.MH.T0004361 | SS.MH.T0004360 | 269.4771 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
689 | 18 | C | SS.GM.T0002678 | SS.MH.T0004360 | SS.MH.T0004359 | 248.1887 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
690 | 18 | B | SS.GM.T0002680 | SS.MH.T0010220 | SS.MH.T0004354 | 159.0195 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
691 | 18 | B | SS.GM.T0002681 | SS.MH.T0004358 | SS.MH.T0004349 | 53.8176 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
692 | 18 | D | SS.GM.T0002682 | SS.MH.T0004347 | SS.MH.T0004345 | 323.5798 | 6 | Point Repair at 18, 22 and 152 ft from 04345 | 14250 | 14250 | Point Repair | Repair
693 | 18 | D | SS.GM.T0002683 | SS.MH.T0004342 | SS.MH.T0005360 | 338.0319 | 6 | Burst to 8" - 3 svc | 24972.0743 | 24972.0743 | Pipe Burst or Replace | Replace
694 | 18 | E | SS.GM.T0002684 | SS.MH.T0000338 | SS.MH.T0004339 | 704.8913 | 6 | Point Repair of Crossbore at 85 ft from 00338 | 4750 | 4750 | Point Repair | Repair
695 | 18 | C | SS.GM.T0002685 | SS.MH.T0015193 | SS.MH.T0004347 | 476.6431 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
696 | 18 | D | SS.GM.T0002687 | SS.MH.T0006406 | SS.MH.T0006407 | 399.9959 | 6 | Point Repair at 361 ft from 06406 | 4750 | 4750 | Point Repair | Repair
697 | 18 | D | SS.GM.T0002688 | SS.MH.T0006405 | SS.MH.T0006406 | 258.1974 | 6 | Point Repair at 149 ft from 06405 | 4750 | 4750 | Point Repair | Repair
698 | 18 | B | SS.GM.T0002689 | SS.MH.T0006404 | SS.MH.T0006405 | 228.7855 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
699 | 18 | B | SS.GM.T0002690 | SS.MH.T0006402 | SS.MH.T0006363 | 129.7319 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
700 | 18 | B | SS.GM.T0002691 | SS.MH.T0006400 | SS.MH.T0006397 | 25.8332 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
701 | 18 | B | SS.GM.T0002693 | SS.MH.T0006396 | SS.MH.T0006402 | 142.1609 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
702 | 18 | C | SS.GM.T0002695 | SS.MH.T0006394 | SS.MH.T0006393 | 169.7589 | 6 | Add to Root Removal Schedule | 339.5179 | 0 | Add to Root Removal Program in CMOM | Maintenance
703 | 18 | C | SS.GM.T0002696 | SS.MH.T0006393 | SS.MH.T0006395 | 204.8545 | 6 | Add to Root Removal Schedule | 409.709 | 0 | Add to Root Removal Program in CMOM | Maintenance
704 | 18 | D | SS.GM.T0002697 | SS.MH.T0006392 | SS.MH.T0006391 | 847.1232 | 6 | Point Repair at 125, 303, 360 ft from 06392 and 38 ft from 06391 | 19000 | 19000 | Point Repair | Repair
705 | 18 | D | SS.GM.T0002698 | SS.MH.T0006390 | SS.MH.T0013211 | 271.4127 | 6 | Point Repair at 191 ft from 13211 | 4750 | 4750 | Point Repair | Repair
706 | 18 | D | SS.GM.T0002699 | SS.MH.T0006389 | SS.MH.T0006388 | 459.2614 | 6 | Point Repair at 235 ft from 06388 and 163 ft from 06389 | 9500 | 9500 | Point Repair | Repair
707 | 18 | B | SS.GM.T0002700 | SS.MH.T0013203 | SS.MH.T0013193 | 373.6528 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
708 | 18 | B | SS.GM.T0002701 | SS.MH.T0013195 | SS.MH.T0013196 | 65.3127 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
709 | 18 | D | SS.GM.T0002702 | SS.MH.T0006388 | SS.MH.T0006386 | 167.5458 | 6 | Replace section 139 ft from 06388 to 06386. | 3840 | 3840 | Replace Section | Repair
710 | 18 | D | SS.GM.T0002703 | SS.MH.T0006381 | SS.MH.T0006382 | 274.0254 | 6 | Replace section 120 to 350 ft from 06381. | 27600 | 27600 | Replace Section | Repair
711 | 18 | C | SS.GM.T0002704 | SS.MH.T0013137 | SS.MH.T0006398 | 1155.1968 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
712 | 18 | D | SS.GM.T0002710 | SS.MH.T0000337 | SS.MH.T0005589 | 88.8853 | 6 | Point Repair at 42 ft from 00337 | 4750 | 4750 | Point Repair | Repair
713 | 18 | B | SS.GM.T0002711 | SS.MH.T0005589 | SS.MH.T0005580 | 146.3214 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
714 | 18 | B | SS.GM.T0002713 | SS.MH.T0009365 | SS.MH.T0005370 | 196.4677 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
715 | 18 | B | SS.GM.T0002714 | SS.MH.T0005370 | SS.MH.T0005368 | 298.1552 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
716 | 18 | B | SS.GM.T0002715 | SS.MH.T0012863 | SS.MH.T0005367 | 353.2771 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
717 | 18 | B | SS.GM.T0002716 | SS.MH.T0005365 | SS.MH.T0005366 | 361.1792 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
718 | 18 | B | SS.GM.T0002717 | SS.MH.T0009364 | SS.MH.T0005365 | 109.5623 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
719 | 18 | C | SS.GM.T0002718 | SS.MH.T0006151 | SS.MH.T0005364 | 342.5391 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
720 | 18 | D | SS.GM.T0002719 | SS.MH.T0013973 | SS.MH.T0005358 | 321.0329 | 6 | Point Repair at 9 ft from 05358 | 4750 | 4750 | Point Repair | Repair
721 | 18 | B | SS.GM.T0002720 | SS.MH.T0000326 | SS.MH.T0006988 | 262.6902 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
722 | 18 | B | SS.GM.T0002721 | SS.MH.T0009361 | SS.MH.T0006987 | 148.1911 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
723 | 18 | B | SS.GM.T0002722 | SS.MH.T0009363 | SS.MH.T0006986 | 132.3382 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
724 | 18 | B | SS.GM.T0002723 | SS.MH.T0010083 | SS.MH.T0000326 | 260.7223 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
725 | 18 | B | SS.GM.T0002724 | SS.MH.T0006281 | SS.MH.T0006985 | 384.9454 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
726 | 18 | B | SS.GM.T0002725 | SS.MH.T0006983 | SS.MH.T0006291 | 395.8964 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
727 | 18 | B | SS.GM.T0002726 | SS.MH.T0006291 | SS.MH.T0006290 | 205.6817 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
728 | 18 | B | SS.GM.T0002727 | SS.MH.T0006290 | SS.MH.T0006978 | 492.4938 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
729 | 18 | C | SS.GM.T0002728 | SS.MH.T0010077 | SS.MH.T0006289 | 286.3492 | 6 | Add to Root Removal Schedule | 572.6984 | 0 | Add to Root Removal Program in CMOM | Maintenance
730 | 18 | B | SS.GM.T0002729 | SS.MH.T0010078 | SS.MH.T0006288 | 212.3773 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
731 | 18 | B | SS.GM.T0002730 | SS.MH.T0006283 | SS.MH.T0006284 | 181.1516 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
732 | 18 | C | SS.GM.T0002731 | SS.MH.T0010079 | SS.MH.T0006283 | 70.8192 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
733 | 18 | C | SS.GM.T0002733 | SS.MH.T0006273 | SS.MH.T0006280 | 210.1305 | 6 | Point Repair at 118 ft from 06273 | 4750 | 0 | Monitor in CMOM | None
734 | 18 | B | SS.GM.T0002734 | SS.MH.T0009477 | SS.MH.T0006277 | 89.0204 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
735 | 18 | B | SS.GM.T0002735 | SS.MH.T0006277 | SS.MH.T0006276 | 117.0305 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
736 | 18 | C | SS.GM.T0002736 | SS.MH.T0006276 | SS.MH.T0006275 | 348.9947 | 6 | Point Repair at 185 ft from 06275 | 4750 | 0 | Monitor in CMOM | None
737 | 18 | B | SS.GM.T0002737 | SS.MH.T0009475 | SS.MH.T0006273 | 188.2273 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
738 | 18 | B | SS.GM.T0002738 | SS.MH.T0009476 | SS.MH.T0006272 | 296.8065 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
739 | 18 | B | SS.GM.T0002751 | SS.MH.T0005445 | SS.MH.T0006170 | 251.3006 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
740 | 18 | B | SS.GM.T0002752 | SS.MH.T0005436 | SS.MH.T0005435 | 167.4499 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
741 | 18 | B | SS.GM.T0002753 | SS.MH.T0009890 | SS.MH.T0005435 | 222.3457 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
742 | 18 | B | SS.GM.T0002755 | SS.MH.T0009530 | SS.MH.T0006176 | 63.852 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
743 | 18 | B | SS.GM.T0002756 | SS.MH.T0009531 | SS.MH.T0006175 | 103.7 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
744 | 18 | D | SS.GM.T0002757 | SS.MH.T0006172 | SS.MH.T0006173 | 314.7701 | 6 | Point Repair at 78 ft from 06173 | 4750 | 4750 | Point Repair | Repair
745 | 18 | B | SS.GM.T0002758 | SS.MH.T0006175 | SS.MH.T0006172 | 38.6335 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
746 | 18 | C | SS.GM.T0002776 | SS.MH.T0005389 | SS.MH.T0005391 | 400.353 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
747 | 18 | D | SS.GM.T0002777 | SS.MH.T0005411 | SS.MH.T0005390 | 508.368 | 6 | Point Repair at 158 ft from 05390 | 4750 | 4750 | Point Repair | Repair
748 | 18 | C | SS.GM.T0002780 | SS.MH.T0005604 | SS.MH.T0000578 | 117.9036 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
749 | 18 | B | SS.GM.T0002795 | SS.MH.T0005314 | SS.MH.T0005313 | 69.9714 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
750 | 18 | D | SS.GM.T0002798 | SS.MH.T0009527 | SS.MH.T0000297 | 186.167 | 6 | Grout Joint at 150 ft from 00297 | 800 | 800 | Grout Joints | Repair
751 | 18 | B | SS.GM.T0002799 | SS.MH.T0009528 | SS.MH.T0006144 | 183.553 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
752 | 18 | B | SS.GM.T0002800 | SS.MH.T0006142 | SS.MH.T0006141 | 91.7727 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
753 | 18 | B | SS.GM.T0002801 | SS.MH.T0006141 | SS.MH.T0006140 | 68.3531 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
754 | 18 | C | SS.GM.T0002802 | SS.MH.T0006140 | SS.MH.T0000296 | 96.2692 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
755 | 18 | B | SS.GM.T0002880 | SS.MH.T0005244 | SS.MH.T0015715 | 204.4891 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
756 | 18 | D | SS.GM.T0002882 | SS.MH.T0005240 | SS.MH.T0000274 | 371.5913 | 6 | Point Repair at 166, 206 and 308 ft from 05240 | 14250 | 14250 | Point Repair | Repair
757 | 18 | D | SS.GM.T0002883 | SS.MH.T0000274 | SS.MH.T0005239 | 34.8233 | 6 | Burst to 8" - 0 svc | 2263.5163 | 2263.5163 | Pipe Burst or Replace | Replace
758 | 18 | D | SS.GM.T0002884 | SS.MH.T0005239 | SS.MH.T0005237 | 265.6886 | 6 | Burst to 8" - 0 svc | 17269.7564 | 17269.7564 | Pipe Burst or Replace | Replace
759 | 18 | D | SS.GM.T0002885 | SS.MH.T0005224 | SS.MH.T0005223 | 255.3485 | 6 | Point Repair at 16, 29 and 182 ft from 05224 | 14250 | 14250 | Point Repair | Repair
760 | 18 | C | SS.GM.T0002886 | SS.MH.T0005221 | SS.MH.T0005231 | 170.2962 | 8 | Point Repair at 74 and 102 ft and Grout Joint at 139 ft from 05221 | 10300 | 0 | Monitor in CMOM | None
761 | 18 | B | SS.GM.T0002888 | SS.MH.T0009303 | SS.MH.T0005216 | 204.1 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
762 | 18 | B | SS.GM.T0002889 | SS.MH.T0005216 | SS.MH.T0000273 | 83.8245 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
763 | 18 | C | SS.GM.T0002901 | SS.MH.T0005195 | SS.MH.T0001685 | 633.9725 | 6 | Assign to high frequency cleaning - Grease | 1901.9175 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
764 | 18 | B | SS.GM.T0002905 | SS.MH.T0000270 | SS.MH.T0005182 | 15.9093 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
765 | 18 | D | SS.GM.T0002908 | SS.MH.T0009302 | SS.MH.T0005178 | 108.4572 | 6 | Point Repair at 23 ft from 09302 | 4750 | 4750 | Point Repair | Repair
766 | 18 | B | SS.GM.T0002910 | SS.MH.T0005168 | SS.MH.T0005167 | 102.3847 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
767 | 18 | C | SS.GM.T0002912 | SS.MH.T0005165 | SS.MH.T0005164 | 531.5106 | 6 | Add to Root Removal Schedule | 1063.0212 | 0 | Add to Root Removal Program in CMOM | Maintenance
768 | 18 | C | SS.GM.T0002913 | SS.MH.T0005164 | SS.MH.T0005163 | 594.0608 | 6 | Point Repair at 245, 411 and 462 ft from 05164 | 14250 | 0 | Monitor in CMOM | None
769 | 18 | D | SS.GM.T0002920 | SS.MH.T0005146 | SS.MH.T0005221 | 1010.6186 | 8 | Replace section 450 to 580 ft from 05146. Point Repair at 90 and 121 ft from 05221 | 26400 | 26400 | Replace Section & Point Repair | Repair
770 | 18 | B | SS.GM.T0002921 | SS.MH.T0005145 | SS.MH.T0005144 | 64.5721 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
771 | 18 | D | SS.GM.T0002922 | SS.MH.T0000750 | SS.MH.T0005221 | 424.512 | 6 | Burst to 8" - 0 svc | 27593.2815 | 27593.2815 | Pipe Burst or Replace | Replace
772 | 18 | D | SS.GM.T0003026 | SS.MH.T0006261 | SS.MH.T0006260 | 741.1326 | 6 | Point Repair at 12, 69, 99 and 374 ft from 06261 | 19000 | 19000 | Point Repair | Repair
773 | 18 | B | SS.GM.T0003027 | SS.MH.T0009613 | SS.MH.T0006145 | 192.7152 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
774 | 18 | D | SS.GM.T0003028 | SS.MH.T0006258 | SS.MH.T0006257 | 324.9853 | 6 | Point Repair at 128 ft from 06257 | 4750 | 4750 | Point Repair | Repair
775 | 18 | B | SS.GM.T0003029 | SS.MH.T0006257 | SS.MH.T0006256 | 64.2765 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
776 | 18 | D | SS.GM.T0003030 | SS.MH.T0006256 | SS.MH.T0006255 | 194.6617 | 6 | Replace - 0 svc | 23359.4022 | 23359.4022 | Replace | Replace
777 | 18 | D | SS.GM.T0003031 | SS.MH.T0006255 | SS.MH.T0006254 | 35.9489 | 6 | Burst to 8" - 0 svc | 2336.678 | 2336.678 | Pipe Burst or Replace | Replace
778 | 18 | D | SS.GM.T0003032 | SS.MH.T0006254 | SS.MH.T0006251 | 95.5752 | 6 | Point Repair at 70 ft from 06254 | 4750 | 4750 | Point Repair | Repair
779 | 18 | D | SS.GM.T0003036 | SS.MH.T0013995 | SS.MH.T0005545 | 490.7916 | 6 | Point Repair at 297, 389, 412 and 452 ft from 13995 | 19000 | 19000 | Point Repair | Repair
780 | 18 | D | SS.GM.T0003037 | SS.MH.T0005542 | SS.MH.T0005543 | 639.1969 | 6 | Burst to 8" - 13 svc | 54547.7985 | 54547.7985 | Pipe Burst or Replace | Replace
781 | 18 | C | SS.GM.T0003038 | SS.MH.T0013284 | SS.MH.T0005539 | 470.2209 | 8 | Add to Root Removal Schedule | 940.4419 | 0 | Add to Root Removal Program in CMOM | Maintenance
782 | 18 | C | SS.GM.T0003039 | SS.MH.T0013949 | SS.MH.T0005540 | 706.4758 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
783 | 18 | B | SS.GM.T0003040 | SS.MH.T0013288 | SS.MH.T0013285 | 64.5149 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
784 | 18 | D | SS.GM.T0003041 | SS.MH.T0005535 | SS.MH.T0005536 | 304.9886 | 6 | Point Repair at 86, 144 and 165 ft from 05536 | 14250 | 14250 | Point Repair | Repair
785 | 18 | D | SS.GM.T0003042 | SS.MH.T0014477 | SS.MH.T0005535 | 503.6249 | 6 | Point Repair at 113, 150 and 186 ft from 05535 | 14250 | 14250 | Point Repair | Repair
786 | 18 | B | SS.GM.T0003044 | SS.MH.T0005532 | SS.MH.T0006234 | 290.715 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
787 | 18 | D | SS.GM.T0003045 | SS.MH.T0000322 | SS.MH.T0005532 | 34.8429 | 6 | Point Repair at 38 ft from 00322 | 4750 | 4750 | Point Repair | Repair
788 | 18 | D | SS.GM.T0003046 | SS.MH.T0005531 | SS.MH.T0006234 | 43.4839 | 6 | Point Repair at 29 ft from 05531 | 4750 | 4750 | Point Repair | Repair
789 | 18 | B | SS.GM.T0003047 | SS.MH.T0013308 | SS.MH.T0006233 | 57.701 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
790 | 18 | C | SS.GM.T0003048 | SS.MH.T0005264 | SS.MH.T0006233 | 164.0567 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
791 | 18 | D | SS.GM.T0003049 | SS.MH.T0006248 | SS.MH.T0006249 | 474.9362 | 6 | Point Repair at 352 ft from 06249 and Roor Removal Program | 5699.8725 | 5699.8725 | Point Repair and Add to Root Removal Program in CMOM | Repair
792 | 18 | D | SS.GM.T0003053 | SS.MH.T0006243 | SS.MH.T0006244 | 308.2855 | 8 | Replace section 70 to 130 ft from 06244. | 7800 | 7800 | Replace Section | Repair
793 | 18 | B | SS.GM.T0003055 | SS.MH.T0006240 | SS.MH.T0006235 | 286.1042 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
794 | 18 | B | SS.GM.T0003056 | SS.MH.T0010076 | SS.MH.T0006238 | 128.6706 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
795 | 18 | B | SS.GM.T0003058 | SS.MH.T0000321 | SS.MH.T0006225 | 90.7537 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
796 | 18 | B | SS.GM.T0003061 | SS.MH.T0010074 | SS.MH.T0006152 | 277.067 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
797 | 18 | C | SS.GM.T0003062 | SS.MH.T0010216 | SS.MH.T0006151 | 319.674 | 6 | Add to Root Removal Schedule | 639.3479 | 0 | Add to Root Removal Program in CMOM | Maintenance
798 | 18 | B | SS.GM.T0003063 | SS.MH.T0010217 | SS.MH.T0006965 | 124.2629 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
799 | 18 | D | SS.GM.T0003064 | SS.MH.T0006965 | SS.MH.T0006964 | 425.1749 | 6 | Point Repair at 149 ft from 06965 | 4750 | 4750 | Point Repair | Repair
800 | 18 | D | SS.GM.T0003065 | SS.MH.T0000292 | SS.MH.T0006957 | 473.2223 | 8 | Point Repair at 245 ft from 06957 and Add to Root Removal Schedule | 5696.4445 | 5696.4445 | Point Repair and Add to Root Removal Program in CMOM | Repair
801 | 18 | C | SS.GM.T0003066 | SS.MH.T0006957 | SS.MH.T0006956 | 354.0097 | 8 | Add to Root Removal Schedule | 708.0195 | 0 | Add to Root Removal Program in CMOM | Maintenance
802 | 18 | C | SS.GM.T0003067 | SS.MH.T0006955 | SS.MH.T0006954 | 313.5129 | 6 | Point Repair at 231 and 242 ft from 06954 | 9500 | 0 | Monitor in CMOM | None
803 | 18 | C | SS.GM.T0003068 | SS.MH.T0006953 | SS.MH.T0006952 | 388.8915 | 8 | Point Repair at 185 ft from 06953 | 4750 | 0 | Monitor in CMOM | None
804 | 18 | B | SS.GM.T0003069 | SS.MH.T0006956 | SS.MH.T0006951 | 427.802 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
805 | 18 | B | SS.GM.T0003070 | SS.MH.T0006952 | SS.MH.T0005290 | 312.4231 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
806 | 18 | D | SS.GM.T0003071 | SS.MH.T0005290 | SS.MH.T0005289 | 196.6339 | 8 | Point Repair at 173 ft from 05290 | 4750 | 4750 | Point Repair | Repair
807 | 18 | D | SS.GM.T0003072 | SS.MH.T0005289 | SS.MH.T0005288 | 397.9717 | 8 | Replace section 65 to 95 ft from 05288 and Point Repair at 142 and 157 ft from 05289 | 13400 | 13400 | Replace Section & Point Repair | Repair
808 | 18 | D | SS.GM.T0003073 | SS.MH.T0005285 | SS.MH.T0006984 | 403.33 | 8 | Point Repair at 104 and 131 ft from 05285 and 224, 253 and 274 from 06984. | 23750 | 23750 | Point Repair | Repair
809 | 18 | D | SS.GM.T0003074 | SS.MH.T0005281 | SS.MH.T0005282 | 498.1408 | 8 | Replace section 60 to 90 ft and Point Repair at 152, 176, 200, 230 and 263 ft from 05281 | 27650 | 27650 | Replace Section & Point Repair | Repair
810 | 18 | D | SS.GM.T0003075 | SS.MH.T0015204 | SS.MH.T0005281 | 430.9269 | 8 | Point Repair at 66 ft from 15204 | 4750 | 4750 | Point Repair | Repair
811 | 18 | B | SS.GM.T0003076 | SS.MH.T0015203 | SS.MH.T0005280 | 227.0531 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
812 | 18 | D | SS.GM.T0003077 | SS.MH.T0005276 | SS.MH.T0006271 | 45.1952 | 6 | Burst to 8" - 0 svc | 2937.6868 | 2937.6868 | Pipe Burst or Replace | Replace
813 | 18 | D | SS.GM.T0003082 | SS.MH.T0009585 | SS.MH.T0005271 | 35.3269 | 8 | Point Repair at 09585 | 4750 | 4750 | Point Repair | Repair
814 | 18 | B | SS.GM.T0003083 | SS.MH.T0005271 | SS.MH.T0005270 | 193.8008 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
815 | 18 | C | SS.GM.T0003084 | SS.MH.T0005270 | SS.MH.T0005268 | 410.8078 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
816 | 18 | C | SS.GM.T0003086 | SS.MH.T0005268 | SS.MH.T0005267 | 235.9193 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
817 | 18 | C | SS.GM.T0003087 | SS.MH.T0006129 | SS.MH.T0015434 | 363.1643 | 6 | Point Repair at 36 ft from 15434 | 4750 | 0 | Monitor in CMOM | None
818 | 18 | B | SS.GM.T0003088 | SS.MH.T0006123 | SS.MH.T0013198 | 123.6555 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
819 | 18 | B | SS.GM.T0003089 | SS.MH.T0006118 | SS.MH.T0006119 | 211.2247 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
820 | 18 | B | SS.GM.T0003092 | SS.MH.T0013497 | SS.MH.T0015110 | 203.9121 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
821 | 18 | B | SS.GM.T0003093 | SS.MH.T0006981 | SS.MH.T0006134 | 221.3507 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
822 | 18 | B | SS.GM.T0003094 | SS.MH.T0009511 | SS.MH.T0000291 | 46.4889 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
823 | 18 | D | SS.GM.T0003095 | SS.MH.T0006132 | SS.MH.T0000290 | 232.2515 | 6 | Point Repair at 102, 185, 194, 197 and 215 ft from 06132 | 23750 | 23750 | Point Repair | Repair
824 | 18 | D | SS.GM.T0003096 | SS.MH.T0000290 | SS.MH.T0006117 | 63.1573 | 6 | Point Repair at 65 ft from 06117 | 4750 | 4750 | Point Repair | Repair
825 | 18 | B | SS.GM.T0003097 | SS.MH.T0009512 | SS.MH.T0006117 | 47.4871 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
826 | 18 | C | SS.GM.T0003098 | SS.MH.T0012354 | SS.MH.T0006116 | 221.662 | 6 | Point Repair at 50, 58, 151 and 210 ft from 06116 | 19000 | 0 | Monitor in CMOM | None
827 | 18 | D | SS.GM.T0003099 | SS.MH.T0013181 | SS.MH.T0000287 | 678.5928 | 8 | 8" CIPP - 2 svc | 32536.6757 | 32536.6757 | Cured In Place Pipe Liner | Rehab
828 | 18 | C | SS.GM.T0003100 | SS.MH.T0010126 | SS.MH.T0006099 | 282.2459 | 6 | Assign to high frequency cleaning - Tubereculation | 846.7378 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
829 | 18 | D | SS.GM.T0003116 | SS.MH.T0012868 | SS.MH.T0004180 | 241.4956 | 6 | Point Repair at 62 and 84 ft from 04180 | 9500 | 9500 | Point Repair | Repair
830 | 18 | B | SS.GM.T0003117 | SS.MH.T0006288 | SS.MH.T0006283 | 214.9412 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
831 | 18 | B | SS.GM.T0003120 | SS.MH.T0005366 | SS.MH.T0012863 | 15.5646 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
832 | 18 | D | SS.GM.T0003138 | SS.MH.T0009612 | SS.MH.T0000725 | 132.0711 | 6 | Point Repair at 122 ft from 00725 | 4750 | 4750 | Point Repair | Repair
833 | 18 | C | SS.GM.T0003298 | SS.MH.T0009277 | SS.MH.T0003667 | 306.0967 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
834 | 18 | B | SS.GM.T0003310 | SS.MH.T0003632 | SS.MH.T0015710 | 142.8291 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
835 | 18 | C | SS.GM.T0003312 | SS.MH.T0003627 | SS.MH.T0003626 | 292.5508 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
836 | 18 | D | SS.GM.T0003313 | SS.MH.T0003626 | SS.MH.T0005170 | 593.1477 | 6 | Point Repair at 333 and 354 ft from 03626 | 9500 | 9500 | Point Repair | Repair
837 | 18 | D | SS.GM.T0003314 | SS.MH.T0003422 | SS.MH.T0003629 | 548.8495 | 6 | Point Repair at 95 and 373 ft and Grout Joint at 120 ft from 03422 | 10300 | 10300 | Point Repair & Grout Joint | Repair
838 | 18 | C | SS.GM.T0003326 | SS.MH.T0003573 | SS.MH.T0003575 | 240.8975 | 8 | Assign to high frequency cleaning - Grease | 722.6924 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
839 | 18 | D | SS.GM.T0003327 | SS.MH.T0015020 | SS.MH.T0003575 | 207.4379 | 8 | Point Repair at 17 ft from 15020 | 4750 | 4750 | Point Repair | Repair
840 | 18 | D | SS.GM.T0003358 | SS.MH.T0003453 | SS.MH.T0003446 | 250.0932 | 6 | Point Repair at 56, 88, 176 and 179 ft from 03446 | 19000 | 19000 | Point Repair | Repair
841 | 18 | D | SS.GM.T0003359 | SS.MH.T0003450 | SS.MH.T0003447 | 263.8089 | 6 | Burst to 8" - 1 svc | 18147.5809 | 18147.5809 | Pipe Burst or Replace | Replace
842 | 18 | A | SS.GM.T0003368 | SS.MH.T0003424 | SS.MH.T0003423 | 119.0347 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
843 | 18 | B | SS.GM.T0003404 | SS.MH.T0006327 | SS.MH.T0006328 | 131.99 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
844 | 18 | D | SS.GM.T0003405 | SS.MH.T0004293 | SS.MH.T0004312 | 420.8257 | 6 | Burst to 8" - 3 svc | 30353.6674 | 30353.6674 | Pipe Burst or Replace | Replace
845 | 18 | C | SS.GM.T0003406 | SS.MH.T0004294 | SS.MH.T0004293 | 187.4036 | 6 | Burst to 8" - 1 svc | 13181.2309 | 0 | Monitor in CMOM | None
846 | 18 | C | SS.GM.T0003407 | SS.MH.T0004295 | SS.MH.T0004294 | 463.5678 | 6 | Point Repair at 64 ft from 04294 | 4750 | 0 | Monitor in CMOM | None
847 | 18 | D | SS.GM.T0003408 | SS.MH.T0004282 | SS.MH.T0004283 | 285.9237 | 6 | Replace section 20 to 42 ft from 04283. | 2640 | 2640 | Replace Section | Repair
848 | 18 | D | SS.GM.T0003409 | SS.MH.T0004281 | SS.MH.T0004282 | 319.7838 | 6 | Point Repair at 124, 135, 193 and 208 ft from 04281 | 19000 | 19000 | Point Repair | Repair
849 | 18 | D | SS.GM.T0003410 | SS.MH.T0004274 | SS.MH.T0004281 | 353.4259 | 6 | Burst to 8" - 6 svc. Crossbore @ 96 & 320 ft from 04274 | 28972.6843 | 28972.6843 | Pipe Burst or Replace | Replace
850 | 18 | D | SS.GM.T0003411 | SS.MH.T0004287 | SS.MH.T0004283 | 527.7107 | 8 | Point Repair at 483 ft from 04287 and Add to Root Removal Schedule | 5805.4214 | 5805.4214 | Point Repair and Add to Root Removal Program in CMOM | Repair
851 | 18 | C | SS.GM.T0003412 | SS.MH.T0004278 | SS.MH.T0004287 | 514.6678 | 8 | Point Repair at 515 ft from 04278 | 4750 | 0 | Monitor in CMOM | None
852 | 18 | B | SS.GM.T0003414 | SS.MH.T0009547 | SS.MH.T0004267 | 897.2547 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
853 | 18 | C | SS.GM.T0003415 | SS.MH.T0004267 | SS.MH.T0004266 | 255.3489 | 6 | Add to Root Removal Schedule | 510.6978 | 0 | Add to Root Removal Program in CMOM | Maintenance
854 | 18 | C | SS.GM.T0003420 | SS.MH.T0004248 | SS.MH.T0004249 | 324.6665 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
855 | 18 | C | SS.GM.T0003445 | SS.MH.T0006217 | SS.MH.T0006216 | 344.5081 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
856 | 18 | C | SS.GM.T0003446 | SS.MH.T0006216 | SS.MH.T0005522 | 220.6089 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
857 | 18 | D | SS.GM.T0003448 | SS.MH.T0010163 | SS.MH.T0006214 | 295.3129 | 6 | Point Repair at 41, 179, 109 and 287 ft from 06214 | 19000 | 19000 | Point Repair | Repair
858 | 18 | D | SS.GM.T0003449 | SS.MH.T0005526 | SS.MH.T0006210 | 281.7043 | 6 | Point Repair at 2 ft from 05526 | 4750 | 4750 | Point Repair | Repair
859 | 18 | C | SS.GM.T0003450 | SS.MH.T0005530 | SS.MH.T0005529 | 341.6 | 8 | Add to Root Removal Schedule | 683.2 | 0 | Add to Root Removal Program in CMOM | Maintenance
860 | 18 | B | SS.GM.T0003451 | SS.MH.T0005522 | SS.MH.T0005527 | 194.4858 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
861 | 18 | B | SS.GM.T0003452 | SS.MH.T0005377 | SS.MH.T0005523 | 419.1666 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
862 | 18 | C | SS.GM.T0003453 | SS.MH.T0005300 | SS.MH.T0005522 | 392.1149 | 6 | Add to Root Removal Schedule | 784.2298 | 0 | Add to Root Removal Program in CMOM | Maintenance
863 | 18 | B | SS.GM.T0003534 | SS.MH.T0011019 | SS.MH.T0003446 | 21.7866 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
864 | 18 | C | SS.GM.T0003535 | SS.MH.T0011229 | SS.MH.T0000692 | 98.7338 | 6 | Point Repair at 95 ft from 00692 | 4750 | 0 | Monitor in CMOM | None
865 | 18 | D | SS.GM.T0003537 | SS.MH.T0011231 | SS.MH.T0005575 | 456.0842 | 6 | Burst to 8" - 8 svc | 37645.4711 | 37645.4711 | Pipe Burst or Replace | Replace
866 | 18 | B | SS.GM.T0003551 | SS.MH.T0010867 | SS.MH.T0004373 | 737.3182 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
867 | 18 | D | SS.GM.T0003554 | SS.MH.T0004357 | SS.MH.T0004358 | 327.9129 | 6 | Point Repair at 50 ft from 04358 and Add to Root Removal Schedule | 5405.8258 | 5405.8258 | Point Repair and Add to Root Removal Program in CMOM | Repair
868 | 18 | D | SS.GM.T0003555 | SS.MH.T0004354 | SS.MH.T0013193 | 216.5256 | 6 | Point Repair at 104 ft from 04354 | 4750 | 4750 | Point Repair | Repair
869 | 18 | B | SS.GM.T0003556 | SS.MH.T0013196 | SS.MH.T0013203 | 152.4304 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
870 | 18 | D | SS.GM.T0003557 | SS.MH.T0004359 | SS.MH.T0004368 | 427.9334 | 8 | Burst to 10" - 0 svc | 32095.0044 | 32095.0044 | Pipe Burst or Replace | Replace
871 | 18 | B | SS.GM.T0003558 | SS.MH.T0012341 | SS.MH.T0004349 | 253.0429 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
872 | 18 | C | SS.GM.T0003559 | SS.MH.T0006378 | SS.MH.T0015193 | 516.8843 | 6 | Add to Root Removal Schedule | 1033.7686 | 0 | Add to Root Removal Program in CMOM | Maintenance
873 | 18 | C | SS.GM.T0003560 | SS.MH.T0012329 | SS.MH.T0004343 | 723.6192 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
874 | 18 | D | SS.GM.T0003561 | SS.MH.T0011217 | SS.MH.T0005361 | 229.517 | 6 | Burst to 8" - 3 svc | 17918.6072 | 17918.6072 | Pipe Burst or Replace | Replace
875 | 18 | C | SS.GM.T0003562 | SS.MH.T0004339 | SS.MH.T0004342 | 298.6107 | 6 | Point Repair at 50 ft from 04232 and 227 ft from 04339 | 9500 | 0 | Monitor in CMOM | None
876 | 18 | D | SS.GM.T0003563 | SS.MH.T0012326 | SS.MH.T0000338 | 362.2548 | 6 | Point Repair at 145 ft from 00338 | 4750 | 4750 | Point Repair | Repair
877 | 18 | C | SS.GM.T0003564 | SS.MH.T0004335 | SS.MH.T0004338 | 504.8072 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
878 | 18 | C | SS.GM.T0003565 | SS.MH.T0006398 | SS.MH.T0006399 | 248.328 | 6 | Add to Root Removal Schedule | 496.656 | 0 | Add to Root Removal Program in CMOM | Maintenance
879 | 18 | B | SS.GM.T0003573 | SS.MH.T0012340 | SS.MH.T0004372 | 192.3647 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
880 | 18 | C | SS.GM.T0003574 | SS.MH.T0009954 | SS.MH.T0006391 | 387.5931 | 6 | Point Repair at 14 ft from 09954 | 4750 | 0 | Monitor in CMOM | None
881 | 18 | B | SS.GM.T0003575 | SS.MH.T0006403 | SS.MH.T0006404 | 135.2232 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
882 | 18 | C | SS.GM.T0003576 | SS.MH.T0011112 | SS.MH.T0006403 | 493.9176 | 6 | Grout Joint at 30 ft from 06403 | 800 | 0 | Monitor in CMOM | None
883 | 18 | B | SS.GM.T0003577 | SS.MH.T0015103 | SS.MH.T0006400 | 167.6025 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
884 | 18 | D | SS.GM.T0003578 | SS.MH.T0011215 | SS.MH.T0006394 | 182.9219 | 6 | Point Repair at 11215 | 4750 | 4750 | Point Repair | Repair
885 | 18 | B | SS.GM.T0003579 | SS.MH.T0006391 | SS.MH.T0006381 | 322.7572 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
886 | 18 | B | SS.GM.T0003580 | SS.MH.T0010865 | SS.MH.T0014431 | 425.3332 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
887 | 18 | B | SS.GM.T0003581 | SS.MH.T0004353 | SS.MH.T0013195 | 160.601 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
888 | 18 | D | SS.GM.T0003583 | SS.MH.T0009953 | SS.MH.T0006390 | 236.8812 | 6 | Burst to 8" - 0 svc | 15397.2791 | 15397.2791 | Pipe Burst or Replace | Replace
889 | 18 | D | SS.GM.T0003584 | SS.MH.T0006377 | SS.MH.T0006378 | 384.5263 | 6 | Burst to 8" - 0 svc | 24994.2115 | 24994.2115 | Pipe Burst or Replace | Replace
890 | 18 | D | SS.GM.T0003585 | SS.MH.T0006376 | SS.MH.T0006377 | 331.3335 | 6 | Point Repair at 102 and 257 ft from 06376 and Add to Root Removal Schedule | 10162.6669 | 10162.6669 | Point Repair and Add to Root Removal Program in CMOM | Repair
891 | 18 | B | SS.GM.T0003586 | SS.MH.T0006373 | SS.MH.T0006376 | 551.1035 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
892 | 18 | B | SS.GM.T0003587 | SS.MH.T0006374 | SS.MH.T0006373 | 53.6691 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
893 | 18 | C | SS.GM.T0003588 | SS.MH.T0010863 | SS.MH.T0006336 | 750.1146 | 6 | Point Repair at 115, 167, 180 and 250 ft from 06336 | 19000 | 0 | Monitor in CMOM | None
894 | 18 | D | SS.GM.T0003592 | SS.MH.T0012180 | SS.MH.T0004309 | 431.9029 | 6 | Point Repair at 9, 16, 44 and 52 ft from 04309 | 19000 | 19000 | Point Repair | Repair
895 | 18 | D | SS.GM.T0003593 | SS.MH.T0012328 | SS.MH.T0004310 | 324.3882 | 6 | Point Repair at 47 ft from 04310 | 4750 | 4750 | Point Repair | Repair
896 | 18 | D | SS.GM.T0003594 | SS.MH.T0011187 | SS.MH.T0004313 | 620.1447 | 6 | Burst to 8" - 8 svc | 48309.408 | 48309.408 | Pipe Burst or Replace | Replace
897 | 18 | B | SS.GM.T0003595 | SS.MH.T0012302 | SS.MH.T0002531 | 78.3644 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
898 | 18 | D | SS.GM.T0003596 | SS.MH.T0011519 | SS.MH.T0004290 | 519.7516 | 6 | Burst to 8" - 3 svc | 36783.8566 | 36783.8566 | Pipe Burst or Replace | Replace
899 | 18 | C | SS.GM.T0003597 | SS.MH.T0011209 | SS.MH.T0004284 | 365.2969 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
900 | 18 | C | SS.GM.T0003599 | SS.MH.T0010853 | SS.MH.T0013992 | 699.4242 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
901 | 18 | D | SS.GM.T0003600 | SS.MH.T0012303 | SS.MH.T0014988 | 419.2039 | 6 | Point Repair at 95 ft from 14988 | 4750 | 4750 | Point Repair | Repair
902 | 18 | D | SS.GM.T0003604 | SS.MH.T0011198 | SS.MH.T0000274 | 559.5547 | 6 | Point Repair at 74 ft from 00274 | 4750 | 4750 | Point Repair | Repair
903 | 18 | B | SS.GM.T0003606 | SS.MH.T0009946 | SS.MH.T0005579 | 92 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
904 | 18 | D | SS.GM.T0003607 | SS.MH.T0006117 | SS.MH.T0015721 | 219.6152 | 6 | Point Repair at 25 ft from 06117 | 4750 | 4750 | Point Repair | Repair
905 | 18 | C | SS.GM.T0003608 | SS.MH.T0005579 | SS.MH.T0005581 | 104.9595 | 8 | Assign to high frequency cleaning - Grease | 314.8786 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
906 | 18 | B | SS.GM.T0003609 | SS.MH.T0006363 | SS.MH.T0006091 | 138.3248 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
907 | 18 | C | SS.GM.T0003610 | SS.MH.T0011120 | SS.MH.T0006216 | 997.0084 | 6 | Grout Joint at 31, 35 and 95 ft from 06216 | 2400 | 0 | Monitor in CMOM | None
908 | 18 | B | SS.GM.T0003611 | SS.MH.T0011117 | SS.MH.T0005371 | 65.6165 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
909 | 18 | B | SS.GM.T0003612 | SS.MH.T0005368 | SS.MH.T0014989 | 229.1287 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
910 | 18 | B | SS.GM.T0003613 | SS.MH.T0005369 | SS.MH.T0005283 | 221.7998 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
911 | 18 | C | SS.GM.T0003614 | SS.MH.T0005283 | SS.MH.T0006365 | 170.3375 | 10 | Add to Root Removal Schedule | 340.675 | 0 | Add to Root Removal Program in CMOM | Maintenance
912 | 18 | C | SS.GM.T0003615 | SS.MH.T0012185 | SS.MH.T0005360 | 205.7738 | 6 | Add to Root Removal Schedule | 411.5475 | 0 | Add to Root Removal Program in CMOM | Maintenance
913 | 18 | D | SS.GM.T0003616 | SS.MH.T0005360 | SS.MH.T0006364 | 323.8401 | 6 | Point Repair at 80, 243, 261 and 286 ft from 05360 | 19000 | 19000 | Point Repair | Repair
914 | 18 | C | SS.GM.T0003618 | SS.MH.T0015113 | SS.MH.T0015479 | 149.2501 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
915 | 18 | B | SS.GM.T0003619 | SS.MH.T0013509 | SS.MH.T0006121 | 237.7133 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
916 | 18 | D | SS.GM.T0003621 | SS.MH.T0011203 | SS.MH.T0006364 | 484.3835 | 6 | Point Repair at 223, 309 and 316 ft from 06364 | 14250 | 14250 | Point Repair | Repair
917 | 18 | D | SS.GM.T0003622 | SS.MH.T0005363 | SS.MH.T0015646 | 487.7117 | 6 | Point Repair at 32 ft and Grout Joint at 19 ft from 15646 | 5550 | 5550 | Point Repair & Grout Joint | Repair
918 | 18 | B | SS.GM.T0003623 | SS.MH.T0005266 | SS.MH.T0006127 | 717.6932 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
919 | 18 | B | SS.GM.T0003625 | SS.MH.T0007586 | SS.MH.T0006187 | 12.1855 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
920 | 18 | B | SS.GM.T0003626 | SS.MH.T0006987 | SS.MH.T0006989 | 263.1981 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
921 | 18 | B | SS.GM.T0003627 | SS.MH.T0006989 | SS.MH.T0000327 | 237.7544 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
922 | 18 | B | SS.GM.T0003729 | SS.MH.T0009888 | SS.MH.T0005436 | 238.4561 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
923 | 18 | B | SS.GM.T0003730 | SS.MH.T0006423 | SS.MH.T0000308 | 85.6441 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
924 | 18 | B | SS.GM.T0003732 | SS.MH.T0006176 | SS.MH.T0006174 | 111.6854 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
925 | 18 | B | SS.GM.T0003733 | SS.MH.T0006174 | SS.MH.T0006175 | 105.1327 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
926 | 18 | B | SS.GM.T0003734 | SS.MH.T0006171 | SS.MH.T0006173 | 444.2533 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
927 | 18 | B | SS.GM.T0003735 | SS.MH.T0006170 | SS.MH.T0006171 | 299.0623 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
928 | 18 | D | SS.GM.T0003741 | SS.MH.T0005412 | SS.MH.T0005411 | 563.7068 | 6 | Point Repair at 222 ft from 05412 and 123 ft from 05411 | 9500 | 9500 | Point Repair | Repair
929 | 18 | D | SS.GM.T0003749 | SS.MH.T0005390 | SS.MH.T0005389 | 54.3082 | 6 | Point Repair at 28 ft from 05389 | 4750 | 4750 | Point Repair | Repair
930 | 18 | D | SS.GM.T0003755 | SS.MH.T0000579 | SS.MH.T0005604 | 322.7589 | 6 | Replace 240 ft from 05604 to 00579 | 9960 | 9960 | Replace Section | Repair
931 | 18 | D | SS.GM.T0003756 | SS.MH.T0000578 | SS.MH.T0000305 | 130.2064 | 8 | Burst to 8" - 0 svc | 8463.4173 | 8463.4173 | Pipe Burst or Replace | Replace
932 | 18 | D | SS.GM.T0003763 | SS.MH.T0006153 | SS.MH.T0005307 | 296.4378 | 18 | Point Repair at 67, 82 and 91 ft from 06153 | 14250 | 14250 | Point Repair | Repair
933 | 18 | B | SS.GM.T0003768 | SS.MH.T0006144 | SS.MH.T0006145 | 41.4444 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
934 | 18 | C | SS.GM.T0003769 | SS.MH.T0006145 | SS.MH.T0000297 | 197.1063 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
935 | 18 | B | SS.GM.T0003770 | SS.MH.T0000297 | SS.MH.T0006146 | 116.4924 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
936 | 18 | D | SS.GM.T0003771 | SS.MH.T0001687 | SS.MH.T0013834 | 142.1911 | 6 | Point Repair at 136 ft from 01687 | 4750 | 4750 | Point Repair | Repair
937 | 18 | B | SS.GM.T0003772 | SS.MH.T0006143 | SS.MH.T0006142 | 103.821 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
938 | 18 | C | SS.GM.T0003818 | SS.MH.T0005223 | SS.MH.T0005222 | 201.7425 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
939 | 18 | D | SS.GM.T0003824 | SS.MH.T0005186 | SS.MH.T0013654 | 221.2362 | 6 | Point Repair at 4 ft from 13654 and Access; Clean and Inspection | 5634.945 | 5634.945 | Point Repair and Access; Clean and Inspection | Repair
940 | 18 | C | SS.GM.T0003827 | SS.MH.T0005170 | SS.MH.T0005171 | 439.3693 | 6 | Point Repair at 260 ft from 05170 | 4750 | 0 | Monitor in CMOM | None
941 | 18 | C | SS.GM.T0003829 | SS.MH.T0004286 | SS.MH.T0005165 | 95.179 | 6 | Point Repair at 67 ft from 04286 | 4750 | 0 | Monitor in CMOM | None
942 | 18 | C | SS.GM.T0003831 | SS.MH.T0005144 | SS.MH.T0005146 | 417.9618 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
943 | 18 | D | SS.GM.T0003832 | SS.MH.T0004315 | SS.MH.T0005145 | 440.0745 | 8 | Point Repair at 27, 37, 161 and 164 ft from 04315 | 19000 | 19000 | Point Repair | Repair
944 | 18 | B | SS.GM.T0003946 | SS.MH.T0009360 | SS.MH.T0006988 | 265.6594 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
945 | 18 | B | SS.GM.T0003947 | SS.MH.T0009359 | SS.MH.T0006986 | 136.6249 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
946 | 18 | B | SS.GM.T0003948 | SS.MH.T0009362 | SS.MH.T0000326 | 58.2518 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
947 | 18 | B | SS.GM.T0003949 | SS.MH.T0006985 | SS.MH.T0006287 | 158.7638 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
948 | 18 | B | SS.GM.T0003950 | SS.MH.T0006275 | SS.MH.T0006274 | 200.9279 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
949 | 18 | D | SS.GM.T0003952 | SS.MH.T0006271 | SS.MH.T0006274 | 430.5374 | 6 | Point Repair at 93 ft from 06274 | 4750 | 4750 | Point Repair | Repair
950 | 18 | C | SS.GM.T0003953 | SS.MH.T0009474 | SS.MH.T0006272 | 190.9589 | 6 | Add to Root Removal Schedule | 381.9177 | 0 | Add to Root Removal Program in CMOM | Maintenance
951 | 18 | C | SS.GM.T0003954 | SS.MH.T0006280 | SS.MH.T0006279 | 124.6069 | 6 | Point Repair at 5 ft from 06279 | 4750 | 0 | Monitor in CMOM | None
952 | 18 | B | SS.GM.T0003955 | SS.MH.T0010080 | SS.MH.T0006282 | 143.2669 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
953 | 18 | D | SS.GM.T0003956 | SS.MH.T0006289 | SS.MH.T0006288 | 259.8719 | 6 | Point Repair at 250 ft from 06288 | 4750 | 4750 | Point Repair | Repair
954 | 18 | B | SS.GM.T0003958 | SS.MH.T0010082 | SS.MH.T0006284 | 83.2263 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
955 | 18 | B | SS.GM.T0003959 | SS.MH.T0006984 | SS.MH.T0015040 | 196.3925 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
956 | 18 | D | SS.GM.T0003970 | SS.MH.T0011245 | SS.MH.T0005311 | 550.9249 | 6 | Point Repair at 249 ft from 05311 | 4750 | 4750 | Point Repair | Repair
957 | 18 | B | SS.GM.T0003971 | SS.MH.T0012372 | SS.MH.T0006261 | 436.0338 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
958 | 18 | B | SS.GM.T0003972 | SS.MH.T0011023 | SS.MH.T0005300 | 77.438 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
959 | 18 | B | SS.GM.T0003973 | SS.MH.T0011240 | SS.MH.T0005314 | 275.8197 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
960 | 18 | B | SS.GM.T0003975 | SS.MH.T0011254 | SS.MH.T0006143 | 232.2969 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
961 | 18 | C | SS.GM.T0003979 | SS.MH.T0006259 | SS.MH.T0006258 | 340.8846 | 6 | Point Repair at 268 ft from 06259 | 4750 | 0 | Monitor in CMOM | None
962 | 18 | D | SS.GM.T0003980 | SS.MH.T0000323 | SS.MH.T0000322 | 301.7528 | 6 | Point Repair at 164, 190, 199 and 226 ft from 00323 | 19000 | 19000 | Point Repair | Repair
963 | 18 | D | SS.GM.T0003981 | SS.MH.T0012198 | SS.MH.T0005534 | 166.664 | 6 | Point Repair at 10, 21, 46, 56 and 60 ft from 05534 | 23750 | 23750 | Point Repair | Repair
964 | 18 | C | SS.GM.T0003982 | SS.MH.T0015096 | SS.MH.T0005536 | 464.4752 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
965 | 18 | B | SS.GM.T0003983 | SS.MH.T0012363 | SS.MH.T0005577 | 161.6575 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
966 | 18 | D | SS.GM.T0003984 | SS.MH.T0010881 | SS.MH.T0005537 | 734.9365 | 6 | Point Repair at 169 and 210 ft from 05537 | 9500 | 9500 | Point Repair | Repair
967 | 18 | B | SS.GM.T0003986 | SS.MH.T0010874 | SS.MH.T0000322 | 201.3367 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
968 | 18 | D | SS.GM.T0003987 | SS.MH.T0010870 | SS.MH.T0005542 | 641.3262 | 6 | Burst to 8" - 2 svc | 43686.2061 | 43686.2061 | Pipe Burst or Replace | Replace
969 | 18 | D | SS.GM.T0003988 | SS.MH.T0011012 | SS.MH.T0005531 | 479.4263 | 6 | Burst to 8" - 8 svc | 39162.7085 | 39162.7085 | Pipe Burst or Replace | Replace
970 | 18 | D | SS.GM.T0003989 | SS.MH.T0011009 | SS.MH.T0005544 | 456.1101 | 6 | Point Repair at 175 ft from 05544 and Add to Root Removal Schedule | 5662.2203 | 5662.2203 | Point Repair and Add to Root Removal Program in CMOM | Repair
971 | 18 | D | SS.GM.T0003990 | SS.MH.T0012360 | SS.MH.T0006248 | 357.8505 | 6 | Point Repair at 49 ft from 06248 | 4750 | 4750 | Point Repair | Repair
972 | 18 | B | SS.GM.T0003992 | SS.MH.T0009468 | SS.MH.T0006236 | 281.9739 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
973 | 18 | B | SS.GM.T0003994 | SS.MH.T0014967 | SS.MH.T0006241 | 203.2326 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
974 | 18 | C | SS.GM.T0003995 | SS.MH.T0009467 | SS.MH.T0006237 | 358.6217 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
975 | 18 | C | SS.GM.T0003999 | SS.MH.T0005364 | SS.MH.T0006224 | 563.7479 | 6 | Point Repair at 105, 163, 271 and 320 ft from 05364 | 19000 | 0 | Monitor in CMOM | None
976 | 18 | B | SS.GM.T0004000 | SS.MH.T0006225 | SS.MH.T0006224 | 56.177 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
977 | 18 | D | SS.GM.T0004001 | SS.MH.T0006226 | SS.MH.T0006227 | 70.2401 | 10 | Point Repair at 14 ft from 06226 | 4750 | 4750 | Point Repair | Repair
978 | 18 | D | SS.GM.T0004002 | SS.MH.T0006227 | SS.MH.T0006228 | 355.4217 | 12 | Point Repair at 94 and 127 ft from 06227 and 27 and 53 ft from 06228 | 19000 | 19000 | Point Repair | Repair
979 | 18 | D | SS.GM.T0004003 | SS.MH.T0006960 | SS.MH.T0006959 | 400.1205 | 6 | Point Repair at 162 ft from 06960 | 4750 | 4750 | Point Repair | Repair
980 | 18 | D | SS.GM.T0004004 | SS.MH.T0010214 | SS.MH.T0006963 | 377.3519 | 6 | Point Repair at 172, 245 and 255 ft from 06963 and Add to Root Removal Schedule | 15004.7037 | 15004.7037 | Point Repair and Add to Root Removal Program in CMOM | Repair
981 | 18 | B | SS.GM.T0004005 | SS.MH.T0010213 | SS.MH.T0006965 | 215.9735 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
982 | 18 | D | SS.GM.T0004006 | SS.MH.T0006964 | SS.MH.T0006958 | 441.7023 | 6 | Point Repair at 117 and 308 ft from 06964 | 9500 | 9500 | Point Repair | Repair
983 | 18 | B | SS.GM.T0004007 | SS.MH.T0010215 | SS.MH.T0000292 | 54.3999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
984 | 18 | B | SS.GM.T0004008 | SS.MH.T0005367 | SS.MH.T0013986 | 402.2849 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
985 | 18 | D | SS.GM.T0004009 | SS.MH.T0005286 | SS.MH.T0005287 | 312.1472 | 6 | Burst to 8" - 5 svc | 25289.5672 | 25289.5672 | Pipe Burst or Replace | Replace
986 | 18 | C | SS.GM.T0004010 | SS.MH.T0012351 | SS.MH.T0005286 | 225.9672 | 6 | Add to Root Removal Schedule | 451.9343 | 0 | Add to Root Removal Program in CMOM | Maintenance
987 | 18 | C | SS.GM.T0004011 | SS.MH.T0006958 | SS.MH.T0006951 | 409.9428 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
988 | 18 | B | SS.GM.T0004012 | SS.MH.T0005291 | SS.MH.T0005287 | 519.8634 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
989 | 18 | B | SS.GM.T0004013 | SS.MH.T0006954 | SS.MH.T0006953 | 334.2632 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
990 | 18 | B | SS.GM.T0004014 | SS.MH.T0005287 | SS.MH.T0005288 | 114.2371 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
991 | 18 | D | SS.GM.T0004015 | SS.MH.T0005284 | SS.MH.T0005285 | 358.209 | 8 | Point Repair at 134, 137, 140, 255, 264 and 272 ft from 05284 | 28500 | 28500 | Point Repair | Repair
992 | 18 | B | SS.GM.T0004016 | SS.MH.T0009586 | SS.MH.T0005284 | 448.8238 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
993 | 18 | B | SS.GM.T0004017 | SS.MH.T0010209 | SS.MH.T0005279 | 248.8853 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
994 | 18 | D | SS.GM.T0004018 | SS.MH.T0005282 | SS.MH.T0000321 | 222.0628 | 8 | Point Repair at 54 ft from 00321 | 4750 | 4750 | Point Repair | Repair
995 | 18 | D | SS.GM.T0004022 | SS.MH.T0005267 | SS.MH.T0006098 | 253.262 | 8 | Point Repair at 28 and 53 ft from 05267 | 9500 | 9500 | Point Repair | Repair
996 | 18 | B | SS.GM.T0004023 | SS.MH.T0006098 | SS.MH.T0015719 | 292.1456 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
997 | 18 | C | SS.GM.T0004024 | SS.MH.T0011957 | SS.MH.T0006123 | 297.0198 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
998 | 18 | B | SS.GM.T0004025 | SS.MH.T0006128 | SS.MH.T0006129 | 8.3653 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
999 | 18 | B | SS.GM.T0004026 | SS.MH.T0006127 | SS.MH.T0006128 | 351.0766 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1000 | 18 | B | SS.GM.T0004027 | SS.MH.T0000291 | SS.MH.T0006132 | 74.2417 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1001 | 18 | B | SS.GM.T0004028 | SS.MH.T0010128 | SS.MH.T0000291 | 149.8201 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1002 | 18 | D | SS.GM.T0004029 | SS.MH.T0000287 | SS.MH.T0015723 | 389.9481 | 8 | 8" CIPP - 2 svc | 19547.6623 | 19547.6623 | Cured In Place Pipe Liner | Rehab
1003 | 18 | B | SS.GM.T0004030 | SS.MH.T0006112 | SS.MH.T0006111 | 93.6135 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1004 | 18 | D | SS.GM.T0004031 | SS.MH.T0006249 | SS.MH.T0006111 | 614.9576 | 6 | Point Repair at 110 ft from 06249 | 4750 | 4750 | Point Repair | Repair
1005 | 18 | B | SS.GM.T0004032 | SS.MH.T0011970 | SS.MH.T0000287 | 320.2997 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1006 | 18 | D | SS.GM.T0004034 | SS.MH.T0012193 | SS.MH.T0005244 | 671.1629 | 6 | Point Repair at 15, 82 and 137 ft from 05244 | 14250 | 14250 | Point Repair | Repair
1007 | 18 | C | SS.GM.T0004035 | SS.MH.T0012192 | SS.MH.T0006087 | 600.0166 | 6 | Point Repair at 132 ft from 06087 | 4750 | 0 | Monitor in CMOM | None
1008 | 18 | D | SS.GM.T0004036 | SS.MH.T0010995 | SS.MH.T0005240 | 773.0088 | 6 | Point Repair at 36, 12, 295 and 301 ft from 05240 | 19000 | 19000 | Point Repair | Repair
1009 | 18 | D | SS.GM.T0004037 | SS.MH.T0011952 | SS.MH.T0005238 | 232.1432 | 6 | Burst to 8" - 2 svc | 17089.3049 | 17089.3049 | Pipe Burst or Replace | Replace
1010 | 18 | D | SS.GM.T0004041 | SS.MH.T0011113 | SS.MH.T0000750 | 618.6347 | 6 | Burst to 8" - 7 svc | 47211.2583 | 47211.2583 | Pipe Burst or Replace | Replace
1011 | 18 | B | SS.GM.T0006027 | SS.MH.T0006799 | SS.MH.T0006800 | 115.3776 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1012 | 18 | B | SS.GM.T0008921 | SS.MH.T0006800 | SS.MH.T0015725 | 263.3051 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1013 | 18 | B | SS.GM.T0008922 | SS.MH.T0013212 | SS.MH.T0006798 | 333.6183 | 8 | Assign to high frequency cleaning - Grease | 1000.8549 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
1014 | 18 | C | SS.GM.T0009458 | SS.MH.T0000631 | SS.MH.T0004295 | 11.1261 | 6 | Point Repair at 10 ft from 00631 | 4750 | 0 | Monitor in CMOM | None
1015 | 18 | D | SS.GM.T0009459 | SS.MH.T0010062 | SS.MH.T0000631 | 210.2832 | 6 | Point Repair at 208 ft from 00631 | 4750 | 4750 | Point Repair | Repair
1016 | 18 | D | SS.GM.T0009460 | SS.MH.T0010063 | SS.MH.T0004315 | 497.5681 | 6 | Burst to 8" - 12 svc | 44341.9246 | 44341.9246 | Pipe Burst or Replace | Replace
1017 | 18 | D | SS.GM.T0009461 | SS.MH.T0006336 | SS.MH.T0000632 | 161.8312 | 8 | Point Repair at 39 ft from 06336 | 4750 | 4750 | Point Repair | Repair
1018 | 18 | C | SS.GM.T0009462 | SS.MH.T0000632 | SS.MH.T0004316 | 151.3929 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1019 | 18 | B | SS.GM.T0009463 | SS.MH.T0000657 | SS.MH.T0000633 | 48.9859 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1020 | 18 | D | SS.GM.T0009464 | SS.MH.T0000633 | SS.MH.T0004282 | 211.5387 | 6 | Point Repair at 33 and 63 ft from 04282 | 9500 | 9500 | Point Repair | Repair
1021 | 18 | C | SS.GM.T0009465 | SS.MH.T0005148 | SS.MH.T0000634 | 272.5618 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1022 | 18 | D | SS.GM.T0009466 | SS.MH.T0000634 | SS.MH.T0004283 | 235.4945 | 6 | Grout Joint at 41 ft from 04283 | 800 | 800 | Grout Joints | Repair
1023 | 18 | D | SS.GM.T0009469 | SS.MH.T0005222 | SS.MH.T0005978 | 129.4936 | 8 | Burst to 8" - 0 svc | 8417.0839 | 8417.0839 | Pipe Burst or Replace | Replace
1024 | 18 | D | SS.GM.T0014969 | SS.MH.T0005978 | SS.MH.T0015099 | 120 | 8 | Burst to 8" - 0 svc | 7800 | 7800 | Pipe Burst or Replace | Replace
1025 | 18 | D | SS.GM.T0009470 | SS.MH.T0015099 | SS.MH.T0005242 | 160.5069 | 8 | Burst to 8" - 0 svc | 10432.9461 | 10432.9461 | Pipe Burst or Replace | Replace
1026 | 18 | D | SS.GM.T0009471 | SS.MH.T0005242 | SS.MH.T0005977 | 375.0701 | 8 | Burst to 8" - 0 svc | 24379.5571 | 24379.5571 | Pipe Burst or Replace | Replace
1027 | 18 | D | SS.GM.T0009472 | SS.MH.T0005977 | SS.MH.T0005976 | 33.5029 | 8 | Burst to 8" - 0 svc | 2177.6907 | 2177.6907 | Pipe Burst or Replace | Replace
1028 | 18 | C | SS.GM.T0009473 | SS.MH.T0005976 | SS.MH.T0005227 | 40.7873 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1029 | 18 | D | SS.GM.T0009474 | SS.MH.T0005235 | SS.MH.T0005980 | 164.8907 | 6 | Burst to 8" - 0 svc | 10717.8967 | 10717.8967 | Pipe Burst or Replace | Replace
1030 | 18 | B | SS.GM.T0009475 | SS.MH.T0005980 | SS.MH.T0015098 | 158.2425 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1031 | 18 | D | SS.GM.T0009477 | SS.MH.T0004329 | SS.MH.T0004332 | 351.7733 | 6 | Point Repair at 276 and 347 ft and Grout Joint at 16 ft from 04329 and Add to Root Removal Schedule | 11003.5466 | 11003.5466 | Point Repair & Grout Joint & Add to Root Removal Schedule | Repair
1032 | 18 | D | SS.GM.T0009478 | SS.MH.T0005142 | SS.MH.T0005981 | 748.0122 | 6 | Burst to 8" - 10 svc | 58620.7903 | 58620.7903 | Pipe Burst or Replace | Replace
1033 | 18 | C | SS.GM.T0009479 | SS.MH.T0005981 | SS.MH.T0000749 | 18.8431 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1034 | 18 | D | SS.GM.T0009480 | SS.MH.T0005238 | SS.MH.T0005235 | 339.2255 | 6 | Burst to 8" - 0 svc | 22049.66 | 22049.66 | Pipe Burst or Replace | Replace
1035 | 18 | B | SS.GM.T0009483 | SS.MH.T0005167 | SS.MH.T0005985 | 344.2923 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1036 | 18 | A | SS.GM.T0009647 | SS.MH.T0007019 | SS.MH.T0006189 | 201.4312 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1037 | 18 | C | SS.GM.T0009648 | SS.MH.T0007021 | SS.MH.T0007020 | 294.2421 | 6 | Add to Root Removal Schedule | 588.4842 | 0 | Add to Root Removal Program in CMOM | Maintenance
1038 | 18 | B | SS.GM.T0009649 | SS.MH.T0007020 | SS.MH.T0007019 | 299.86 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1039 | 18 | D | SS.GM.T0009652 | SS.MH.T0006192 | SS.MH.T0007024 | 374.0961 | 12 | Point Repair at 196, 342, 354, 369 and 374 ft from 06192 and Add to Root Removal Schedule | 24498.1921 | 24498.1921 | Point Repair and Add to Root Removal Program in CMOM | Repair
1040 | 18 | B | SS.GM.T0009653 | SS.MH.T0007024 | SS.MH.T0007025 | 289.606 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1041 | 18 | C | SS.GM.T0009654 | SS.MH.T0015477 | SS.MH.T0007026 | 265.8059 | 12 | Add to Root Removal Schedule | 531.6118 | 0 | Add to Root Removal Program in CMOM | Maintenance
1042 | 18 | D | SS.GM.T0009676 | SS.MH.T0005311 | SS.MH.T0000844 | 285.934 | 6 | Point Repair at 66, 165 and 247 ft from 05311 | 14250 | 14250 | Point Repair | Repair
1043 | 18 | C | SS.GM.T0009677 | SS.MH.T0000844 | SS.MH.T0005308 | 35.3029 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1044 | 18 | C | SS.GM.T0009678 | SS.MH.T0000845 | SS.MH.T0005309 | 28.2688 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1045 | 18 | C | SS.GM.T0009683 | SS.MH.T0000848 | SS.MH.T0005312 | 15.0305 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1046 | 18 | D | SS.GM.T0009684 | SS.MH.T0005313 | SS.MH.T0000848 | 313.7999 | 8 | Point Repair at 126, 131 and 139 ft from 05313 | 14250 | 14250 | Point Repair | Repair
1047 | 18 | D | SS.GM.T0009688 | SS.MH.T0006211 | SS.MH.T0006209 | 264.0802 | 6 | Replace section 34 to 48 ft from 06209. Point Repair at 167 ft from 06209 | 6430 | 6430 | Replace Section & Point Repair | Repair
1048 | 18 | B | SS.GM.T0009689 | SS.MH.T0015628 | SS.MH.T0006891 | 346.0378 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1049 | 18 | D | SS.GM.T0009690 | SS.MH.T0006894 | SS.MH.T0000320 | 31.3907 | 6 | Burst to 8" - 1 svc | 3040.3954 | 3040.3954 | Pipe Burst or Replace | Replace
1050 | 18 | B | SS.GM.T0009695 | SS.MH.T0000650 | SS.MH.T0015482 | 114.5785 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1051 | 18 | B | SS.GM.T0009697 | SS.MH.T0009460 | SS.MH.T0000652 | 120.6136 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1052 | 18 | A | SS.GM.T0009702 | SS.MH.T0006901 | SS.MH.T0006900 | 136.549 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1053 | 18 | B | SS.GM.T0009703 | SS.MH.T0006900 | SS.MH.T0000655 | 124.6158 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1054 | 18 | D | SS.GM.T0009704 | SS.MH.T0015732 | SS.MH.T0000654 | 316.3034 | 6 | Point Repair at 312 ft from 15732 | 4750 | 4750 | Point Repair | Repair
1055 | 18 | B | SS.GM.T0009705 | SS.MH.T0000654 | SS.MH.T0006422 | 148.7036 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1056 | 18 | D | SS.GM.T0009767 | SS.MH.T0011102 | SS.MH.T0000631 | 398.8428 | 6 | Burst to 8" - 2 svc | 27924.7836 | 27924.7836 | Pipe Burst or Replace | Replace
1057 | 18 | D | SS.GM.T0009768 | SS.MH.T0011189 | SS.MH.T0010063 | 221.7245 | 6 | Point Repair at 152 and 193 ft from 10063 | 9500 | 9500 | Point Repair | Repair
1058 | 18 | C | SS.GM.T0009770 | SS.MH.T0011689 | SS.MH.T0004285 | 523.8185 | 6 | Add to Root Removal Schedule | 1047.637 | 0 | Add to Root Removal Program in CMOM | Maintenance
1059 | 18 | C | SS.GM.T0009771 | SS.MH.T0011688 | SS.MH.T0004286 | 316.0153 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1060 | 18 | C | SS.GM.T0009772 | SS.MH.T0011690 | SS.MH.T0005165 | 86.2595 | 6 | Point Repair at 77 ft from 05165 | 4750 | 0 | Monitor in CMOM | None
1061 | 18 | D | SS.GM.T0009773 | SS.MH.T0012750 | SS.MH.T0005975 | 498.3869 | 6 | Point Repair at 23 ft from 05975 | 4750 | 4750 | Point Repair | Repair
1062 | 18 | B | SS.GM.T0009774 | SS.MH.T0012751 | SS.MH.T0005975 | 167.4234 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1063 | 18 | D | SS.GM.T0009775 | SS.MH.T0012752 | SS.MH.T0005241 | 126.113 | 6 | Point Repair at 44 ft from 05241 | 4750 | 4750 | Point Repair | Repair
1064 | 18 | B | SS.GM.T0009798 | SS.MH.T0011506 | SS.MH.T0007021 | 600.1685 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1065 | 18 | C | SS.GM.T0009800 | SS.MH.T0011243 | SS.MH.T0000845 | 442.9677 | 6 | Point Repair at 86 ft from 00845 | 4750 | 0 | Monitor in CMOM | None
1066 | 18 | B | SS.GM.T0009802 | SS.MH.T0015279 | SS.MH.T0006892 | 97.3001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1067 | 18 | B | SS.GM.T0009803 | SS.MH.T0013023 | SS.MH.T0006892 | 175.8121 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1068 | 18 | B | SS.GM.T0009805 | SS.MH.T0011509 | SS.MH.T0000320 | 15.191 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1069 | 18 | B | SS.GM.T0009864 | SS.MH.T0009786 | SS.MH.T0008022 | 287.9614 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1070 | 18 | B | SS.GM.T0009865 | SS.MH.T0008021 | SS.MH.T0008022 | 204.5723 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1071 | 18 | B | SS.GM.T0009866 | SS.MH.T0008026 | SS.MH.T0008025 | 251.227 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1072 | 18 | B | SS.GM.T0009867 | SS.MH.T0008024 | SS.MH.T0008025 | 300.5421 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1073 | 18 | B | SS.GM.T0009868 | SS.MH.T0008014 | SS.MH.T0008015 | 396.6751 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1074 | 18 | B | SS.GM.T0009869 | SS.MH.T0008017 | SS.MH.T0008016 | 84.6028 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1075 | 18 | B | SS.GM.T0009870 | SS.MH.T0008016 | SS.MH.T0015729 | 266.8536 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1076 | 18 | B | SS.GM.T0009871 | SS.MH.T0008025 | SS.MH.T0015728 | 269 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1077 | 18 | B | SS.GM.T0009872 | SS.MH.T0015716 | SS.MH.T0005444 | 402.7 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1078 | 18 | B | SS.GM.T0009873 | SS.MH.T0008018 | SS.MH.T0008017 | 221.2085 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1079 | 18 | B | SS.GM.T0009874 | SS.MH.T0008019 | SS.MH.T0008018 | 349.769 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1080 | 18 | B | SS.GM.T0009875 | SS.MH.T0008029 | SS.MH.T0008028 | 252.6873 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1081 | 18 | B | SS.GM.T0009876 | SS.MH.T0009790 | SS.MH.T0008029 | 153.1444 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1082 | 18 | B | SS.GM.T0009877 | SS.MH.T0009789 | SS.MH.T0008029 | 93.9496 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1083 | 18 | B | SS.GM.T0009878 | SS.MH.T0008007 | SS.MH.T0008046 | 237.4001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1084 | 18 | B | SS.GM.T0009879 | SS.MH.T0008008 | SS.MH.T0008007 | 386.9167 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1085 | 18 | B | SS.GM.T0009880 | SS.MH.T0008012 | SS.MH.T0008011 | 395.2841 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1086 | 18 | B | SS.GM.T0009945 | SS.MH.T0007973 | SS.MH.T0007975 | 195.0204 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1087 | 18 | B | SS.GM.T0009946 | SS.MH.T0007975 | SS.MH.T0007976 | 156.5028 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1088 | 18 | B | SS.GM.T0009947 | SS.MH.T0012776 | SS.MH.T0007975 | 265.1999 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1089 | 18 | B | SS.GM.T0009954 | SS.MH.T0015001 | SS.MH.T0008001 | 63.0359 | 4 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1090 | 18 | C | SS.GM.T0009955 | SS.MH.T0015799 | SS.MH.T0007984 | 128.1 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1091 | 18 | B | SS.GM.T0009956 | SS.MH.T0007997 | SS.MH.T0007998 | 239.3613 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1092 | 18 | B | SS.GM.T0009957 | SS.MH.T0007990 | SS.MH.T0007989 | 303.7408 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1093 | 18 | B | SS.GM.T0009958 | SS.MH.T0009782 | SS.MH.T0007991 | 239.3162 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1094 | 18 | B | SS.GM.T0009961 | SS.MH.T0008166 | SS.MH.T0008165 | 268.9256 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1095 | 18 | B | SS.GM.T0009963 | SS.MH.T0008161 | SS.MH.T0008162 | 156.9791 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1096 | 18 | B | SS.GM.T0009964 | SS.MH.T0008155 | SS.MH.T0008154 | 102.087 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1097 | 18 | B | SS.GM.T0009965 | SS.MH.T0009804 | SS.MH.T0008162 | 157.5114 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1098 | 18 | B | SS.GM.T0009966 | SS.MH.T0009803 | SS.MH.T0008159 | 106.3182 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1099 | 18 | B | SS.GM.T0009967 | SS.MH.T0008150 | SS.MH.T0008151 | 323.4662 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1100 | 18 | B | SS.GM.T0009969 | SS.MH.T0008149 | SS.MH.T0008148 | 132.4766 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1101 | 18 | B | SS.GM.T0009970 | SS.MH.T0008140 | SS.MH.T0008141 | 232.8796 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1102 | 18 | B | SS.GM.T0009971 | SS.MH.T0007985 | SS.MH.T0007914 | 508.9985 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1103 | 18 | B | SS.GM.T0009972 | SS.MH.T0007983 | SS.MH.T0015740 | 584.9589 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1104 | 18 | B | SS.GM.T0009973 | SS.MH.T0005441 | SS.MH.T0005442 | 464.8297 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1105 | 18 | B | SS.GM.T0010111 | SS.MH.T0013913 | SS.MH.T0006211 | 262.8044 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1106 | 18 | B | SS.GM.T0010191 | SS.MH.T0015730 | SS.MH.T0008134 | 224.9928 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1107 | 18 | C | SS.GM.T0010192 | SS.MH.T0009796 | SS.MH.T0008130 | 171.6315 | 6 | Add to Root Removal Schedule | 343.263 | 0 | Add to Root Removal Program in CMOM | Maintenance
1108 | 18 | B | SS.GM.T0010194 | SS.MH.T0008133 | SS.MH.T0008132 | 197.9235 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1109 | 18 | B | SS.GM.T0010195 | SS.MH.T0009797 | SS.MH.T0008131 | 270.9327 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1110 | 18 | B | SS.GM.T0010200 | SS.MH.T0008125 | SS.MH.T0008128 | 161.9127 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1111 | 18 | B | SS.GM.T0010202 | SS.MH.T0008126 | SS.MH.T0008125 | 403.4773 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1112 | 18 | B | SS.GM.T0010203 | SS.MH.T0010459 | SS.MH.T0008124 | 282.6536 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1113 | 18 | B | SS.GM.T0010204 | SS.MH.T0010458 | SS.MH.T0008123 | 316.0011 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1114 | 18 | B | SS.GM.T0010205 | SS.MH.T0008122 | SS.MH.T0008121 | 454.0496 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1115 | 18 | B | SS.GM.T0010206 | SS.MH.T0008116 | SS.MH.T0008115 | 360.9241 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1116 | 18 | B | SS.GM.T0010207 | SS.MH.T0008095 | SS.MH.T0008134 | 424.4376 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1117 | 18 | B | SS.GM.T0010222 | SS.MH.T0008115 | SS.MH.T0008114 | 24.2006 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1118 | 18 | B | SS.GM.T0010296 | SS.MH.T0006897 | SS.MH.T0006896 | 277.4913 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1119 | 18 | C | SS.GM.T0010297 | SS.MH.T0006966 | SS.MH.T0006967 | 173.8749 | 6 | Point Repair at 174 ft from 06966 | 4750 | 0 | Monitor in CMOM | None
1120 | 18 | B | SS.GM.T0010298 | SS.MH.T0007284 | SS.MH.T0006896 | 187.1267 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1121 | 18 | B | SS.GM.T0010299 | SS.MH.T0010490 | SS.MH.T0008697 | 324.1359 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1122 | 18 | B | SS.GM.T0010300 | SS.MH.T0010491 | SS.MH.T0008698 | 105.4523 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1123 | 18 | B | SS.GM.T0010301 | SS.MH.T0008711 | SS.MH.T0008712 | 398.2388 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1124 | 18 | B | SS.GM.T0010302 | SS.MH.T0008696 | SS.MH.T0008698 | 383.3596 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1125 | 18 | B | SS.GM.T0010303 | SS.MH.T0008703 | SS.MH.T0008704 | 403.5947 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1126 | 18 | B | SS.GM.T0010304 | SS.MH.T0010494 | SS.MH.T0008700 | 363.6298 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1127 | 18 | B | SS.GM.T0010311 | SS.MH.T0008709 | SS.MH.T0008707 | 399.1613 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1128 | 18 | B | SS.GM.T0010312 | SS.MH.T0008706 | SS.MH.T0008704 | 342.0305 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1129 | 18 | B | SS.GM.T0010314 | SS.MH.T0000327 | SS.MH.T0008713 | 168.673 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1130 | 18 | B | SS.GM.T0010316 | SS.MH.T0000516 | SS.MH.T0000519 | 149.2661 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1131 | 18 | B | SS.GM.T0010317 | SS.MH.T0013293 | SS.MH.T0013295 | 283.853 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1132 | 18 | B | SS.GM.T0010318 | SS.MH.T0009867 | SS.MH.T0000520 | 87.6538 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1133 | 18 | B | SS.GM.T0010319 | SS.MH.T0005336 | SS.MH.T0005335 | 181.5859 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1134 | 18 | B | SS.GM.T0010320 | SS.MH.T0005333 | SS.MH.T0005330 | 195.5808 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1135 | 18 | B | SS.GM.T0010321 | SS.MH.T0005335 | SS.MH.T0005333 | 258.8299 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1136 | 18 | B | SS.GM.T0010322 | SS.MH.T0015280 | SS.MH.T0006890 | 48.5963 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1137 | 18 | B | SS.GM.T0010323 | SS.MH.T0005334 | SS.MH.T0005333 | 119.6938 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1138 | 18 | B | SS.GM.T0010325 | SS.MH.T0007579 | SS.MH.T0007584 | 197.1996 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1139 | 18 | B | SS.GM.T0010326 | SS.MH.T0005337 | SS.MH.T0005335 | 173.5802 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1140 | 18 | B | SS.GM.T0010327 | SS.MH.T0005340 | SS.MH.T0007584 | 158.551 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1141 | 18 | B | SS.GM.T0010328 | SS.MH.T0000302 | SS.MH.T0005340 | 290.1641 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1142 | 18 | B | SS.GM.T0010329 | SS.MH.T0009885 | SS.MH.T0005341 | 110.5036 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1143 | 18 | B | SS.GM.T0010330 | SS.MH.T0000303 | SS.MH.T0005343 | 183.1279 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1144 | 18 | B | SS.GM.T0010331 | SS.MH.T0009972 | SS.MH.T0000302 | 65.7804 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1145 | 18 | B | SS.GM.T0010332 | SS.MH.T0009311 | SS.MH.T0000568 | 202.3037 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1146 | 18 | B | SS.GM.T0010333 | SS.MH.T0009886 | SS.MH.T0000566 | 145.986 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1147 | 18 | B | SS.GM.T0010334 | SS.MH.T0009751 | SS.MH.T0007583 | 193.2847 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1148 | 18 | B | SS.GM.T0010335 | SS.MH.T0000660 | SS.MH.T0007583 | 259.1036 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1149 | 18 | B | SS.GM.T0010336 | SS.MH.T0015636 | SS.MH.T0015637 | 171.8073 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1150 | 18 | B | SS.GM.T0010337 | SS.MH.T0015013 | SS.MH.T0000660 | 152.8456 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1151 | 18 | B | SS.GM.T0010338 | SS.MH.T0015011 | SS.MH.T0000660 | 124.276 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1152 | 18 | B | SS.GM.T0010339 | SS.MH.T0007583 | SS.MH.T0007585 | 262.5174 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1153 | 18 | C | SS.GM.T0010340 | SS.MH.T0006891 | SS.MH.T0000569 | 57.9585 | 15 | Point Repair at 37 ft from 00569 | 4750 | 0 | Monitor in CMOM | None
1154 | 18 | D | SS.GM.T0010341 | SS.MH.T0005331 | SS.MH.T0006154 | 439.0476 | 15 | 15" CIPP - 1 svc | 36123.8107 | 36123.8107 | Cured In Place Pipe Liner | Rehab
1155 | 18 | D | SS.GM.T0010342 | SS.MH.T0000569 | SS.MH.T0005332 | 500.7548 | 15 | Point Repair at 157, 470 and 478 ft from 00569 | 14250 | 14250 | Point Repair | Repair
1156 | 18 | B | SS.GM.T0010343 | SS.MH.T0008700 | SS.MH.T0008701 | 131.8971 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1157 | 18 | B | SS.GM.T0010345 | SS.MH.T0008698 | SS.MH.T0008699 | 181.9023 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1158 | 18 | A | SS.GM.T0010354 | SS.MH.T0015071 | SS.MH.T0015090 | 131.5001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1159 | 18 | A | SS.GM.T0010355 | SS.MH.T0015072 | SS.MH.T0015090 | 90 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1160 | 18 | B | SS.GM.T0010356 | SS.MH.T0015090 | SS.MH.T0013206 | 273.5277 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1161 | 18 | B | SS.GM.T0010358 | SS.MH.T0013206 | SS.MH.T0007673 | 231.2369 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1162 | 18 | D | SS.GM.T0010442 | SS.MH.T0007669 | SS.MH.T0007668 | 89.6427 | 8 | Grout Joint at 5 ft from 07668 | 800 | 800 | Grout Joints | Repair
1163 | 18 | B | SS.GM.T0010525 | SS.MH.T0007602 | SS.MH.T0007079 | 301.7521 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1164 | 18 | B | SS.GM.T0010526 | SS.MH.T0012770 | SS.MH.T0007081 | 278.5252 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1165 | 18 | A | SS.GM.T0010527 | SS.MH.T0007593 | SS.MH.T0007604 | 206.7117 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1166 | 18 | B | SS.GM.T0010528 | SS.MH.T0007603 | SS.MH.T0007078 | 351.4869 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1167 | 18 | B | SS.GM.T0010529 | SS.MH.T0013208 | SS.MH.T0013205 | 201.7375 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1168 | 18 | B | SS.GM.T0010530 | SS.MH.T0007594 | SS.MH.T0007080 | 213.6664 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1169 | 18 | B | SS.GM.T0010531 | SS.MH.T0012769 | SS.MH.T0007789 | 151.8147 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1170 | 18 | B | SS.GM.T0010532 | SS.MH.T0007789 | SS.MH.T0013207 | 136.4613 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1171 | 18 | A | SS.GM.T0010541 | SS.MH.T0013710 | SS.MH.T0013711 | 364.0036 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1172 | 18 | A | SS.GM.T0010542 | SS.MH.T0013282 | SS.MH.T0001473 | 377.0054 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1173 | 18 | A | SS.GM.T0010543 | SS.MH.T0013709 | SS.MH.T0009771 | 156.3392 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1174 | 18 | B | SS.GM.T0010544 | SS.MH.T0001471 | SS.MH.T0001458 | 63.6018 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1175 | 18 | B | SS.GM.T0010700 | SS.MH.T0007580 | SS.MH.T0007581 | 132.4649 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1176 | 18 | A | SS.GM.T0010712 | SS.MH.T0007609 | SS.MH.T0007610 | 150.5319 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1177 | 18 | B | SS.GM.T0010784 | SS.MH.T0007672 | SS.MH.T0007669 | 104.6459 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1178 | 18 | B | SS.GM.T0010786 | SS.MH.T0015091 | SS.MH.T0007671 | 103.4506 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1179 | 18 | A | SS.GM.T0010787 | SS.MH.T0007671 | SS.MH.T0007670 | 25.8196 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1180 | 18 | B | SS.GM.T0010788 | SS.MH.T0007660 | Ss.Ls.T0000019 | 9.133 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1181 | 18 | B | SS.GM.T0010789 | SS.MH.T0007673 | SS.MH.T0007672 | 49.5065 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1182 | 18 | B | SS.GM.T0010809 | SS.MH.T0008697 | SS.MH.T0008700 | 263.1468 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1183 | 18 | B | SS.GM.T0010833 | SS.MH.T0007708 | SS.MH.T0007709 | 209.9924 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1184 | 18 | B | SS.GM.T0010834 | SS.MH.T0007709 | SS.MH.T0007710 | 196.0529 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1185 | 18 | B | SS.GM.T0010835 | SS.MH.T0007710 | SS.MH.T0007712 | 221.9792 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1186 | 18 | B | SS.GM.T0010836 | SS.MH.T0007741 | SS.MH.T0007742 | 453.2435 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1187 | 18 | B | SS.GM.T0010837 | SS.MH.T0010413 | SS.MH.T0007700 | 388.4191 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1188 | 18 | B | SS.GM.T0010838 | SS.MH.T0007700 | SS.MH.T0007699 | 399.7424 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1189 | 18 | D | SS.GM.T0010839 | SS.MH.T0007701 | SS.MH.T0007699 | 407.6806 | 6 | Burst to 8" - 10 svc | 36499.2398 | 36499.2398 | Pipe Burst or Replace | Replace
1190 | 18 | B | SS.GM.T0010840 | SS.MH.T0007702 | SS.MH.T0007701 | 241.3842 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1191 | 18 | B | SS.GM.T0010841 | SS.MH.T0010414 | SS.MH.T0007702 | 96.0192 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1192 | 18 | B | SS.GM.T0010842 | SS.MH.T0010415 | SS.MH.T0007702 | 299.4138 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1193 | 18 | B | SS.GM.T0010843 | SS.MH.T0009754 | SS.MH.T0007706 | 275.3398 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1194 | 18 | B | SS.GM.T0010844 | SS.MH.T0007706 | SS.MH.T0007705 | 73.6754 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1195 | 18 | B | SS.GM.T0010845 | SS.MH.T0007705 | SS.MH.T0007704 | 279.1683 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1196 | 18 | B | SS.GM.T0010846 | SS.MH.T0009755 | SS.MH.T0007703 | 261.8738 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1197 | 18 | B | SS.GM.T0010847 | SS.MH.T0007703 | SS.MH.T0007696 | 298.1557 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1198 | 18 | B | SS.GM.T0010848 | SS.MH.T0007704 | SS.MH.T0007694 | 302.7762 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1199 | 18 | B | SS.GM.T0010849 | SS.MH.T0007707 | SS.MH.T0007692 | 401.7371 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1200 | 18 | B | SS.GM.T0010850 | SS.MH.T0009756 | SS.MH.T0007707 | 399.9772 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1201 | 18 | B | SS.GM.T0010854 | SS.MH.T0007692 | SS.MH.T0007712 | 431.8213 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1202 | 18 | C | SS.GM.T0010855 | SS.MH.T0007694 | SS.MH.T0007692 | 367.2145 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1203 | 18 | B | SS.GM.T0010856 | SS.MH.T0007696 | SS.MH.T0007694 | 352.1895 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1204 | 18 | B | SS.GM.T0010857 | SS.MH.T0007699 | SS.MH.T0007696 | 373.9517 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1205 | 18 | B | SS.GM.T0010858 | SS.MH.T0007698 | SS.MH.T0007697 | 466.8764 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1206 | 18 | B | SS.GM.T0010859 | SS.MH.T0007697 | SS.MH.T0007696 | 399.9843 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1207 | 18 | B | SS.GM.T0010860 | SS.MH.T0010412 | SS.MH.T0007695 | 353.0886 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1208 | 18 | D | SS.GM.T0010861 | SS.MH.T0007695 | SS.MH.T0007694 | 501.5605 | 6 | Burst to 8" - 1 svc | 33601.431 | 33601.431 | Pipe Burst or Replace | Replace
1209 | 18 | B | SS.GM.T0010862 | SS.MH.T0007693 | SS.MH.T0007692 | 450.6655 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1210 | 18 | B | SS.GM.T0010863 | SS.MH.T0010411 | SS.MH.T0007693 | 401.0966 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1211 | 18 | B | SS.GM.T0010922 | SS.MH.T0009765 | SS.MH.T0007745 | 81.2051 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1212 | 18 | B | SS.GM.T0010923 | SS.MH.T0009766 | SS.MH.T0007746 | 79.1637 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1213 | 18 | B | SS.GM.T0010924 | SS.MH.T0009767 | SS.MH.T0007747 | 75.5995 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1214 | 18 | B | SS.GM.T0010928 | SS.MH.T0007748 | SS.MH.T0007747 | 199.7366 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1215 | 18 | B | SS.GM.T0010929 | SS.MH.T0007747 | SS.MH.T0007746 | 198.4288 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1216 | 18 | C | SS.GM.T0010930 | SS.MH.T0007746 | SS.MH.T0007745 | 208.7808 | 8 | Point Repair at 161 ft from 07746 | 4750 | 0 | Monitor in CMOM | None
1217 | 18 | B | SS.GM.T0010931 | SS.MH.T0007745 | SS.MH.T0007712 | 242.178 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1218 | 18 | A | SS.GM.T0010975 | SS.MH.T0000241 | SS.MH.T0000245 | 319.8467 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1219 | 18 | A | SS.GM.T0010976 | SS.MH.T0000245 | SS.MH.T0000243 | 40.8888 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1220 | 18 | B | SS.GM.T0010977 | SS.MH.T0000243 | SS.MH.T0000244 | 169.6345 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1221 | 18 | A | SS.GM.T0010978 | SS.MH.T0007711 | SS.MH.T0000242 | 352.3755 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1222 | 18 | A | SS.GM.T0010979 | SS.MH.T0000244 | SS.MH.T0000242 | 48.2821 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1223 | 18 | B | SS.GM.T0010980 | SS.MH.T0000242 | SS.MH.T0000240 | 130.9921 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1224 | 18 | A | SS.GM.T0010981 | SS.MH.T0010420 | SS.MH.T0007711 | 411.9455 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1225 | 18 | A | SS.GM.T0010982 | SS.MH.T0010419 | SS.MH.T0000241 | 400.8752 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1226 | 18 | B | SS.GM.T0011002 | SS.MH.T0007675 | SS.MH.T0007783 | 34.6459 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1227 | 18 | B | SS.GM.T0011003 | SS.MH.T0007783 | SS.MH.T0007782 | 224.8459 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1228 | 18 | C | SS.GM.T0011006 | SS.MH.T0007782 | SS.MH.T0007788 | 263.3335 | 8 | Point Repair at 35 ft from 07782 | 4750 | 0 | Monitor in CMOM | None
1229 | 18 | B | SS.GM.T0011007 | SS.MH.T0007787 | SS.MH.T0007786 | 119.6227 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1230 | 18 | B | SS.GM.T0011008 | SS.MH.T0007788 | SS.MH.T0007787 | 161.1342 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1231 | 18 | B | SS.GM.T0011009 | SS.MH.T0007786 | SS.MH.T0008598 | 180.0096 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1232 | 18 | B | SS.GM.T0011013 | SS.MH.T0013924 | SS.MH.T0008598 | 317.1999 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1233 | 18 | A | SS.GM.T0011015 | SS.MH.T0010401 | SS.MH.T0007607 | 92.7457 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1234 | 18 | A | SS.GM.T0011016 | SS.MH.T0007607 | SS.MH.T0007606 | 261.434 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1235 | 18 | A | SS.GM.T0011017 | SS.MH.T0007606 | SS.MH.T0007605 | 40.3891 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1236 | 18 | A | SS.GM.T0011018 | SS.MH.T0007605 | SS.MH.T0007591 | 153.6579 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1237 | 18 | A | SS.GM.T0011019 | SS.MH.T0010402 | SS.MH.T0007608 | 185.4564 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1238 | 18 | A | SS.GM.T0011020 | SS.MH.T0007608 | SS.MH.T0007609 | 39.2415 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1239 | 18 | A | SS.GM.T0011021 | SS.MH.T0007610 | SS.MH.T0007591 | 63.0481 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1240 | 18 | A | SS.GM.T0011022 | SS.MH.T0007591 | SS.MH.T0007592 | 140.8969 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1241 | 18 | B | SS.GM.T0011024 | SS.MH.T0007604 | SS.MH.T0007594 | 67.6262 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1242 | 18 | B | SS.GM.T0011025 | SS.MH.T0007081 | SS.MH.T0007594 | 268.2763 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1243 | 18 | B | SS.GM.T0011026 | SS.MH.T0007080 | SS.MH.T0007079 | 75.6144 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1244 | 18 | B | SS.GM.T0011027 | SS.MH.T0010422 | SS.MH.T0007602 | 49.0019 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1245 | 18 | B | SS.GM.T0011028 | SS.MH.T0007078 | SS.MH.T0007789 | 349.0417 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1246 | 18 | B | SS.GM.T0011029 | SS.MH.T0012768 | SS.MH.T0007603 | 216.9977 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1247 | 18 | B | SS.GM.T0011405 | SS.MH.T0009870 | SS.MH.T0000529 | 224.4414 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1248 | 18 | B | SS.GM.T0011406 | SS.MH.T0000529 | SS.MH.T0000528 | 34.8358 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1249 | 18 | B | SS.GM.T0011408 | SS.MH.T0007742 | SS.MH.T0007743 | 400.915 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1250 | 18 | B | SS.GM.T0011409 | SS.MH.T0007743 | SS.MH.T0007744 | 301.4794 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1251 | 18 | D | SS.GM.T0011431 | SS.MH.T0015436 | SS.MH.T0006973 | 446.4479 | 12 | 12" CIPP - 0 svc | 31251.3523 | 31251.3523 | Cured In Place Pipe Liner | Rehab
1252 | 18 | D | SS.GM.T0011530 | SS.MH.T0007979 | SS.MH.T0007980 | 85.0328 | 8 | Point Repair at 26 ft from 07979 | 4750 | 4750 | Point Repair | Repair
1253 | 18 | B | SS.GM.T0011531 | SS.MH.T0007978 | SS.MH.T0007979 | 63.5625 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1254 | 18 | B | SS.GM.T0011532 | SS.MH.T0007977 | SS.MH.T0007978 | 119.9497 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1255 | 18 | B | SS.GM.T0011533 | SS.MH.T0007976 | SS.MH.T0007977 | 27.2334 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1256 | 18 | B | SS.GM.T0011536 | SS.MH.T0007984 | SS.MH.T0007983 | 323.0002 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1257 | 18 | B | SS.GM.T0011537 | SS.MH.T0007982 | SS.MH.T0007985 | 24.9339 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1258 | 18 | A | SS.GM.T0011538 | SS.MH.T0007986 | SS.MH.T0015741 | 54.2 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1259 | 18 | B | SS.GM.T0011539 | SS.MH.T0007987 | SS.MH.T0007986 | 233.5856 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1260 | 18 | B | SS.GM.T0011540 | SS.MH.T0007988 | SS.MH.T0007987 | 129.1466 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1261 | 18 | B | SS.GM.T0011541 | SS.MH.T0007989 | SS.MH.T0007988 | 76.6861 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1262 | 18 | B | SS.GM.T0011542 | SS.MH.T0007991 | SS.MH.T0007990 | 112.7059 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1263 | 18 | B | SS.GM.T0011543 | SS.MH.T0007992 | SS.MH.T0007991 | 89.6562 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1264 | 18 | B | SS.GM.T0011544 | SS.MH.T0007993 | SS.MH.T0007992 | 256.8451 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1265 | 18 | B | SS.GM.T0011545 | SS.MH.T0007994 | SS.MH.T0007993 | 143.5467 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1266 | 18 | B | SS.GM.T0011546 | SS.MH.T0007995 | SS.MH.T0007994 | 450.3387 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1267 | 18 | B | SS.GM.T0011547 | SS.MH.T0009784 | SS.MH.T0008002 | 148.4261 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1268 | 18 | B | SS.GM.T0011548 | SS.MH.T0008002 | SS.MH.T0008003 | 97.5279 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1269 | 18 | B | SS.GM.T0011549 | SS.MH.T0008003 | SS.MH.T0008004 | 96.1164 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1270 | 18 | B | SS.GM.T0011550 | SS.MH.T0008004 | SS.MH.T0008005 | 98.4592 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1271 | 18 | B | SS.GM.T0011551 | SS.MH.T0008005 | SS.MH.T0008006 | 298.5732 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1272 | 18 | B | SS.GM.T0011552 | SS.MH.T0008006 | SS.MH.T0008007 | 323.8896 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1273 | 18 | B | SS.GM.T0011553 | SS.MH.T0008010 | SS.MH.T0008009 | 197.1014 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1274 | 18 | B | SS.GM.T0011554 | SS.MH.T0008009 | SS.MH.T0008008 | 137.4255 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1275 | 18 | B | SS.GM.T0011555 | SS.MH.T0008011 | SS.MH.T0008010 | 403.5499 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1276 | 18 | B | SS.GM.T0011556 | SS.MH.T0008013 | SS.MH.T0008012 | 95.4216 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1277 | 18 | B | SS.GM.T0011557 | SS.MH.T0009785 | SS.MH.T0008013 | 91.5595 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1278 | 18 | B | SS.GM.T0011558 | SS.MH.T0009788 | SS.MH.T0008020 | 392.6992 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1279 | 18 | B | SS.GM.T0011559 | SS.MH.T0008020 | SS.MH.T0008019 | 201.0072 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1280 | 18 | B | SS.GM.T0011560 | SS.MH.T0008015 | SS.MH.T0008016 | 218.7502 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1281 | 18 | B | SS.GM.T0011561 | SS.MH.T0009787 | SS.MH.T0008014 | 100.2048 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1282 | 18 | B | SS.GM.T0011562 | SS.MH.T0008022 | SS.MH.T0008023 | 252.6901 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1283 | 18 | B | SS.GM.T0011563 | SS.MH.T0008023 | SS.MH.T0008024 | 299.8968 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1284 | 18 | B | SS.GM.T0011564 | SS.MH.T0008027 | SS.MH.T0008026 | 396.9908 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1285 | 18 | B | SS.GM.T0011565 | SS.MH.T0008028 | SS.MH.T0008027 | 252.1044 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1286 | 18 | B | SS.GM.T0011566 | SS.MH.T0008000 | SS.MH.T0008001 | 264.406 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1287 | 18 | B | SS.GM.T0011567 | SS.MH.T0007999 | SS.MH.T0008000 | 127.1746 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1288 | 18 | B | SS.GM.T0011568 | SS.MH.T0007998 | SS.MH.T0007999 | 159.6338 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1289 | 18 | B | SS.GM.T0011569 | SS.MH.T0009783 | SS.MH.T0007997 | 149.8651 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1290 | 18 | B | SS.GM.T0011629 | SS.MH.T0008099 | SS.MH.T0008098 | 385.568 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1291 | 18 | B | SS.GM.T0011630 | SS.MH.T0008098 | SS.MH.T0008097 | 41.9423 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1292 | 18 | B | SS.GM.T0011631 | SS.MH.T0008097 | SS.MH.T0008096 | 326.5793 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1293 | 18 | B | SS.GM.T0011683 | SS.MH.T0008157 | SS.MH.T0008158 | 490.6708 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1294 | 18 | B | SS.GM.T0011684 | SS.MH.T0009802 | SS.MH.T0008157 | 139.9055 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1295 | 18 | B | SS.GM.T0011686 | SS.MH.T0008159 | SS.MH.T0008160 | 111.607 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1296 | 18 | B | SS.GM.T0011687 | SS.MH.T0008160 | SS.MH.T0008161 | 125.2988 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1297 | 18 | B | SS.GM.T0011688 | SS.MH.T0008162 | SS.MH.T0008163 | 57.9984 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1298 | 18 | B | SS.GM.T0011689 | SS.MH.T0008163 | SS.MH.T0008156 | 146.5418 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1299 | 18 | B | SS.GM.T0011690 | SS.MH.T0008156 | SS.MH.T0008155 | 166.3054 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1300 | 18 | C | SS.GM.T0011691 | SS.MH.T0008154 | SS.MH.T0008153 | 82.5559 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1301 | 18 | B | SS.GM.T0011692 | SS.MH.T0008152 | SS.MH.T0008153 | 149.0648 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1302 | 18 | B | SS.GM.T0011693 | SS.MH.T0008151 | SS.MH.T0008152 | 167.078 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1303 | 18 | B | SS.GM.T0011694 | SS.MH.T0009801 | SS.MH.T0008150 | 246.2807 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1304 | 18 | D | SS.GM.T0011695 | SS.MH.T0010457 | SS.MH.T0008123 | 187.9735 | 6 | Construct Cleanout at End Of Line | 3000 | 3000 | Point Repair | Repair
1305 | 18 | B | SS.GM.T0011696 | SS.MH.T0010455 | SS.MH.T0008119 | 414.4474 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1306 | 18 | B | SS.GM.T0011697 | SS.MH.T0008119 | SS.MH.T0008118 | 49.2015 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1307 | 18 | B | SS.GM.T0011698 | SS.MH.T0008118 | SS.MH.T0008117 | 401.1349 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1308 | 18 | B | SS.GM.T0011699 | SS.MH.T0008117 | SS.MH.T0008116 | 200.4186 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1309 | 18 | B | SS.GM.T0011700 | SS.MH.T0010454 | SS.MH.T0008099 | 42.9954 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1310 | 18 | B | SS.GM.T0011701 | SS.MH.T0008134 | SS.MH.T0008133 | 300.0908 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1311 | 18 | B | SS.GM.T0011702 | SS.MH.T0008132 | SS.MH.T0008129 | 103.7456 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1312 | 18 | B | SS.GM.T0011703 | SS.MH.T0015005 | SS.MH.T0008114 | 118.9104 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1313 | 18 | B | SS.GM.T0011704 | SS.MH.T0008123 | SS.MH.T0008122 | 234.7383 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1314 | 18 | B | SS.GM.T0011705 | SS.MH.T0008120 | SS.MH.T0008115 | 192.7959 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1315 | 18 | B | SS.GM.T0011706 | SS.MH.T0008121 | SS.MH.T0008120 | 54.917 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1316 | 18 | C | SS.GM.T0011707 | SS.MH.T0008144 | SS.MH.T0008145 | 69.7946 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1317 | 18 | B | SS.GM.T0011708 | SS.MH.T0008143 | SS.MH.T0008144 | 120.9671 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1318 | 18 | B | SS.GM.T0011709 | SS.MH.T0008142 | SS.MH.T0008143 | 114.5189 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1319 | 18 | B | SS.GM.T0011710 | SS.MH.T0008141 | SS.MH.T0008142 | 317.1507 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1320 | 18 | B | SS.GM.T0011711 | SS.MH.T0009799 | SS.MH.T0008140 | 86.0081 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1321 | 18 | B | SS.GM.T0011712 | SS.MH.T0008146 | SS.MH.T0008145 | 88.0955 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1322 | 18 | B | SS.GM.T0011713 | SS.MH.T0008147 | SS.MH.T0008146 | 246.8567 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1323 | 18 | B | SS.GM.T0011714 | SS.MH.T0008148 | SS.MH.T0008147 | 125.2319 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1324 | 18 | B | SS.GM.T0011715 | SS.MH.T0009800 | SS.MH.T0008149 | 120.5926 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1325 | 18 | B | SS.GM.T0011716 | SS.MH.T0009798 | SS.MH.T0008138 | 95.2534 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1326 | 18 | B | SS.GM.T0011717 | SS.MH.T0008138 | SS.MH.T0008137 | 179.9907 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1327 | 18 | B | SS.GM.T0011718 | SS.MH.T0008137 | SS.MH.T0008136 | 174.8362 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1328 | 18 | B | SS.GM.T0011719 | SS.MH.T0008136 | SS.MH.T0008135 | 169.4695 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1329 | 18 | B | SS.GM.T0011720 | SS.MH.T0008135 | SS.MH.T0008139 | 210.3116 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1330 | 18 | B | SS.GM.T0011721 | SS.MH.T0008165 | SS.MH.T0015731 | 183 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1331 | 18 | C | SS.GM.T0011722 | SS.MH.T0008139 | SS.MH.T0008166 | 93.4903 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1332 | 18 | B | SS.GM.T0011723 | SS.MH.T0010453 | SS.MH.T0008095 | 75.8003 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1333 | 18 | B | SS.GM.T0011724 | SS.MH.T0008127 | SS.MH.T0008126 | 166.8727 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1334 | 18 | B | SS.GM.T0011725 | SS.MH.T0009795 | SS.MH.T0008127 | 59.8353 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1335 | 18 | B | SS.GM.T0011974 | SS.MH.T0009791 | SS.MH.T0008030 | 206.5984 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1336 | 18 | B | SS.GM.T0011975 | SS.MH.T0008030 | SS.MH.T0008031 | 203.0146 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1337 | 18 | B | SS.GM.T0011976 | SS.MH.T0008031 | SS.MH.T0008032 | 153.1305 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1338 | 18 | B | SS.GM.T0011977 | SS.MH.T0008032 | SS.MH.T0008033 | 177.8186 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1339 | 18 | B | SS.GM.T0011978 | SS.MH.T0008033 | SS.MH.T0008034 | 302.4635 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1340 | 18 | C | SS.GM.T0011979 | SS.MH.T0007996 | SS.MH.T0007995 | 309.7031 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1341 | 18 | D | SS.GM.T0012058 | SS.MH.T0008598 | SS.MH.T0009285 | 402.7001 | 10 | Point Repair at 124 ft from 08598 | 4750 | 4750 | Point Repair | Repair
1342 | 18 | B | SS.GM.T0012757 | SS.MH.T0009753 | SS.MH.T0007582 | 82.2042 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1343 | 18 | B | SS.GM.T0012758 | SS.MH.T0007582 | SS.MH.T0007580 | 107.64 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1344 | 18 | B | SS.GM.T0012759 | SS.MH.T0007581 | SS.MH.T0007585 | 58.428 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1345 | 18 | B | SS.GM.T0012760 | SS.MH.T0000568 | SS.MH.T0006425 | 65.3697 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1346 | 18 | B | SS.GM.T0012761 | SS.MH.T0006425 | SS.MH.T0000567 | 46.834 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1347 | 18 | B | SS.GM.T0012762 | SS.MH.T0000566 | SS.MH.T0000567 | 101.6617 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1348 | 18 | B | SS.GM.T0012763 | SS.MH.T0005343 | SS.MH.T0005342 | 77.6143 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1349 | 18 | B | SS.GM.T0012764 | SS.MH.T0005342 | SS.MH.T0000302 | 89.8891 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1350 | 18 | B | SS.GM.T0012765 | SS.MH.T0005341 | SS.MH.T0005340 | 123.4841 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1351 | 18 | B | SS.GM.T0012766 | SS.MH.T0009752 | SS.MH.T0007578 | 118.5582 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1352 | 18 | B | SS.GM.T0012767 | SS.MH.T0007578 | SS.MH.T0007579 | 197.659 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1353 | 18 | B | SS.GM.T0012769 | SS.MH.T0007584 | SS.MH.T0006424 | 219.4487 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1354 | 18 | B | SS.GM.T0012770 | SS.MH.T0006424 | SS.MH.T0005338 | 121.0854 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1355 | 18 | B | SS.GM.T0012771 | SS.MH.T0005338 | SS.MH.T0005337 | 240.7902 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1356 | 18 | D | SS.GM.T0012772 | SS.MH.T0009884 | SS.MH.T0005336 | 87.0049 | 6 | Point Repair at 9 ft from 05336 | 4750 | 4750 | Point Repair | Repair
1357 | 18 | B | SS.GM.T0012828 | SS.MH.T0010460 | SS.MH.T0008125 | 84.3429 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1358 | 18 | D | SS.GM.T0012829 | SS.MH.T0001473 | SS.MH.T0001472 | 364.304 | 8 | Grout Joint at 199 ft from 01473 | 800 | 800 | Grout Joints | Repair
1359 | 18 | B | SS.GM.T0012832 | SS.MH.T0001457 | SS.MH.T0001456 | 338.6001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1360 | 18 | B | SS.GM.T0012834 | SS.MH.T0008699 | SS.MH.T0013275 | 121.8233 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1361 | 18 | B | SS.GM.T0012835 | SS.MH.T0010492 | SS.MH.T0008696 | 352.8942 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1362 | 18 | B | SS.GM.T0012836 | SS.MH.T0008710 | SS.MH.T0008711 | 398.4474 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1363 | 18 | B | SS.GM.T0012837 | SS.MH.T0008712 | SS.MH.T0008706 | 333.8054 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1364 | 18 | B | SS.GM.T0012843 | SS.MH.T0007281 | SS.MH.T0014972 | 406.2282 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1365 | 18 | B | SS.GM.T0012844 | SS.MH.T0006967 | SS.MH.T0006968 | 164.8927 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1366 | 18 | B | SS.GM.T0012845 | SS.MH.T0007283 | SS.MH.T0007284 | 108.7038 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1367 | 18 | B | SS.GM.T0012846 | SS.MH.T0007285 | SS.MH.T0007283 | 213.0688 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1368 | 18 | B | SS.GM.T0012847 | SS.MH.T0006896 | SS.MH.T0006895 | 115.6291 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1369 | 18 | B | SS.GM.T0012848 | SS.MH.T0006899 | SS.MH.T0006898 | 302.9012 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1370 | 18 | B | SS.GM.T0012849 | SS.MH.T0006898 | SS.MH.T0006897 | 301.7259 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1371 | 18 | B | SS.GM.T0012850 | SS.MH.T0009299 | SS.MH.T0006899 | 245.3886 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1372 | 18 | B | SS.GM.T0012851 | SS.MH.T0006895 | SS.MH.T0006966 | 36.7955 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1373 | 18 | B | SS.GM.T0012852 | SS.MH.T0007286 | SS.MH.T0007285 | 102.6883 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1374 | 18 | B | SS.GM.T0012863 | SS.MH.T0009887 | SS.MH.T0000303 | 74.8945 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1375 | 18 | B | SS.GM.T0012866 | SS.MH.T0009866 | SS.MH.T0000516 | 59.6024 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1376 | 18 | B | SS.GM.T0012867 | SS.MH.T0000519 | SS.MH.T0000520 | 77.4956 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1377 | 18 | B | SS.GM.T0012877 | SS.MH.T0006890 | SS.MH.T0000659 | 134.0361 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1378 | 18 | B | SS.GM.T0012878 | SS.MH.T0000659 | SS.MH.T0005334 | 171.596 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1379 | 18 | D | SS.GM.T0012879 | SS.MH.T0005332 | SS.MH.T0005330 | 380.6832 | 15 | 15" CIPP - 2 svc | 32454.6528 | 32454.6528 | Cured In Place Pipe Liner | Rehab
1380 | 18 | D | SS.GM.T0012880 | SS.MH.T0005330 | SS.MH.T0005331 | 114.5445 | 15 | Point Repair at 39 ft from 05330 | 4750 | 4750 | Point Repair | Repair
1381 | 18 | B | SS.GM.T0012899 | SS.MH.T0005442 | SS.MH.T0007984 | 320.4543 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1382 | 18 | D | SS.GM.T0012900 | SS.MH.T0005443 | SS.MH.T0005441 | 270.4557 | 8 | Locate and Expose 13056; Clean and CCTV | 2431.8228 | 2431.8228 | Access; Clean and Inspection | Inspect
1383 | 18 | D | SS.GM.T0012902 | SS.MH.T0006154 | SS.MH.T0006153 | 199.6464 | 15 | 15" CIPP - 0 svc | 15971.7081 | 15971.7081 | Cured In Place Pipe Liner | Rehab
1384 | 18 | B | SS.GM.T0012932 | SS.MH.T0015160 | SS.MH.T0001471 | 27.5001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1385 | 18 | B | SS.GM.T0012943 | SS.MH.T0008702 | SS.MH.T0008703 | 395.7654 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1386 | 18 | B | SS.GM.T0012944 | SS.MH.T0008704 | SS.MH.T0008705 | 127.1867 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1387 | 18 | B | SS.GM.T0012945 | SS.MH.T0008707 | SS.MH.T0008706 | 391.8611 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1388 | 18 | B | SS.GM.T0012972 | SS.MH.T0007712 | SS.MH.T0007741 | 296.2275 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1389 | 18 | D | SS.GM.T0012995 | SS.MH.T0005163 | SS.MH.T0013309 | 477.5874 | 6 | Point Repair at 35 and 344 ft from 05163 | 9500 | 9500 | Point Repair | Repair
1390 | 18 | B | SS.GM.T0013161 | SS.MH.T0012989 | SS.MH.T0012990 | 294.8586 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1391 | 18 | B | SS.GM.T0013176 | SS.MH.T0013015 | SS.MH.T0013016 | 184.1242 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1392 | 18 | B | SS.GM.T0013177 | SS.MH.T0013022 | SS.MH.T0013023 | 106.123 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1393 | 18 | B | SS.GM.T0013232 | SS.MH.T0012992 | SS.MH.T0012994 | 75.3568 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1394 | 18 | B | SS.GM.T0013233 | SS.MH.T0012991 | SS.MH.T0012992 | 160.8607 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1395 | 18 | B | SS.GM.T0013234 | SS.MH.T0012990 | SS.MH.T0012991 | 108.4463 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1396 | 18 | B | SS.GM.T0013235 | SS.MH.T0014476 | SS.MH.T0012989 | 159.973 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1397 | 18 | B | SS.GM.T0013236 | SS.MH.T0012994 | SS.MH.T0013020 | 118.0257 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1398 | 18 | B | SS.GM.T0013237 | SS.MH.T0013020 | SS.MH.T0013021 | 161.0951 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1399 | 18 | B | SS.GM.T0013238 | SS.MH.T0013021 | SS.MH.T0013022 | 84.6437 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1400 | 18 | B | SS.GM.T0013239 | SS.MH.T0012993 | SS.MH.T0012992 | 45.9148 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1401 | 18 | B | SS.GM.T0013240 | SS.MH.T0013019 | SS.MH.T0012993 | 195.8127 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1402 | 18 | B | SS.GM.T0013241 | SS.MH.T0013018 | SS.MH.T0013019 | 118.4127 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1403 | 18 | B | SS.GM.T0013242 | SS.MH.T0013017 | SS.MH.T0013018 | 154.1204 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1404 | 18 | B | SS.GM.T0013243 | SS.MH.T0013016 | SS.MH.T0013017 | 160.6417 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1405 | 18 | B | SS.GM.T0013244 | SS.MH.T0013014 | SS.MH.T0013015 | 151.7313 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1406 | 18 | D | SS.GM.T0013273 | SS.MH.T0011226 | SS.MH.T0013096 | 393.2816 | 6 | Point Repair at 75 and 81 ft from 13096 | 9500 | 9500 | Point Repair | Repair
1407 | 18 | B | SS.GM.T0013276 | SS.MH.T0013105 | SS.MH.T0003424 | 264.2827 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1408 | 18 | B | SS.GM.T0013277 | SS.MH.T0013106 | SS.MH.T0013105 | 232.7035 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1409 | 18 | B | SS.GM.T0013293 | SS.MH.T0013123 | SS.MH.T0013124 | 289.7724 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1410 | 18 | D | SS.GM.T0013367 | SS.MH.T0006109 | SS.MH.T0006110 | 157.7413 | 6 | Burst to 8" - 0 svc | 10253.1852 | 10253.1852 | Pipe Burst or Replace | Replace
1411 | 18 | B | SS.GM.T0013370 | SS.MH.T0013187 | SS.MH.T0013186 | 14.8874 | 18 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1412 | 18 | B | SS.GM.T0013372 | SS.MH.T0006119 | SS.MH.T0013185 | 12.1541 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1413 | 18 | D | SS.GM.T0013373 | SS.MH.T0013185 | SS.MH.T0013186 | 16.9109 | 10 | Point Repair at 13 ft from 13185 | 4750 | 4750 | Point Repair | Repair
1414 | 18 | B | SS.GM.T0013375 | SS.MH.T0006121 | SS.MH.T0013188 | 46.4257 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1415 | 18 | B | SS.GM.T0013376 | SS.MH.T0013188 | SS.MH.T0013189 | 99.3715 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1416 | 18 | D | SS.GM.T0013377 | SS.MH.T0010988 | SS.MH.T0006138 | 10.4361 | 6 | Burst to 8" - 0 svc | 678.3455 | 678.3455 | Pipe Burst or Replace | Replace
1417 | 18 | C | SS.GM.T0013378 | SS.MH.T0013192 | SS.MH.T0013191 | 139.7866 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1418 | 18 | C | SS.GM.T0013379 | SS.MH.T0006130 | SS.MH.T0013192 | 31.8771 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1419 | 18 | C | SS.GM.T0013380 | SS.MH.T0006134 | SS.MH.T0006130 | 206.1976 | 16 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1420 | 18 | B | SS.GM.T0013382 | SS.MH.T0013209 | SS.MH.T0015733 | 319.0637 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1421 | 18 | B | SS.GM.T0013385 | SS.MH.T0013207 | SS.MH.T0013209 | 314.4346 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1422 | 18 | B | SS.GM.T0013386 | SS.MH.T0013013 | SS.MH.T0013212 | 134.9629 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1423 | 18 | B | SS.GM.T0013387 | SS.MH.T0013213 | SS.MH.T0006798 | 366.0007 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1424 | 18 | B | SS.GM.T0013388 | SS.MH.T0013194 | SS.MH.T0004361 | 118.6615 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1425 | 18 | B | SS.GM.T0013389 | SS.MH.T0015173 | SS.MH.T0006385 | 9.1773 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1426 | 18 | B | SS.GM.T0013390 | SS.MH.T0013211 | SS.MH.T0006389 | 127.1064 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1427 | 18 | A | SS.GM.T0013391 | SS.MH.T0013217 | SS.MH.T0013215 | 89.0253 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1428 | 18 | A | SS.GM.T0013392 | SS.MH.T0013210 | SS.MH.T0013214 | 257.203 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1429 | 18 | A | SS.GM.T0013393 | SS.MH.T0013215 | SS.MH.T0013219 | 65.4891 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1430 | 18 | A | SS.GM.T0013394 | SS.MH.T0013214 | SS.MH.T0013215 | 92.4501 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1431 | 18 | A | SS.GM.T0013395 | SS.MH.T0013216 | SS.MH.T0013217 | 77.134 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1432 | 18 | D | SS.GM.T0013396 | SS.MH.T0013205 | SS.MH.T0013206 | 213.5094 | 8 | Point Repair at 188 and 121 ft from 13205 | 9500 | 9500 | Point Repair | Repair
1433 | 18 | B | SS.GM.T0013397 | SS.MH.T0007079 | SS.MH.T0013208 | 101.9835 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1434 | 18 | A | SS.GM.T0013398 | SS.MH.T0013220 | SS.MH.T0007672 | 92.6697 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1435 | 18 | D | SS.GM.T0013420 | SS.MH.T0005422 | SS.MH.T0009277 | 259.7341 | 6 | Burst to 8" - 0 svc | 16882.7193 | 16882.7193 | Pipe Burst or Replace | Replace
1436 | 18 | C | SS.GM.T0013421 | SS.MH.T0003667 | SS.MH.T0004151 | 19.7866 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1437 | 18 | D | SS.GM.T0013427 | SS.MH.T0013948 | SS.MH.T0000323 | 227.6438 | 6 | Construct Cleanout at End Of Line | 3000 | 3000 | Point Repair | Repair
1438 | 18 | B | SS.GM.T0013452 | SS.MH.T0013278 | SS.MH.T0006976 | 50.3751 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1439 | 18 | D | SS.GM.T0013455 | SS.MH.T0013277 | SS.MH.T0013279 | 281.3647 | 12 | Point Repair at 166 ft from 13279 | 4750 | 4750 | Point Repair | Repair
1440 | 18 | B | SS.GM.T0013456 | SS.MH.T0001472 | SS.MH.T0006977 | 50.99 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1441 | 18 | D | SS.GM.T0013457 | SS.MH.T0005541 | SS.MH.T0013284 | 325.5508 | 8 | Replace section from 05541 to 20 ft from 05541 | 2600 | 2600 | Replace Section | Repair
1442 | 18 | D | SS.GM.T0013458 | SS.MH.T0005536 | SS.MH.T0013286 | 209.2345 | 6 | Point Repair at 113 ft from 05536 | 4750 | 4750 | Point Repair | Repair
1443 | 18 | B | SS.GM.T0013459 | SS.MH.T0013286 | SS.MH.T0013287 | 40.1191 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1444 | 18 | B | SS.GM.T0013460 | SS.MH.T0013287 | SS.MH.T0013288 | 41.8314 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1445 | 18 | D | SS.GM.T0013461 | SS.MH.T0013285 | SS.MH.T0015026 | 56.79 | 12 | Burst to 18" - 1 svc | 6395.0457 | 6395.0457 | Pipe Burst or Replace | Replace
1446 | 18 | B | SS.GM.T0013463 | SS.MH.T0013292 | SS.MH.T0000569 | 49.7267 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1447 | 18 | B | SS.GM.T0013464 | SS.MH.T0000520 | SS.MH.T0013294 | 215.2059 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1448 | 18 | B | SS.GM.T0013465 | SS.MH.T0013294 | SS.MH.T0013293 | 148.5312 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1449 | 18 | B | SS.GM.T0013466 | SS.MH.T0013295 | SS.MH.T0015176 | 212.0959 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1450 | 18 | B | SS.GM.T0013467 | SS.MH.T0015176 | SS.MH.T0005312 | 47.1648 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1451 | 18 | A | SS.GM.T0013498 | SS.MH.T0001456 | SS.MH.T0001458 | 103.4244 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1452 | 18 | B | SS.GM.T0013499 | SS.MH.T0001458 | SS.MH.T0001472 | 117.5661 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1453 | 18 | A | SS.GM.T0013511 | SS.MH.T0013280 | SS.MH.T0001456 | 117.5642 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1454 | 18 | B | SS.GM.T0013514 | SS.MH.T0009771 | SS.MH.T0013282 | 347.5844 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1455 | 18 | B | SS.GM.T0013525 | SS.MH.T0013128 | SS.MH.T0013335 | 177.077 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1456 | 18 | B | SS.GM.T0013526 | SS.MH.T0013126 | SS.MH.T0013128 | 267.7267 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1457 | 18 | B | SS.GM.T0013527 | SS.MH.T0013124 | SS.MH.T0013125 | 194.2036 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1458 | 18 | B | SS.GM.T0013529 | SS.MH.T0013121 | SS.MH.T0013123 | 169.7731 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1459 | 18 | B | SS.GM.T0013530 | SS.MH.T0013125 | SS.MH.T0013126 | 150.0017 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1460 | 18 | B | SS.GM.T0013531 | SS.MH.T0013127 | SS.MH.T0013128 | 21.5152 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1461 | 18 | C | SS.GM.T0013537 | SS.MH.T0004372 | SS.MH.T0004370 | 390.6813 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1462 | 18 | B | SS.GM.T0013585 | SS.MH.T0013503 | SS.MH.T0013504 | 361.0362 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1463 | 18 | C | SS.GM.T0013590 | SS.MH.T0013560 | SS.MH.T0005178 | 171.435 | 6 | Point Repair at 85 and 126 ft from 05178 | 9500 | 0 | Monitor in CMOM | None
1464 | 18 | B | SS.GM.T0013613 | SS.MH.T0015800 | SS.MH.T0013127 | 204.1331 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1465 | 18 | B | SS.GM.T0013615 | SS.MH.T0015734 | SS.MH.T0013959 | 205.6197 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1466 | 18 | B | SS.GM.T0013616 | SS.MH.T0013871 | SS.MH.T0013872 | 196.1497 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1467 | 18 | B | SS.GM.T0013617 | SS.MH.T0013870 | SS.MH.T0013871 | 157.0765 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1468 | 18 | B | SS.GM.T0013618 | SS.MH.T0014727 | SS.MH.T0013870 | 212.7373 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1469 | 18 | B | SS.GM.T0013619 | SS.MH.T0013335 | Ss.Ls.T0000042 | 27.951 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1470 | 18 | A | SS.GM.T0013667 | SS.MH.T0013498 | SS.MH.T0013499 | 213.9706 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1471 | 18 | A | SS.GM.T0013668 | SS.MH.T0013499 | SS.MH.T0013500 | 360.7381 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1472 | 18 | B | SS.GM.T0013669 | SS.MH.T0013500 | SS.MH.T0013502 | 239.7223 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1473 | 18 | B | SS.GM.T0013670 | SS.MH.T0013502 | SS.MH.T0013503 | 375.8817 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1474 | 18 | B | SS.GM.T0013671 | SS.MH.T0013504 | SS.MH.T0013121 | 176.8192 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1475 | 18 | C | SS.GM.T0013679 | SS.MH.T0013654 | SS.MH.T0005195 | 162.1218 | 6 | Assign to high frequency cleaning - Grease | 486.3655 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
1476 | 18 | A | SS.GM.T0013693 | SS.MH.T0013673 | SS.MH.T0013503 | 374.2125 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1477 | 18 | A | SS.GM.T0013694 | SS.MH.T0013674 | SS.MH.T0013673 | 113.8018 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1478 | 18 | A | SS.GM.T0013718 | SS.MH.T0014981 | SS.MH.T0013710 | 96.512 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1479 | 18 | A | SS.GM.T0013719 | SS.MH.T0013711 | SS.MH.T0001457 | 351.0487 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1480 | 18 | B | SS.GM.T0013807 | SS.MH.T0005561 | SS.MH.T0013473 | 27.6643 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1481 | 18 | B | SS.GM.T0013809 | SS.MH.T0006136 | SS.MH.T0015111 | 128.5445 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1482 | 18 | B | SS.GM.T0013814 | SS.MH.T0013505 | SS.MH.T0013126 | 185.4665 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1483 | 18 | B | SS.GM.T0013826 | SS.MH.T0013501 | SS.MH.T0013500 | 20.7585 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1484 | 18 | A | SS.GM.T0013865 | SS.MH.T0013218 | SS.MH.T0013219 | 163.0224 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1485 | 18 | A | SS.GM.T0013874 | SS.MH.T0013831 | SS.MH.T0013830 | 151.3043 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1486 | 18 | A | SS.GM.T0013875 | SS.MH.T0013830 | SS.MH.T0013218 | 142.7949 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1487 | 18 | B | SS.GM.T0013877 | SS.MH.T0006234 | SS.MH.T0013308 | 14.8312 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1488 | 18 | C | SS.GM.T0013882 | SS.MH.T0013834 | SS.MH.T0000295 | 102.0307 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1489 | 18 | B | SS.GM.T0013954 | SS.MH.T0013974 | SS.MH.T0006127 | 293.0979 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1490 | 18 | B | SS.GM.T0013970 | SS.MH.T0013869 | SS.MH.T0013960 | 201.8465 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1491 | 18 | B | SS.GM.T0014006 | SS.MH.T0013959 | SS.MH.T0013873 | 27.0358 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1492 | 18 | B | SS.GM.T0014007 | SS.MH.T0013960 | SS.MH.T0013868 | 69.9001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1493 | 18 | B | SS.GM.T0014008 | SS.MH.T0013961 | SS.MH.T0013869 | 38.7919 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1494 | 18 | B | SS.GM.T0014009 | SS.MH.T0013868 | SS.MH.T0013505 | 190.2551 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1495 | 18 | B | SS.GM.T0014010 | SS.MH.T0013962 | SS.MH.T0013868 | 265.9935 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1496 | 18 | B | SS.GM.T0014021 | SS.MH.T0013978 | SS.MH.T0013979 | 87.9999 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1497 | 18 | B | SS.GM.T0014022 | SS.MH.T0013979 | SS.MH.T0013980 | 213.4992 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1498 | 18 | B | SS.GM.T0014023 | SS.MH.T0013980 | SS.MH.T0013981 | 206.5001 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1499 | 18 | B | SS.GM.T0014024 | SS.MH.T0013981 | SS.MH.T0013982 | 94.3 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1500 | 18 | B | SS.GM.T0014025 | SS.MH.T0013982 | SS.MH.T0015718 | 115.4143 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1501 | 18 | B | SS.GM.T0014028 | SS.MH.T0013986 | SS.MH.T0000292 | 286.3902 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1502 | 18 | D | SS.GM.T0014031 | SS.MH.T0013992 | SS.MH.T0004278 | 535.3812 | 8 | Point Repair at 161 ft from 13992 and Add to Root Removal Schedule | 5820.7624 | 5820.7624 | Point Repair and Add to Root Removal Program in CMOM | Repair
1503 | 18 | D | SS.GM.T0014033 | SS.MH.T0004344 | SS.MH.T0013994 | 643.1355 | 8 | Replace section 30 to 70 ft from 04344. | 5200 | 5200 | Replace Section | Repair
1504 | 18 | D | SS.GM.T0014034 | SS.MH.T0005544 | SS.MH.T0013995 | 441.225 | 6 | Burst to 8" - 8 svc | 36679.6266 | 36679.6266 | Pipe Burst or Replace | Replace
1505 | 18 | B | SS.GM.T0014111 | SS.MH.T0013796 | SS.MH.T0012769 | 139.31 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1506 | 18 | B | SS.GM.T0014323 | SS.MH.T0014432 | SS.MH.T0015764 | 271.007 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1507 | 18 | C | SS.GM.T0014324 | SS.MH.T0014431 | SS.MH.T0014432 | 61.1697 | 6 | Add to Root Removal Schedule | 122.3395 | 0 | Add to Root Removal Program in CMOM | Maintenance
1508 | 18 | D | SS.GM.T0014401 | SS.MH.T0005534 | SS.MH.T0014477 | 458.4323 | 6 | Point Repair at 36 and 57 ft from 05534 | 9500 | 9500 | Point Repair | Repair
1509 | 18 | D | SS.GM.T0014496 | SS.MH.T0005154 | SS.MH.T0005155 | 345.049 | 6 | Point Repair at 327 ft from 05154 | 4750 | 4750 | Point Repair | Repair
1510 | 18 | B | SS.GM.T0014516 | SS.MH.T0014625 | SS.MH.T0014624 | 346.9624 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1511 | 18 | B | SS.GM.T0014517 | SS.MH.T0014624 | SS.MH.T0014623 | 292.6013 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1512 | 18 | B | SS.GM.T0014524 | SS.MH.T0014632 | SS.MH.T0014621 | 4.9211 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1513 | 18 | B | SS.GM.T0014525 | SS.MH.T0014636 | SS.MH.T0014620 | 125.7515 | 6 | Assign to high frequency cleaning | 377.2545 | 0 | Add to High Frequency Cleaning in CMOM | Maintenance
1514 | 18 | B | SS.GM.T0014837 | SS.MH.T0014938 | SS.MH.T0006374 | 19.4206 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1515 | 18 | B | SS.GM.T0014838 | SS.MH.T0014958 | SS.MH.T0003504 | 62.9995 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1516 | 18 | B | SS.GM.T0014839 | SS.MH.T0014955 | SS.MH.T0003424 | 39.8855 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1517 | 18 | D | SS.GM.T0014843 | SS.MH.T0014957 | SS.MH.T0003442 | 539.1347 | 8 | Burst to 8" - 5 svc | 40043.7548 | 40043.7548 | Pipe Burst or Replace | Replace
1518 | 18 | C | SS.GM.T0014845 | SS.MH.T0012314 | SS.MH.T0014963 | 251.0168 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1519 | 18 | D | SS.GM.T0014846 | SS.MH.T0014964 | SS.MH.T0005376 | 339.7005 | 6 | Point Repair at 33, 59, 105, 128, 196 and 302 ft from 14964 | 28500 | 28500 | Point Repair | Repair
1520 | 18 | B | SS.GM.T0014847 | SS.MH.T0014965 | SS.MH.T0006113 | 40.5869 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1521 | 18 | B | SS.GM.T0014848 | SS.MH.T0014966 | SS.MH.T0006240 | 294.4173 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1522 | 18 | E | SS.GM.T0014849 | SS.MH.T0014971 | SS.MH.T0013986 | 224.607 | 6 | Point Repair at 122 and 158 ft from 13986 | 9500 | 9500 | Point Repair | Repair
1523 | 18 | B | SS.GM.T0014850 | SS.MH.T0014972 | SS.MH.T0007286 | 378.5174 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1524 | 18 | B | SS.GM.T0014851 | SS.MH.T0014969 | SS.MH.T0014968 | 175.6135 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1525 | 18 | D | SS.GM.T0014852 | SS.MH.T0014968 | SS.MH.T0011011 | 267.9371 | 6 | Point Repair at 123 ft from 14968 | 4750 | 4750 | Point Repair | Repair
1526 | 18 | B | SS.GM.T0014853 | SS.MH.T0014970 | SS.MH.T0014969 | 132.1725 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1527 | 18 | B | SS.GM.T0014861 | SS.MH.T0014979 | SS.MH.T0014978 | 7.5979 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1528 | 18 | B | SS.GM.T0014862 | SS.MH.T0014978 | SS.MH.T0004294 | 128.0896 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1529 | 18 | B | SS.GM.T0014868 | SS.MH.T0014996 | SS.MH.T0014994 | 464.9612 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1530 | 18 | D | SS.GM.T0014869 | SS.MH.T0014994 | SS.MH.T0014993 | 313.7998 | 8 | Replace - 1 svc | 41793.9753 | 41793.9753 | Replace | Replace
1531 | 18 | D | SS.GM.T0014871 | SS.MH.T0014995 | SS.MH.T0014994 | 415.9322 | 8 | Replace - 8 svc | 62071.1812 | 62071.1812 | Replace | Replace
1532 | 18 | B | SS.GM.T0014873 | SS.MH.T0014980 | SS.MH.T0000337 | 317.5274 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1533 | 18 | C | SS.GM.T0014874 | SS.MH.T0014988 | SS.MH.T0004248 | 386.1765 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1534 | 18 | B | SS.GM.T0014875 | SS.MH.T0014990 | SS.MH.T0014989 | 22.0543 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1535 | 18 | B | SS.GM.T0014876 | SS.MH.T0014989 | SS.MH.T0005369 | 154.2497 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1536 | 18 | B | SS.GM.T0014879 | SS.MH.T0014983 | SS.MH.T0015722 | 1.9999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1537 | 18 | D | SS.GM.T0014897 | SS.MH.T0014998 | SS.MH.T0005608 | 149.6685 | 8 | Point Repair at 50 ft from 05608 | 4750 | 4750 | Point Repair | Repair
1538 | 18 | A | SS.GM.T0014898 | SS.MH.T0014999 | SS.MH.T0005609 | 11.8097 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1539 | 18 | B | SS.GM.T0014899 | SS.MH.T0015000 | SS.MH.T0006900 | 62.8971 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1540 | 18 | B | SS.GM.T0014903 | SS.MH.T0008124 | SS.MH.T0015005 | 52.3302 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1541 | 18 | A | SS.GM.T0014906 | SS.MH.T0015010 | SS.MH.T0015009 | 176.5408 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1542 | 18 | A | SS.GM.T0014907 | SS.MH.T0015009 | SS.MH.T0015008 | 201.944 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1543 | 18 | B | SS.GM.T0014908 | SS.MH.T0000567 | SS.MH.T0015011 | 74.1524 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1544 | 18 | B | SS.GM.T0014910 | SS.MH.T0013915 | SS.MH.T0015015 | 65.0722 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1545 | 18 | B | SS.GM.T0014911 | SS.MH.T0015015 | SS.MH.T0015014 | 118.4602 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1546 | 18 | B | SS.GM.T0014912 | SS.MH.T0015014 | SS.MH.T0015013 | 109.7784 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1547 | 18 | B | SS.GM.T0014915 | SS.MH.T0004133 | SS.MH.T0015020 | 40.3907 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1548 | 18 | A | SS.GM.T0014916 | SS.MH.T0015019 | SS.MH.T0015018 | 381.7457 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1549 | 18 | B | SS.GM.T0014917 | SS.MH.T0015018 | SS.MH.T0003449 | 227.0548 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1550 | 18 | A | SS.GM.T0014918 | SS.MH.T0003580 | SS.MH.T0015018 | 81.4969 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1551 | 18 | B | SS.GM.T0014921 | SS.MH.T0015025 | SS.MH.T0015024 | 129.0428 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1552 | 18 | B | SS.GM.T0014922 | SS.MH.T0015024 | SS.MH.T0015023 | 149.1082 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1553 | 18 | B | SS.GM.T0014923 | SS.MH.T0015023 | SS.MH.T0005445 | 315.8432 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1554 | 18 | B | SS.GM.T0014924 | SS.MH.T0015026 | SS.MH.T0005539 | 21.2375 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1555 | 18 | B | SS.GM.T0014925 | SS.MH.T0015027 | SS.MH.T0006211 | 39.4806 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1556 | 18 | D | SS.GM.T0014928 | SS.MH.T0015030 | SS.MH.T0012387 | 196.2057 | 6 | Grout Joint at 63 ft from 12387 | 800 | 800 | Grout Joints | Repair
1557 | 18 | B | SS.GM.T0014937 | SS.MH.T0015040 | SS.MH.T0006983 | 50.4235 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1558 | 18 | B | SS.GM.T0014938 | SS.MH.T0015045 | SS.MH.T0015044 | 61.9983 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1559 | 18 | B | SS.GM.T0014939 | SS.MH.T0015044 | SS.MH.T0015043 | 232.1388 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1560 | 18 | B | SS.GM.T0014940 | SS.MH.T0015043 | SS.MH.T0015042 | 45.1951 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1561 | 18 | B | SS.GM.T0014941 | SS.MH.T0015042 | SS.MH.T0015041 | 190.5207 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1562 | 18 | B | SS.GM.T0014942 | SS.MH.T0015041 | SS.MH.T0015040 | 155.741 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1563 | 18 | B | SS.GM.T0014943 | SS.MH.T0015047 | SS.MH.T0015046 | 76.1823 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1564 | 18 | B | SS.GM.T0014944 | SS.MH.T0015046 | SS.MH.T0015041 | 248.9704 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1565 | 18 | A | SS.GM.T0014946 | SS.MH.T0013219 | SS.MH.T0015091 | 257.8617 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1566 | 18 | D | SS.GM.T0014949 | SS.MH.T0015094 | SS.MH.T0000324 | 509.3116 | 6 | Burst to 8" - 5 svc | 38105.253 | 38105.253 | Pipe Burst or Replace | Replace
1567 | 18 | D | SS.GM.T0014950 | SS.MH.T0000324 | SS.MH.T0000323 | 404.5365 | 6 | Point Repair at 11 and 210 ft from 00324 | 9500 | 9500 | Point Repair | Repair
1568 | 18 | B | SS.GM.T0014951 | SS.MH.T0015095 | SS.MH.T0013287 | 104.9832 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1569 | 18 | C | SS.GM.T0014952 | SS.MH.T0015097 | SS.MH.T0005411 | 34.3854 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1570 | 18 | A | SS.GM.T0014958 | SS.MH.T0015109 | SS.MH.T0015108 | 48.5279 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1571 | 18 | B | SS.GM.T0014959 | SS.MH.T0015108 | SS.MH.T0015107 | 57.799 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1572 | 18 | B | SS.GM.T0014960 | SS.MH.T0015107 | SS.MH.T0015106 | 240.3106 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1573 | 18 | B | SS.GM.T0014961 | SS.MH.T0015106 | SS.MH.T0004357 | 70.1973 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1574 | 18 | C | SS.GM.T0014963 | SS.MH.T0015112 | SS.MH.T0006136 | 11.4621 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1575 | 18 | C | SS.GM.T0014964 | SS.MH.T0015111 | SS.MH.T0013497 | 55.5627 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1576 | 18 | C | SS.GM.T0014965 | SS.MH.T0015110 | SS.MH.T0015479 | 82.1361 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1577 | 18 | B | SS.GM.T0014966 | SS.MH.T0006135 | SS.MH.T0015113 | 10.509 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1578 | 18 | D | SS.GM.T0014968 | SS.MH.T0015098 | SS.MH.T0005223 | 19.7377 | 6 | Point Repair at 11 ft from 05223 | 4750 | 4750 | Point Repair | Repair
1579 | 18 | B | SS.GM.T0014970 | SS.MH.T0011751 | SS.MH.T0015100 | 247.5101 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1580 | 18 | B | SS.GM.T0014972 | SS.MH.T0015101 | SS.MH.T0011751 | 222.9984 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1581 | 18 | C | SS.GM.T0014973 | SS.MH.T0006401 | SS.MH.T0015103 | 70.7091 | 6 | Point Repair at 65 ft from 15103 | 4750 | 0 | Monitor in CMOM | None
1582 | 18 | D | SS.GM.T0014974 | SS.MH.T0015104 | SS.MH.T0006401 | 98.1367 | 6 | Point Repair at 100 ft from 06401 | 4750 | 4750 | Point Repair | Repair
1583 | 18 | B | SS.GM.T0014975 | SS.MH.T0015105 | SS.MH.T0006095 | 146.1406 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1584 | 18 | C | SS.GM.T0015010 | SS.MH.T0012346 | SS.MH.T0015240 | 288.0719 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1585 | 18 | B | SS.GM.T0015033 | SS.MH.T0011108 | SS.MH.T0015194 | 177.7626 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1586 | 18 | C | SS.GM.T0015034 | SS.MH.T0015195 | SS.MH.T0006385 | 149.9999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1587 | 18 | A | SS.GM.T0015067 | SS.MH.T0015202 | SS.MH.T0015201 | 14.0859 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1588 | 18 | A | SS.GM.T0015068 | SS.MH.T0015201 | SS.MH.T0010419 | 200.468 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1589 | 18 | D | SS.GM.T0015069 | SS.MH.T0015439 | SS.MH.T0005263 | 92.8681 | 12 | 12" CIPP - 0 svc | 6500.7656 | 6500.7656 | Cured In Place Pipe Liner | Rehab
1590 | 18 | B | SS.GM.T0015070 | SS.MH.T0015440 | SS.MH.T0015439 | 14.5 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1591 | 18 | C | SS.GM.T0015094 | SS.MH.T0015309 | SS.MH.T0004368 | 158.5143 | 8 | Point Repair at 38 ft from 15309 | 4750 | 0 | Monitor in CMOM | None
1592 | 18 | B | SS.GM.T0015096 | SS.MH.T0013279 | SS.MH.T0015436 | 118.1983 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1593 | 18 | D | SS.GM.T0015098 | SS.MH.T0015313 | SS.MH.T0007914 | 105.2895 | 6 | Point Repair at 45 ft from 07914 and Access; Clean and Inspection | 5171.1581 | 5171.1581 | Point Repair and Access; Clean and Inspection | Repair
1594 | 18 | B | SS.GM.T0015100 | SS.MH.T0015437 | SS.MH.T0006226 | 97.6813 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1595 | 18 | B | SS.GM.T0015101 | SS.MH.T0015316 | SS.MH.T0015437 | 11.2443 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1596 | 18 | B | SS.GM.T0015115 | SS.MH.T0015211 | SS.MH.T0009954 | 123.9922 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1597 | 18 | D | SS.GM.T0015117 | SS.MH.T0015208 | SS.MH.T0013213 | 199.9998 | 8 | Burst to 8" - 1 svc | 13999.9879 | 13999.9879 | Pipe Burst or Replace | Replace
1598 | 18 | D | SS.GM.T0015118 | SS.MH.T0015207 | SS.MH.T0013212 | 280.3046 | 6 | Burst to 8" - 1 svc | 19219.7991 | 19219.7991 | Pipe Burst or Replace | Replace
1599 | 18 | B | SS.GM.T0015119 | SS.MH.T0015205 | SS.MH.T0015204 | 234.5721 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1600 | 18 | C | SS.GM.T0015120 | SS.MH.T0015206 | SS.MH.T0015205 | 400.9847 | 6 | Point Repair at 397 ft from 15206 | 4750 | 0 | Monitor in CMOM | None
1601 | 18 | B | SS.GM.T0015121 | SS.MH.T0005279 | SS.MH.T0015203 | 77.4189 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1602 | 18 | B | SS.GM.T0015122 | SS.MH.T0005280 | SS.MH.T0015204 | 66.3019 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1603 | 18 | A | SS.GM.T0015123 | SS.MH.T0015210 | SS.MH.T0015209 | 61.0001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1604 | 18 | A | SS.GM.T0015124 | SS.MH.T0015209 | SS.MH.T0010420 | 200.0409 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1605 | 18 | C | SS.GM.T0015170 | SS.MH.T0007025 | SS.MH.T0015477 | 204.6632 | 12 | Add to Root Removal Schedule | 409.3264 | 0 | Add to Root Removal Program in CMOM | Maintenance
1606 | 18 | B | SS.GM.T0015183 | SS.MH.T0015481 | SS.MH.T0000650 | 388.9812 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1607 | 18 | B | SS.GM.T0015184 | SS.MH.T0006974 | SS.MH.T0000652 | 273.5753 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1608 | 18 | B | SS.GM.T0015187 | SS.MH.T0015031 | SS.MH.T0013014 | 130.6591 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1609 | 18 | B | SS.GM.T0015274 | SS.MH.T0011508 | SS.MH.T0015279 | 585.6744 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1610 | 18 | B | SS.GM.T0015277 | SS.MH.T0006892 | SS.MH.T0015628 | 177.8048 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1611 | 18 | B | SS.GM.T0015285 | SS.MH.T0007585 | SS.MH.T0015636 | 126.1429 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1612 | 18 | B | SS.GM.T0015286 | SS.MH.T0015637 | SS.MH.T0013292 | 168.6541 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1613 | 18 | B | SS.GM.T0015296 | SS.MH.T0015281 | SS.MH.T0006893 | 70.5582 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1614 | 18 | D | SS.GM.T0015323 | SS.MH.T0015646 | SS.MH.T0005359 | 390.1413 | 6 | Point Repair at 89 and 263 ft from 05359 and Add to Root Removal Schedule | 10280.2825 | 10280.2825 | Point Repair and Add to Root Removal Program in CMOM | Repair
1615 | 18 | D | SS.GM.T0015407 | SS.MH.T0015763 | SS.MH.T0003445 | 53.7448 | 6 | Burst to 8" - 1 svc | 4493.4108 | 4493.4108 | Pipe Burst or Replace | Replace
1616 | 18 | B | SS.GM.T0015418 | SS.MH.T0015714 | SS.MH.T0006382 | 104.1322 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1617 | 18 | A | SS.GM.T0015419 | SS.MH.T0015764 | SS.MH.T0015714 | 21.569 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1618 | 18 | B | SS.GM.T0015420 | SS.MH.T0015721 | SS.MH.T0014980 | 111.5304 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1619 | 18 | D | SS.GM.T0015422 | SS.MH.T0015765 | SS.MH.T0003450 | 168.3448 | 6 | Point Repair at 32, 46 and 64 ft from 03450 | 14250 | 14250 | Point Repair | Repair
1620 | 18 | C | SS.GM.T0015423 | SS.MH.T0015719 | SS.MH.T0006097 | 168.9613 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1621 | 18 | B | SS.GM.T0015424 | SS.MH.T0015720 | SS.MH.T0004362 | 33.3366 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1622 | 18 | D | SS.GM.T0015428 | SS.MH.T0010878 | SS.MH.T0014315 | 200.0845 | 8 | Burst to 10" - 0 svc | 15006.3411 | 15006.3411 | Pipe Burst or Replace | Replace
1623 | 18 | B | SS.GM.T0015429 | SS.MH.T0015767 | SS.MH.T0004129 | 163.5247 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1624 | 18 | B | SS.GM.T0015430 | SS.MH.T0015768 | SS.MH.T0015767 | 53.9262 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1625 | 18 | C | SS.GM.T0015462 | SS.MH.T0015723 | SS.MH.T0006112 | 300.6262 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1626 | 18 | B | SS.GM.T0015473 | SS.MH.T0006801 | SS.MH.T0015726 | 52.398 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1627 | 18 | B | SS.GM.T0015474 | SS.MH.T0015726 | SS.MH.T0015727 | 165.7325 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1628 | 18 | B | SS.GM.T0015475 | SS.MH.T0015725 | SS.MH.T0006801 | 178.656 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1629 | 18 | B | SS.GM.T0015477 | SS.MH.T0015715 | SS.MH.T0005246 | 46.7166 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1630 | 18 | B | SS.GM.T0015478 | SS.MH.T0015728 | SS.MH.T0008017 | 248.4657 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1631 | 18 | B | SS.GM.T0015479 | SS.MH.T0015729 | SS.MH.T0008008 | 245.3 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1632 | 18 | B | SS.GM.T0015480 | SS.MH.T0015731 | SS.MH.T0008159 | 179.2087 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1633 | 18 | B | SS.GM.T0015481 | SS.MH.T0008096 | SS.MH.T0015730 | 143.0108 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1634 | 18 | B | SS.GM.T0015482 | SS.MH.T0008046 | SS.MH.T0007996 | 213.1001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1635 | 18 | B | SS.GM.T0015483 | SS.MH.T0000655 | SS.MH.T0015732 | 194.6 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1636 | 18 | D | SS.GM.T0015484 | SS.MH.T0015722 | SS.MH.T0000288 | 59.0652 | 0 | Point Repair at 55 ft from 00288 | 4750 | 4750 | Point Repair | Repair
1637 | 18 | B | SS.GM.T0015486 | SS.MH.T0008034 | SS.MH.T0015716 | 323.2686 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1638 | 18 | B | SS.GM.T0015511 | SS.MH.T0015733 | SS.MH.T0007079 | 135.8001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1639 | 18 | B | SS.GM.T0015512 | SS.MH.T0008001 | SS.MH.T0015717 | 87.0004 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1640 | 18 | B | SS.GM.T0015514 | SS.MH.T0015718 | SS.MH.T0005538 | 44.2592 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1641 | 18 | B | SS.GM.T0015515 | SS.MH.T0013872 | SS.MH.T0015734 | 99.9999 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1642 | 18 | B | SS.GM.T0015516 | SS.MH.T0015724 | SS.MH.T0004176 | 260 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1643 | 18 | B | SS.GM.T0015517 | SS.MH.T0013873 | SS.MH.T0015800 | 146.0447 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1644 | 18 | B | SS.GM.T0015568 | SS.MH.T0015740 | SS.MH.T0007985 | 66.8274 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1645 | 18 | A | SS.GM.T0015569 | SS.MH.T0015741 | SS.MH.T0015742 | 155.1001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1646 | 18 | A | SS.GM.T0015570 | SS.MH.T0015742 | SS.MH.T0015743 | 291.1998 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1647 | 18 | D | SS.GM.T0015693 | SS.MH.T0006360 | SS.MH.T0015851 | 119.9 | 6 | Burst to 8" - 1 svc | 8793.5 | 8793.5 | Pipe Burst or Replace | Replace
1648 | 19 | B | SS.GM.T0014981 | SS.MH.T0015119 | SS.MH.T0006333 | 200.8072 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1649 | 20 | B | SS.GM.T0010622 | SS.MH.T0007380 | SS.MH.T0007441 | 421.1002 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1650 | 21 | C | SS.GM.T0000968 | SS.MH.T0006358 | SS.MH.T0006355 | 210.5918 | 12 | Add to Root Removal Schedule | 421.1836 | 0 | Add to Root Removal Program in CMOM | Maintenance
1651 | 21 | B | SS.GM.T0000969 | SS.MH.T0006355 | SS.MH.T0006354 | 80.8154 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1652 | 21 | D | SS.GM.T0000972 | SS.MH.T0006347 | SS.MH.T0006348 | 346.3268 | 6 | Point Repair at 53, 81, 137 and 294 ft from 06347 | 19000 | 19000 | Point Repair | Repair
1653 | 21 | D | SS.GM.T0000973 | SS.MH.T0006346 | SS.MH.T0006347 | 322.7464 | 6 | Point Repair at 34, 88, 139, 159, 170 and 231 ft from 06346 | 28500 | 28500 | Point Repair | Repair
1654 | 21 | D | SS.GM.T0000974 | SS.MH.T0000335 | SS.MH.T0006352 | 317.7599 | 6 | Burst to 8" - 5 svc | 25654.3962 | 25654.3962 | Pipe Burst or Replace | Replace
1655 | 21 | C | SS.GM.T0000975 | SS.MH.T0006348 | SS.MH.T0006349 | 315.1552 | 6 | Add to Root Removal Schedule | 630.3104 | 0 | Add to Root Removal Program in CMOM | Maintenance
1656 | 21 | D | SS.GM.T0000976 | SS.MH.T0006345 | SS.MH.T0006346 | 278.3719 | 6 | Point Repair at 276 ft from 06346 | 4750 | 4750 | Point Repair | Repair
1657 | 21 | D | SS.GM.T0001181 | SS.MH.T0006415 | SS.MH.T0004375 | 643.9673 | 6 | Point Repair at 505 ft from 06415 | 4750 | 4750 | Point Repair | Repair
1658 | 21 | C | SS.GM.T0001182 | SS.MH.T0011101 | SS.MH.T0006351 | 209.3001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1659 | 21 | D | SS.GM.T0001183 | SS.MH.T0012316 | SS.MH.T0004205 | 184.4117 | 6 | Point Repair at 127, 148 and 164 ft from 04205 | 14250 | 14250 | Point Repair | Repair
1660 | 21 | D | SS.GM.T0001184 | SS.MH.T0011195 | SS.MH.T0004205 | 232.2457 | 6 | Burst to 8" - 4 svc | 19095.9735 | 19095.9735 | Pipe Burst or Replace | Replace
1661 | 21 | B | SS.GM.T0001185 | SS.MH.T0012315 | SS.MH.T0006352 | 72.8999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1662 | 21 | D | SS.GM.T0001186 | SS.MH.T0006413 | SS.MH.T0006415 | 360.6926 | 6 | Point Repair at 91, 195, 225 and 227 ft from 06413 and Add to Root Removal Schedule | 19721.3852 | 19721.3852 | Point Repair and Add to Root Removal Program in CMOM | Repair
1663 | 21 | D | SS.GM.T0001187 | SS.MH.T0010861 | SS.MH.T0006413 | 272.0111 | 6 | Point Repair at 30 ft from 06413 | 4750 | 4750 | Point Repair | Repair
1664 | 21 | D | SS.GM.T0001189 | SS.MH.T0011935 | SS.MH.T0006347 | 78.4 | 6 | Construct Cleanout at End Of Line | 3000 | 3000 | Point Repair | Repair
1665 | 21 | C | SS.GM.T0001190 | SS.MH.T0011948 | SS.MH.T0006345 | 152.6001 | 6 | Add to Root Removal Schedule | 305.2003 | 0 | Add to Root Removal Program in CMOM | Maintenance
1666 | 21 | B | SS.GM.T0001191 | SS.MH.T0010860 | SS.MH.T0006345 | 272.7492 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1667 | 21 | C | SS.GM.T0001192 | SS.MH.T0011947 | SS.MH.T0006344 | 395.0001 | 6 | Point Repair at 304 ft from 06344 | 4750 | 0 | Monitor in CMOM | None
1668 | 21 | B | SS.GM.T0001381 | SS.MH.T0006164 | SS.MH.T0006162 | 263.079 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1669 | 21 | B | SS.GM.T0001382 | SS.MH.T0010159 | SS.MH.T0006206 | 228.3525 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1670 | 21 | B | SS.GM.T0001383 | SS.MH.T0006206 | SS.MH.T0006207 | 160.2646 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1671 | 21 | B | SS.GM.T0001388 | SS.MH.T0013691 | SS.MH.T0014693 | 265.7043 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1672 | 21 | B | SS.GM.T0001389 | SS.MH.T0006929 | SS.MH.T0006928 | 166.0999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1673 | 21 | B | SS.GM.T0001390 | SS.MH.T0006928 | SS.MH.T0006927 | 194.0001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1674 | 21 | D | SS.GM.T0001391 | SS.MH.T0006927 | SS.MH.T0006926 | 194.7454 | 6 | Point Repair at 77 ft from 06926 | 4750 | 4750 | Point Repair | Repair
1675 | 21 | C | SS.GM.T0001392 | SS.MH.T0006926 | SS.MH.T0006925 | 167.6 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1676 | 21 | B | SS.GM.T0001508 | SS.MH.T0009606 | SS.MH.T0006310 | 334.6873 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1677 | 21 | D | SS.GM.T0001509 | SS.MH.T0005260 | SS.MH.T0005259 | 430.1071 | 6 | Replace section 220 to 130 ft from 05260. | 10800 | 10800 | Replace Section | Repair
1678 | 21 | D | SS.GM.T0001510 | SS.MH.T0009519 | SS.MH.T0005260 | 321.6001 | 6 | Point Repair at 254 and 263 ft from 05260 | 9500 | 9500 | Point Repair | Repair
1679 | 21 | B | SS.GM.T0001513 | SS.MH.T0010136 | SS.MH.T0006049 | 176.4452 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1680 | 21 | D | SS.GM.T0001514 | SS.MH.T0006049 | SS.MH.T0005567 | 201.928 | 6 | Replace section 29 to 50 ft from 05567 and Point Repair at 5 ft from 06049. | 7270 | 7270 | Replace Section | Repair
1681 | 21 | D | SS.GM.T0001515 | SS.MH.T0006050 | SS.MH.T0006049 | 127.5111 | 6 | Replace section 12 to 30 ft from 06049. | 2160 | 2160 | Replace Section | Repair
1682 | 21 | D | SS.GM.T0001516 | SS.MH.T0006007 | SS.MH.T0006050 | 306.4676 | 6 | Point Repair at 238 ft from 06007 | 4750 | 4750 | Point Repair | Repair
1683 | 21 | D | SS.GM.T0001517 | SS.MH.T0005257 | SS.MH.T0005572 | 385.8977 | 15 | Point Repair at 60 ft from 05257 and CIPP - 0 svc | 22115.3947 | 22115.3947 | Point Repair and Cured In Place Pipe Liner | Rehab
1684 | 21 | C | SS.GM.T0001518 | SS.MH.T0006026 | SS.MH.T0005257 | 218.4328 | 15 | 15" CIPP - 0 svc | 17474.6259 | 0 | Monitor in CMOM | None
1685 | 21 | C | SS.GM.T0001523 | SS.MH.T0005252 | SS.MH.T0005253 | 212.0334 | 15 | 15" CIPP - 0 svc | 16962.6691 | 0 | Monitor in CMOM | None
1686 | 21 | C | SS.GM.T0001524 | SS.MH.T0005251 | SS.MH.T0005252 | 358.8955 | 15 | 15" CIPP - 0 svc | 28711.6432 | 0 | Monitor in CMOM | None
1687 | 21 | C | SS.GM.T0001525 | SS.MH.T0015736 | SS.MH.T0005251 | 241.507 | 15 | 15" CIPP - 0 svc | 19320.5637 | 0 | Monitor in CMOM | None
1688 | 21 | B | SS.GM.T0001526 | SS.MH.T0005248 | SS.MH.T0005250 | 254.1888 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1689 | 21 | B | SS.GM.T0001527 | SS.MH.T0005249 | SS.MH.T0005248 | 108.1589 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1690 | 21 | C | SS.GM.T0001528 | SS.MH.T0009036 | SS.MH.T0005249 | 809.8939 | 15 | Point Repair at 352 ft from 09036 | 4750 | 0 | Monitor in CMOM | None
1691 | 21 | B | SS.GM.T0001531 | SS.MH.T0005262 | SS.MH.T0005261 | 252.7745 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1692 | 21 | B | SS.GM.T0001532 | SS.MH.T0006002 | SS.MH.T0005262 | 64.2951 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1693 | 21 | B | SS.GM.T0001533 | SS.MH.T0010065 | SS.MH.T0006002 | 391.1989 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1694 | 21 | B | SS.GM.T0001534 | SS.MH.T0010070 | SS.MH.T0005261 | 105.9998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1695 | 21 | B | SS.GM.T0001535 | SS.MH.T0006003 | SS.MH.T0005261 | 345.0589 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1696 | 21 | B | SS.GM.T0001536 | SS.MH.T0006004 | SS.MH.T0006003 | 353.326 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1697 | 21 | C | SS.GM.T0001537 | SS.MH.T0006005 | SS.MH.T0006004 | 115.1117 | 6 | Point Repair at 113 ft from 06005 | 4750 | 0 | Monitor in CMOM | None
1698 | 21 | B | SS.GM.T0001538 | SS.MH.T0010069 | SS.MH.T0006004 | 82.4595 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1699 | 21 | B | SS.GM.T0001539 | SS.MH.T0010068 | SS.MH.T0006005 | 153.3 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1700 | 21 | D | SS.GM.T0001544 | SS.MH.T0006023 | SS.MH.T0006022 | 126.7977 | 6 | Point Repair at 89 ft from 06023 | 4750 | 4750 | Point Repair | Repair
1701 | 21 | B | SS.GM.T0001545 | SS.MH.T0009309 | SS.MH.T0006023 | 88.4684 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1702 | 21 | B | SS.GM.T0001546 | SS.MH.T0005562 | SS.MH.T0006031 | 102.7762 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1703 | 21 | B | SS.GM.T0001547 | SS.MH.T0006029 | SS.MH.T0005562 | 278.4863 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1704 | 21 | B | SS.GM.T0001548 | SS.MH.T0006028 | SS.MH.T0006029 | 99.7206 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1705 | 21 | B | SS.GM.T0001549 | SS.MH.T0010135 | SS.MH.T0006028 | 42.5562 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1706 | 21 | B | SS.GM.T0001550 | SS.MH.T0006313 | SS.MH.T0006302 | 214.7002 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1707 | 21 | B | SS.GM.T0001551 | SS.MH.T0009326 | SS.MH.T0006313 | 311.9819 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1708 | 21 | D | SS.GM.T0001552 | SS.MH.T0006046 | SS.MH.T0000279 | 61.2789 | 6 | Replace section 8 to 45 ft from 06046 and Point Repair at 5 ft from 00279. | 9190 | 9190 | Replace Section | Repair
1709 | 21 | D | SS.GM.T0001553 | SS.MH.T0006045 | SS.MH.T0006046 | 182.1683 | 6 | Replace section 12 to 30 ft from 06045. | 2160 | 2160 | Replace Section | Repair
1710 | 21 | B | SS.GM.T0001554 | SS.MH.T0005564 | SS.MH.T0006045 | 504.2565 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1711 | 21 | B | SS.GM.T0001555 | SS.MH.T0006062 | SS.MH.T0005564 | 541.0461 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1712 | 21 | B | SS.GM.T0001556 | SS.MH.T0006063 | SS.MH.T0006062 | 174.2657 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1713 | 21 | B | SS.GM.T0001557 | SS.MH.T0010131 | SS.MH.T0006063 | 331.0001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1714 | 21 | B | SS.GM.T0001558 | SS.MH.T0006919 | SS.MH.T0006040 | 293.2948 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1715 | 21 | B | SS.GM.T0001559 | SS.MH.T0010130 | SS.MH.T0006919 | 49.6505 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1716 | 21 | B | SS.GM.T0001570 | SS.MH.T0009523 | SS.MH.T0006936 | 156.3 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1717 | 21 | B | SS.GM.T0001571 | SS.MH.T0006936 | SS.MH.T0006937 | 105.1475 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1718 | 21 | B | SS.GM.T0001703 | SS.MH.T0009366 | SS.MH.T0006164 | 349.8001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1719 | 21 | D | SS.GM.T0001704 | SS.MH.T0011119 | SS.MH.T0006207 | 115.1328 | 6 | Point Repair at 64 and 84 ft from 06207 | 9500 | 9500 | Point Repair | Repair
1720 | 21 | B | SS.GM.T0001738 | SS.MH.T0007588 | SS.MH.T0014730 | 137.302 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1721 | 21 | B | SS.GM.T0001739 | SS.MH.T0012337 | SS.MH.T0000276 | 41.5 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1722 | 21 | B | SS.GM.T0001740 | SS.MH.T0012184 | SS.MH.T0006320 | 368.1998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1723 | 21 | C | SS.GM.T0002544 | SS.MH.T0006357 | SS.MH.T0006324 | 335.5151 | 12 | Add to Root Removal Schedule | 671.0303 | 0 | Add to Root Removal Program in CMOM | Maintenance
1724 | 21 | B | SS.GM.T0002545 | SS.MH.T0006356 | SS.MH.T0006357 | 129.8688 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1725 | 21 | B | SS.GM.T0002547 | SS.MH.T0006352 | SS.MH.T0006348 | 605.2412 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1726 | 21 | B | SS.GM.T0002549 | SS.MH.T0006343 | SS.MH.T0006325 | 142.5806 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1727 | 21 | B | SS.GM.T0002550 | SS.MH.T0006341 | SS.MH.T0015739 | 394.3251 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1728 | 21 | B | SS.GM.T0002551 | SS.MH.T0006339 | SS.MH.T0006340 | 322.2049 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1729 | 21 | B | SS.GM.T0002552 | SS.MH.T0006338 | SS.MH.T0006339 | 398.3114 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1730 | 21 | B | SS.GM.T0002553 | SS.MH.T0006337 | SS.MH.T0006338 | 514.3429 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1731 | 21 | D | SS.GM.T0002586 | SS.MH.T0006325 | SS.MH.T0006321 | 224.3518 | 6 | Point Repair at 106, 115 and 221 ft from 06325 | 14250 | 14250 | Point Repair | Repair
1732 | 21 | C | SS.GM.T0002587 | SS.MH.T0006323 | SS.MH.T0000331 | 86.9007 | 12 | Add to Root Removal Schedule | 173.8014 | 0 | Add to Root Removal Program in CMOM | Maintenance
1733 | 21 | C | SS.GM.T0002588 | SS.MH.T0000331 | SS.MH.T0006322 | 167.2119 | 15 | 15" CIPP - 0 svc | 13376.9525 | 0 | Monitor in CMOM | None
1734 | 21 | B | SS.GM.T0002590 | SS.MH.T0006013 | SS.MH.T0006319 | 279.4823 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1735 | 21 | B | SS.GM.T0002594 | SS.MH.T0005565 | SS.MH.T0006906 | 51.4999 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1736 | 21 | D | SS.GM.T0002600 | SS.MH.T0007029 | SS.MH.T0006317 | 103.8182 | 6 | Point Repair at 67 ft from 07029 | 4750 | 4750 | Point Repair | Repair
1737 | 21 | B | SS.GM.T0002601 | SS.MH.T0006312 | SS.MH.T0006318 | 335.3833 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1738 | 21 | B | SS.GM.T0002603 | SS.MH.T0006316 | SS.MH.T0006059 | 377.1047 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1739 | 21 | B | SS.GM.T0002606 | SS.MH.T0006311 | SS.MH.T0006312 | 279.3033 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1740 | 21 | B | SS.GM.T0002607 | SS.MH.T0009328 | SS.MH.T0006311 | 192.1001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1741 | 21 | B | SS.GM.T0002608 | SS.MH.T0006310 | SS.MH.T0006309 | 109.9288 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1742 | 21 | B | SS.GM.T0002610 | SS.MH.T0006308 | SS.MH.T0006306 | 175.029 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1743 | 21 | B | SS.GM.T0002634 | SS.MH.T0006208 | SS.MH.T0006067 | 305.5019 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1744 | 21 | B | SS.GM.T0002635 | SS.MH.T0006203 | SS.MH.T0006204 | 116 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1745 | 21 | C | SS.GM.T0002636 | SS.MH.T0006205 | SS.MH.T0006203 | 216.0073 | 6 | Add to Root Removal Schedule | 432.0147 | 0 | Add to Root Removal Program in CMOM | Maintenance
1746 | 21 | B | SS.GM.T0002637 | SS.MH.T0006204 | SS.MH.T0006202 | 139.0138 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1747 | 21 | B | SS.GM.T0002638 | SS.MH.T0006202 | SS.MH.T0006201 | 187.5541 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1748 | 21 | D | SS.GM.T0002686 | SS.MH.T0006412 | SS.MH.T0004375 | 1023.5235 | 6 | Point Repair at 28 and 109 ft from 06412 and 11 and 129 ft from 04375 | 19000 | 19000 | Point Repair | Repair
1749 | 21 | C | SS.GM.T0002790 | SS.MH.T0010157 | SS.MH.T0006163 | 300.0083 | 6 | Point Repair at 166 ft from 06163 | 4750 | 0 | Monitor in CMOM | None
1750 | 21 | D | SS.GM.T0002791 | SS.MH.T0006161 | SS.MH.T0006162 | 295.9632 | 6 | Point Repair at 292 ft from 06161 | 4750 | 4750 | Point Repair | Repair
1751 | 21 | D | SS.GM.T0002792 | SS.MH.T0006160 | SS.MH.T0006161 | 393.5708 | 6 | Point Repair at 156 ft from 06160 | 4750 | 4750 | Point Repair | Repair
1752 | 21 | B | SS.GM.T0002793 | SS.MH.T0006159 | SS.MH.T0006160 | 319.4775 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1753 | 21 | B | SS.GM.T0002794 | SS.MH.T0006158 | SS.MH.T0006159 | 76.0844 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1754 | 21 | B | SS.GM.T0002813 | SS.MH.T0009524 | SS.MH.T0006935 | 333.0999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1755 | 21 | B | SS.GM.T0002814 | SS.MH.T0006935 | SS.MH.T0006934 | 444.1 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1756 | 21 | B | SS.GM.T0002815 | SS.MH.T0015883 | SS.MH.T0006933 | 398.2 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1757 | 21 | B | SS.GM.T0002817 | SS.MH.T0006937 | SS.MH.T0006079 | 485.9832 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1758 | 21 | D | SS.GM.T0002818 | SS.MH.T0006079 | SS.MH.T0006078 | 326.1797 | 6 | Point Repair at 40 ft from 06078 | 4750 | 4750 | Point Repair | Repair
1759 | 21 | B | SS.GM.T0002819 | SS.MH.T0006077 | SS.MH.T0012865 | 295.0001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1760 | 21 | D | SS.GM.T0002820 | SS.MH.T0006073 | SS.MH.T0006074 | 244.7302 | 6 | Point Repair at 274 ft from 06074 | 4750 | 4750 | Point Repair | Repair
1761 | 21 | D | SS.GM.T0002821 | SS.MH.T0009882 | SS.MH.T0006072 | 413.1594 | 6 | Point Repair at 228 ft from 06072 | 4750 | 4750 | Point Repair | Repair
1762 | 21 | C | SS.GM.T0002822 | SS.MH.T0006070 | SS.MH.T0013966 | 199.5001 | 6 | Add to Root Removal Schedule | 399.0002 | 0 | Add to Root Removal Program in CMOM | Maintenance
1763 | 21 | D | SS.GM.T0002823 | SS.MH.T0013966 | SS.MH.T0007972 | 213.6001 | 6 | Point Repair at 187 ft from 07972 | 4750 | 4750 | Point Repair | Repair
1764 | 21 | C | SS.GM.T0002825 | SS.MH.T0006201 | SS.MH.T0006067 | 190.4072 | 6 | Add to Root Removal Schedule | 380.8145 | 0 | Add to Root Removal Program in CMOM | Maintenance
1765 | 21 | B | SS.GM.T0002826 | SS.MH.T0006921 | SS.MH.T0006924 | 313.2183 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1766 | 21 | B | SS.GM.T0002827 | SS.MH.T0009546 | SS.MH.T0006923 | 175.7609 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1767 | 21 | B | SS.GM.T0002828 | SS.MH.T0009880 | SS.MH.T0006921 | 367.4201 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1768 | 21 | B | SS.GM.T0002829 | SS.MH.T0006920 | SS.MH.T0006919 | 315.423 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1769 | 21 | B | SS.GM.T0002831 | SS.MH.T0006916 | SS.MH.T0008617 | 578.6226 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1770 | 21 | D | SS.GM.T0002833 | SS.MH.T0006915 | SS.MH.T0006916 | 267.0999 | 8 | Point Repair at 146, 149 and 218 ft from 06915 | 14250 | 14250 | Point Repair | Repair
1771 | 21 | B | SS.GM.T0002834 | SS.MH.T0006914 | SS.MH.T0006915 | 51.0001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1772 | 21 | D | SS.GM.T0002835 | SS.MH.T0006913 | SS.MH.T0006914 | 398.325 | 8 | Point Repair at 217 ft from 06913 and Add to Root Removal Schedule | 5546.65 | 5546.65 | Point Repair and Add to Root Removal Program in CMOM | Repair
1773 | 21 | C | SS.GM.T0002836 | SS.MH.T0006912 | SS.MH.T0006913 | 156.6001 | 8 | Add to Root Removal Schedule | 313.2002 | 0 | Add to Root Removal Program in CMOM | Maintenance
1774 | 21 | D | SS.GM.T0002837 | SS.MH.T0006911 | SS.MH.T0006912 | 176.1918 | 8 | Point Repair at 5 ft from 06912 | 4750 | 4750 | Point Repair | Repair
1775 | 21 | D | SS.GM.T0002840 | SS.MH.T0006906 | SS.MH.T0006317 | 517.0098 | 8 | Grout Joint at 29 and 492 ft from 06906 | 1600 | 1600 | Grout Joints | Repair
1776 | 21 | D | SS.GM.T0002842 | SS.MH.T0006904 | SS.MH.T0006903 | 86.6456 | 6 | Point Repair at 20 ft from 06904 | 4750 | 4750 | Point Repair | Repair
1777 | 21 | B | SS.GM.T0002843 | SS.MH.T0006903 | SS.MH.T0006909 | 104.3814 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1778 | 21 | B | SS.GM.T0002844 | SS.MH.T0006902 | SS.MH.T0006920 | 207.6791 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1779 | 21 | B | SS.GM.T0002845 | SS.MH.T0000281 | SS.MH.T0006064 | 246.9409 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1780 | 21 | B | SS.GM.T0002846 | SS.MH.T0000280 | SS.MH.T0000281 | 199.3028 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1781 | 21 | B | SS.GM.T0002847 | SS.MH.T0009522 | SS.MH.T0000280 | 167.7687 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1782 | 21 | B | SS.GM.T0002850 | SS.MH.T0006059 | SS.MH.T0006318 | 445.6035 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1783 | 21 | C | SS.GM.T0002851 | SS.MH.T0006053 | SS.MH.T0006058 | 298.0999 | 6 | Point Repair at 235 ft from 06053 | 4750 | 0 | Monitor in CMOM | None
1784 | 21 | B | SS.GM.T0002852 | SS.MH.T0010140 | SS.MH.T0006053 | 415.8001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1785 | 21 | D | SS.GM.T0002853 | SS.MH.T0006044 | SS.MH.T0006045 | 114.3765 | 6 | Point Repair at 24 ft from 06045 | 4750 | 4750 | Point Repair | Repair
1786 | 21 | B | SS.GM.T0002854 | SS.MH.T0006043 | SS.MH.T0006044 | 105.2675 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1787 | 21 | B | SS.GM.T0002855 | SS.MH.T0006041 | SS.MH.T0006043 | 128.7397 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1788 | 21 | B | SS.GM.T0002856 | SS.MH.T0006042 | SS.MH.T0006041 | 401.5908 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1789 | 21 | B | SS.GM.T0002857 | SS.MH.T0006065 | SS.MH.T0006040 | 378.1747 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1790 | 21 | B | SS.GM.T0002860 | SS.MH.T0010137 | SS.MH.T0006034 | 206.0036 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1791 | 21 | B | SS.GM.T0002861 | SS.MH.T0000276 | SS.MH.T0000278 | 214.8568 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1792 | 21 | B | SS.GM.T0002862 | SS.MH.T0000277 | SS.MH.T0006030 | 255.9214 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1793 | 21 | B | SS.GM.T0002863 | SS.MH.T0010134 | SS.MH.T0006027 | 96.8149 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1794 | 21 | B | SS.GM.T0002864 | SS.MH.T0006021 | SS.MH.T0006020 | 101.2907 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1795 | 21 | B | SS.GM.T0002865 | SS.MH.T0006032 | SS.MH.T0006020 | 309.691 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1796 | 21 | B | SS.GM.T0002866 | SS.MH.T0006019 | SS.MH.T0006018 | 251.81 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1797 | 21 | D | SS.GM.T0002868 | SS.MH.T0006320 | SS.MH.T0006016 | 392.2723 | 8 | Point Repair at 86, 114, 120, 226, 256 and 345 ft from 06320 | 28500 | 28500 | Point Repair | Repair
1798 | 21 | D | SS.GM.T0002869 | SS.MH.T0006016 | SS.MH.T0006015 | 66.9447 | 8 | Replace section 42 to 20 ft from 06016. | 2860 | 2860 | Replace Section | Repair
1799 | 21 | B | SS.GM.T0002870 | SS.MH.T0006015 | SS.MH.T0006014 | 134.2741 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1800 | 21 | B | SS.GM.T0002871 | SS.MH.T0006014 | SS.MH.T0006013 | 179.8362 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1801 | 21 | B | SS.GM.T0002872 | SS.MH.T0000275 | SS.MH.T0005571 | 63.0231 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1802 | 21 | B | SS.GM.T0002873 | SS.MH.T0006011 | SS.MH.T0000275 | 100.6695 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1803 | 21 | B | SS.GM.T0002874 | SS.MH.T0006010 | SS.MH.T0006011 | 131.0537 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1804 | 21 | C | SS.GM.T0002876 | SS.MH.T0005256 | SS.MH.T0005572 | 148.9907 | 15 | 15" CIPP - 0 svc | 11919.2576 | 0 | Monitor in CMOM | None
1805 | 21 | C | SS.GM.T0002877 | SS.MH.T0005255 | SS.MH.T0005256 | 261.7343 | 15 | 15" CIPP - 0 svc | 20938.7432 | 0 | Monitor in CMOM | None
1806 | 21 | B | SS.GM.T0002958 | SS.MH.T0009307 | SS.MH.T0006007 | 236.5 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1807 | 21 | D | SS.GM.T0002959 | SS.MH.T0006076 | SS.MH.T0006075 | 110.6002 | 8 | Point Repair at 39 ft from 06075 | 4750 | 4750 | Point Repair | Repair
1808 | 21 | D | SS.GM.T0003119 | SS.MH.T0012865 | SS.MH.T0006076 | 404.5667 | 8 | Point Repair at 128 ft from 06076 | 4750 | 4750 | Point Repair | Repair
1809 | 21 | D | SS.GM.T0003141 | SS.MH.T0011197 | SS.MH.T0006007 | 289.255 | 6 | Point Repair at 5 ft from 06007 | 4750 | 4750 | Point Repair | Repair
1810 | 21 | B | SS.GM.T0003395 | SS.MH.T0006324 | SS.MH.T0006323 | 70.0202 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1811 | 21 | B | SS.GM.T0003396 | SS.MH.T0006354 | SS.MH.T0006356 | 325.3473 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1812 | 21 | C | SS.GM.T0003397 | SS.MH.T0004205 | SS.MH.T0006348 | 411.3501 | 6 | Burst to 8" - 4 svc | 30737.7573 | 0 | Monitor in CMOM | None
1813 | 21 | C | SS.GM.T0003398 | SS.MH.T0006351 | SS.MH.T0004205 | 350.068 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1814 | 21 | D | SS.GM.T0003399 | SS.MH.T0006344 | SS.MH.T0006349 | 615.0001 | 6 | Point Repair at 310 ft from 06344 and Add to Root Removal Schedule | 5980.0002 | 5980.0002 | Point Repair and Add to Root Removal Program in CMOM | Repair
1815 | 21 | C | SS.GM.T0003400 | SS.MH.T0006340 | SS.MH.T0006341 | 273.7516 | 6 | Point Repair at 104 and 111 ft from 06340 | 9500 | 0 | Monitor in CMOM | None
1816 | 21 | B | SS.GM.T0003438 | SS.MH.T0006318 | SS.MH.T0007029 | 95.1241 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1817 | 21 | B | SS.GM.T0003439 | SS.MH.T0009324 | SS.MH.T0006311 | 295.1 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1818 | 21 | B | SS.GM.T0003441 | SS.MH.T0009539 | SS.MH.T0006313 | 380.8212 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1819 | 21 | B | SS.GM.T0003442 | SS.MH.T0009327 | SS.MH.T0006316 | 342.6838 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1820 | 21 | D | SS.GM.T0003443 | SS.MH.T0006309 | SS.MH.T0006308 | 388.8692 | 6 | Point Repair at 164 and 267 ft from 06309 | 9500 | 9500 | Point Repair | Repair
1821 | 21 | B | SS.GM.T0003454 | SS.MH.T0010158 | SS.MH.T0006205 | 179.5 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1822 | 21 | B | SS.GM.T0003455 | SS.MH.T0006207 | SS.MH.T0006208 | 249.2722 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1823 | 21 | D | SS.GM.T0003456 | SS.MH.T0015745 | SS.MH.T0006071 | 335.3848 | 6 | Point Repair at 188 and 210 ft from 06071 | 9500 | 9500 | Point Repair | Repair
1824 | 21 | D | SS.GM.T0003566 | SS.MH.T0011107 | SS.MH.T0000335 | 244.1001 | 6 | Burst to 8" - 6 svc | 21866.5088 | 21866.5088 | Pipe Burst or Replace | Replace
1825 | 21 | D | SS.GM.T0003567 | SS.MH.T0010698 | SS.MH.T0006351 | 485.8435 | 6 | Burst to 8" - 12 svc | 43579.8273 | 43579.8273 | Pipe Burst or Replace | Replace
1826 | 21 | B | SS.GM.T0003569 | SS.MH.T0010864 | SS.MH.T0006412 | 236.2302 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1827 | 21 | C | SS.GM.T0003762 | SS.MH.T0006162 | SS.MH.T0006163 | 135.0239 | 6 | Add to Root Removal Schedule | 270.0478 | 0 | Add to Root Removal Program in CMOM | Maintenance
1828 | 21 | B | SS.GM.T0003778 | SS.MH.T0006078 | SS.MH.T0006075 | 455.3368 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1829 | 21 | B | SS.GM.T0003779 | SS.MH.T0006074 | SS.MH.T0012865 | 147.8 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1830 | 21 | B | SS.GM.T0003780 | SS.MH.T0006944 | SS.MH.T0006073 | 375.0001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1831 | 21 | B | SS.GM.T0003781 | SS.MH.T0006072 | SS.MH.T0015218 | 362.9998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1832 | 21 | B | SS.GM.T0003782 | SS.MH.T0009881 | SS.MH.T0006072 | 344.7 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1833 | 21 | B | SS.GM.T0003783 | SS.MH.T0006923 | SS.MH.T0006922 | 106.8511 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1834 | 21 | B | SS.GM.T0003784 | SS.MH.T0009879 | SS.MH.T0006922 | 242.778 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1835 | 21 | B | SS.GM.T0003785 | SS.MH.T0006922 | SS.MH.T0006921 | 386.7224 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1836 | 21 | C | SS.GM.T0003786 | SS.MH.T0006924 | SS.MH.T0006914 | 132 | 6 | Point Repair at 26 ft from 06924 | 4750 | 0 | Monitor in CMOM | None
1837 | 21 | B | SS.GM.T0003790 | SS.MH.T0006905 | SS.MH.T0006904 | 107.2223 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1838 | 21 | B | SS.GM.T0003791 | SS.MH.T0009877 | SS.MH.T0006904 | 133.6434 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1839 | 21 | B | SS.GM.T0003792 | SS.MH.T0009876 | SS.MH.T0006902 | 331.1998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1840 | 21 | B | SS.GM.T0003793 | SS.MH.T0009310 | SS.MH.T0000280 | 225.1001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1841 | 21 | B | SS.GM.T0003794 | SS.MH.T0006064 | SS.MH.T0006065 | 255.9699 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1842 | 21 | B | SS.GM.T0003797 | SS.MH.T0006040 | SS.MH.T0006041 | 314.2252 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1843 | 21 | B | SS.GM.T0003800 | SS.MH.T0010139 | SS.MH.T0006031 | 104.4999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1844 | 21 | B | SS.GM.T0003801 | SS.MH.T0006031 | SS.MH.T0006032 | 312.889 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1845 | 21 | B | SS.GM.T0003802 | SS.MH.T0006033 | SS.MH.T0006032 | 91.5001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1846 | 21 | D | SS.GM.T0003803 | SS.MH.T0006034 | SS.MH.T0005571 | 102.7689 | 6 | Replace section 85 ft from 06034 to 05571. | 5400 | 5400 | Replace Section | Repair
1847 | 21 | B | SS.GM.T0003804 | SS.MH.T0006027 | SS.MH.T0006033 | 186.2266 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1848 | 21 | B | SS.GM.T0003805 | SS.MH.T0010133 | SS.MH.T0000278 | 380.1998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1849 | 21 | B | SS.GM.T0003806 | SS.MH.T0006030 | SS.MH.T0000276 | 102.6028 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1850 | 21 | B | SS.GM.T0003807 | SS.MH.T0000278 | SS.MH.T0006320 | 307.7136 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1851 | 21 | B | SS.GM.T0003808 | SS.MH.T0006009 | SS.MH.T0006010 | 154.2145 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1852 | 21 | B | SS.GM.T0003809 | SS.MH.T0006020 | SS.MH.T0006019 | 150.4274 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1853 | 21 | C | SS.GM.T0003810 | SS.MH.T0010138 | SS.MH.T0006020 | 171.5998 | 6 | Point Repair at 169 ft from 06020 | 4750 | 0 | Monitor in CMOM | None
1854 | 21 | B | SS.GM.T0003811 | SS.MH.T0009518 | SS.MH.T0006021 | 152.9093 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1855 | 21 | C | SS.GM.T0003812 | SS.MH.T0009308 | SS.MH.T0006009 | 186.6001 | 6 | Point Repair at 17 ft from 06009 | 4750 | 0 | Monitor in CMOM | None
1856 | 21 | B | SS.GM.T0003813 | SS.MH.T0009306 | SS.MH.T0006006 | 407.7001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1857 | 21 | D | SS.GM.T0003816 | SS.MH.T0006006 | SS.MH.T0005259 | 274.1123 | 6 | Burst to 8" - 5 svc | 22817.3021 | 22817.3021 | Pipe Burst or Replace | Replace
1858 | 21 | D | SS.GM.T0003817 | SS.MH.T0006322 | SS.MH.T0005255 | 407.2722 | 15 | 15" CIPP - 0 svc | 32581.7778 | 32581.7778 | Cured In Place Pipe Liner | Rehab
1859 | 21 | B | SS.GM.T0003969 | SS.MH.T0011233 | SS.MH.T0006158 | 150.3589 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1860 | 21 | D | SS.GM.T0004020 | SS.MH.T0006081 | SS.MH.T0012865 | 615.7387 | 6 | Point Repair at 3 ft from 12865 and Access; Clean and Inspection | 7212.9549 | 7212.9549 | Point Repair and Access; Clean and Inspection | Repair
1861 | 21 | B | SS.GM.T0004021 | SS.MH.T0011116 | SS.MH.T0006077 | 229.9998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1862 | 21 | B | SS.GM.T0004033 | SS.MH.T0010125 | SS.MH.T0000277 | 241.1002 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1863 | 21 | B | SS.GM.T0004602 | SS.MH.T0006576 | SS.MH.T0006469 | 199.152 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1864 | 21 | B | SS.GM.T0004603 | SS.MH.T0006575 | SS.MH.T0006576 | 199.6239 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1865 | 21 | B | SS.GM.T0004604 | SS.MH.T0006479 | SS.MH.T0006575 | 187.1001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1866 | 21 | D | SS.GM.T0004605 | SS.MH.T0010279 | SS.MH.T0006479 | 374.2 | 6 | Point Repair at 228 ft from 06479 | 4750 | 4750 | Point Repair | Repair
1867 | 21 | B | SS.GM.T0004606 | SS.MH.T0006469 | SS.MH.T0006468 | 251.6106 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1868 | 21 | C | SS.GM.T0004607 | SS.MH.T0006468 | SS.MH.T0006467 | 154.9497 | 6 | Point Repair at 9 ft from 06468 | 4750 | 0 | Monitor in CMOM | None
1869 | 21 | B | SS.GM.T0004608 | SS.MH.T0006467 | SS.MH.T0006466 | 92.9089 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1870 | 21 | B | SS.GM.T0004609 | SS.MH.T0006466 | SS.MH.T0006465 | 136.1971 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1871 | 21 | B | SS.GM.T0004611 | SS.MH.T0009424 | SS.MH.T0006790 | 252.481 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1872 | 21 | B | SS.GM.T0004919 | SS.MH.T0011643 | SS.MH.T0006482 | 49.06 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1873 | 21 | B | SS.GM.T0004920 | SS.MH.T0012619 | SS.MH.T0006480 | 36.4215 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1874 | 21 | B | SS.GM.T0004921 | SS.MH.T0012620 | SS.MH.T0006462 | 24.3838 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1875 | 21 | D | SS.GM.T0004922 | SS.MH.T0006797 | SS.MH.T0006461 | 138.0423 | 10 | 10" CIPP - 0 svc | 6902.1128 | 6902.1128 | Cured In Place Pipe Liner | Rehab
1876 | 21 | B | SS.GM.T0004923 | SS.MH.T0006790 | SS.MH.T0006792 | 102.2686 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1877 | 21 | B | SS.GM.T0004924 | SS.MH.T0006792 | SS.MH.T0006791 | 204.4554 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1878 | 21 | D | SS.GM.T0004925 | SS.MH.T0006791 | SS.MH.T0006794 | 227.1247 | 6 | Point Repair at 111 ft from 06791 | 4750 | 4750 | Point Repair | Repair
1879 | 21 | B | SS.GM.T0008550 | SS.MH.T0006541 | SS.MH.T0006793 | 136.9425 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1880 | 21 | D | SS.GM.T0008551 | SS.MH.T0006548 | SS.MH.T0006550 | 399.1675 | 10 | Replace section 157 ft from 06548 to 06550. | 34020 | 34020 | Replace Section | Repair
1881 | 21 | B | SS.GM.T0008568 | SS.MH.T0006481 | SS.MH.T0006463 | 332.3441 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1882 | 21 | D | SS.GM.T0008569 | SS.MH.T0006532 | SS.MH.T0006481 | 273.2804 | 6 | Burst to 8" - 13 svc | 30763.2249 | 30763.2249 | Pipe Burst or Replace | Replace
1883 | 21 | B | SS.GM.T0008607 | SS.MH.T0000393 | SS.MH.T0006469 | 31.3 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1884 | 21 | D | SS.GM.T0008608 | SS.MH.T0009641 | SS.MH.T0000393 | 383.0907 | 6 | Point Repair at 83 and 105 ft from 00393. Corss bore at 105. | 9500 | 9500 | Point Repair | Repair
1885 | 21 | B | SS.GM.T0008609 | SS.MH.T0009642 | SS.MH.T0000393 | 251.7286 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1886 | 21 | B | SS.GM.T0008610 | SS.MH.T0000392 | SS.MH.T0006468 | 31.8793 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1887 | 21 | B | SS.GM.T0008611 | SS.MH.T0009640 | SS.MH.T0000392 | 309.2 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1888 | 21 | B | SS.GM.T0008612 | SS.MH.T0009647 | SS.MH.T0006466 | 365.6999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1889 | 21 | B | SS.GM.T0008613 | SS.MH.T0006480 | SS.MH.T0006482 | 457.3357 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1890 | 21 | B | SS.GM.T0008614 | SS.MH.T0006482 | SS.MH.T0006532 | 213.1032 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1891 | 21 | B | SS.GM.T0008615 | SS.MH.T0006483 | SS.MH.T0006796 | 42.3905 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1892 | 21 | C | SS.GM.T0008616 | SS.MH.T0006458 | SS.MH.T0006460 | 302.4546 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1893 | 21 | B | SS.GM.T0008617 | SS.MH.T0009646 | SS.MH.T0006458 | 130.4306 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1894 | 21 | B | SS.GM.T0008618 | SS.MH.T0009645 | SS.MH.T0006458 | 147.5001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1895 | 21 | B | SS.GM.T0008620 | SS.MH.T0006461 | SS.MH.T0006460 | 208.0466 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1896 | 21 | B | SS.GM.T0008621 | SS.MH.T0006462 | SS.MH.T0006461 | 252.5017 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1897 | 21 | B | SS.GM.T0008622 | SS.MH.T0006463 | SS.MH.T0006462 | 218.5828 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1898 | 21 | C | SS.GM.T0008623 | SS.MH.T0006464 | SS.MH.T0006463 | 368.4976 | 10 | Point Repair at 53 ft from 06464 | 4750 | 0 | Monitor in CMOM | None
1899 | 21 | C | SS.GM.T0008624 | SS.MH.T0006465 | SS.MH.T0006464 | 238.8146 | 8 | Add to Root Removal Schedule | 477.6292 | 0 | Add to Root Removal Program in CMOM | Maintenance
1900 | 21 | B | SS.GM.T0008754 | SS.MH.T0006542 | SS.MH.T0006541 | 142.1082 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1901 | 21 | B | SS.GM.T0008755 | SS.MH.T0006543 | SS.MH.T0006542 | 241.8221 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1902 | 21 | B | SS.GM.T0008756 | SS.MH.T0006544 | SS.MH.T0006543 | 104.2232 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1903 | 21 | B | SS.GM.T0008757 | SS.MH.T0009423 | SS.MH.T0006544 | 143.1804 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1904 | 21 | B | SS.GM.T0008765 | SS.MH.T0006459 | SS.MH.T0006548 | 397.6837 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1905 | 21 | B | SS.GM.T0008857 | SS.MH.T0006796 | SS.MH.T0006532 | 359.3288 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1906 | 21 | B | SS.GM.T0008900 | SS.MH.T0006793 | SS.MH.T0006790 | 170.3238 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1907 | 21 | D | SS.GM.T0009563 | SS.MH.T0006460 | SS.MH.T0006459 | 247.5924 | 10 | Grout Joint at 201 ft from 06460 | 800 | 800 | Grout Joints | Repair
1908 | 21 | B | SS.GM.T0009564 | SS.MH.T0006550 | SS.MH.T0006794 | 140.0474 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1909 | 21 | D | SS.GM.T0009565 | SS.MH.T0004208 | SS.MH.T0004207 | 237.9531 | 12 | Point Repair at 177, 182 and 224 ft from 04208 | 14250 | 14250 | Point Repair | Repair
1910 | 21 | D | SS.GM.T0009566 | SS.MH.T0004207 | SS.MH.T0004206 | 273.1784 | 12 | Point Repair at 111 ft from 04207 | 4750 | 4750 | Point Repair | Repair
1911 | 21 | C | SS.GM.T0009567 | SS.MH.T0004206 | SS.MH.T0005250 | 284.1216 | 12 | Add to Root Removal Schedule | 568.2431 | 0 | Add to Root Removal Program in CMOM | Maintenance
1912 | 21 | B | SS.GM.T0009568 | SS.MH.T0006342 | SS.MH.T0006343 | 332.6194 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1913 | 21 | B | SS.GM.T0009572 | SS.MH.T0006849 | SS.MH.T0006009 | 87.8345 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1914 | 21 | B | SS.GM.T0009576 | SS.MH.T0006850 | SS.MH.T0000277 | 276.6726 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1915 | 21 | B | SS.GM.T0009577 | SS.MH.T0006851 | SS.MH.T0006850 | 104.1949 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1916 | 21 | B | SS.GM.T0009578 | SS.MH.T0006852 | SS.MH.T0006850 | 266.4629 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1917 | 21 | B | SS.GM.T0009579 | SS.MH.T0009708 | SS.MH.T0006853 | 175.9982 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1918 | 21 | B | SS.GM.T0009580 | SS.MH.T0010064 | SS.MH.T0006854 | 49 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1919 | 21 | B | SS.GM.T0009581 | SS.MH.T0006854 | SS.MH.T0006852 | 71.6675 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1920 | 21 | B | SS.GM.T0009582 | SS.MH.T0009457 | SS.MH.T0000639 | 387.6999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1921 | 21 | D | SS.GM.T0009583 | SS.MH.T0006853 | SS.MH.T0006852 | 266.5962 | 6 | Point Repair at 86 ft from 06853 | 4750 | 4750 | Point Repair | Repair
1922 | 21 | B | SS.GM.T0009584 | SS.MH.T0000637 | SS.MH.T0006853 | 343.1584 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1923 | 21 | B | SS.GM.T0009585 | SS.MH.T0000638 | SS.MH.T0000637 | 86.3126 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1924 | 21 | D | SS.GM.T0009586 | SS.MH.T0000639 | SS.MH.T0000638 | 57.9986 | 6 | Burst to 8" - 0 svc | 3769.9064 | 3769.9064 | Pipe Burst or Replace | Replace
1925 | 21 | B | SS.GM.T0009587 | SS.MH.T0000640 | SS.MH.T0000639 | 161.8093 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1926 | 21 | D | SS.GM.T0009588 | SS.MH.T0000641 | SS.MH.T0000640 | 226.313 | 6 | Replace section 12 to 32 ft from 00641. | 1200 | 1200 | Replace Section | Repair
1927 | 21 | D | SS.GM.T0009589 | SS.MH.T0000646 | SS.MH.T0000645 | 395.9231 | 6 | Point Repair at 22 ft from 00645 | 4750 | 4750 | Point Repair | Repair
1928 | 21 | B | SS.GM.T0009590 | SS.MH.T0000645 | SS.MH.T0000644 | 107.55 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1929 | 21 | B | SS.GM.T0009591 | SS.MH.T0000644 | SS.MH.T0000643 | 109.9058 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1930 | 21 | B | SS.GM.T0009592 | SS.MH.T0009710 | SS.MH.T0006855 | 79.1929 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1931 | 21 | B | SS.GM.T0009593 | SS.MH.T0006855 | SS.MH.T0006851 | 128.9911 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1932 | 21 | B | SS.GM.T0009594 | SS.MH.T0009709 | SS.MH.T0000648 | 267.8 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1933 | 21 | B | SS.GM.T0009595 | SS.MH.T0000648 | SS.MH.T0000647 | 88.7466 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1934 | 21 | C | SS.GM.T0009596 | SS.MH.T0000647 | SS.MH.T0015735 | 273.7 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1935 | 21 | B | SS.GM.T0009597 | SS.MH.T0009520 | SS.MH.T0006856 | 254.2457 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1936 | 21 | B | SS.GM.T0009598 | SS.MH.T0006856 | SS.MH.T0006042 | 370.2527 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1937 | 21 | D | SS.GM.T0009599 | SS.MH.T0006071 | SS.MH.T0006070 | 452.211 | 6 | Point Repair at 349 ft from 06070 | 4750 | 4750 | Point Repair | Repair
1938 | 21 | B | SS.GM.T0009602 | SS.MH.T0006075 | SS.MH.T0006859 | 263.7001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1939 | 21 | B | SS.GM.T0009607 | SS.MH.T0006878 | SS.MH.T0006877 | 304.8682 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1940 | 21 | B | SS.GM.T0009608 | SS.MH.T0006881 | SS.MH.T0006880 | 322.5 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1941 | 21 | B | SS.GM.T0009609 | SS.MH.T0006880 | SS.MH.T0006879 | 248.9342 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1942 | 21 | B | SS.GM.T0009610 | SS.MH.T0006879 | SS.MH.T0006877 | 75.0431 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1943 | 21 | B | SS.GM.T0009611 | SS.MH.T0006877 | SS.MH.T0013204 | 391.1959 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1944 | 21 | B | SS.GM.T0009612 | SS.MH.T0006862 | SS.MH.T0008617 | 219.5 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1945 | 21 | B | SS.GM.T0009613 | SS.MH.T0007006 | SS.MH.T0007005 | 137.4512 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1946 | 21 | B | SS.GM.T0009614 | SS.MH.T0007005 | SS.MH.T0007004 | 125.0012 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1947 | 21 | B | SS.GM.T0009615 | SS.MH.T0006863 | SS.MH.T0013204 | 177.4068 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1948 | 21 | B | SS.GM.T0009616 | SS.MH.T0007008 | SS.MH.T0007007 | 197.6 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1949 | 21 | B | SS.GM.T0009617 | SS.MH.T0007007 | SS.MH.T0006865 | 92.7165 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1950 | 21 | B | SS.GM.T0009618 | SS.MH.T0006876 | SS.MH.T0007011 | 165.9662 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1951 | 21 | B | SS.GM.T0009619 | SS.MH.T0007011 | SS.MH.T0007010 | 106.6 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1952 | 21 | B | SS.GM.T0009620 | SS.MH.T0007010 | SS.MH.T0007009 | 288.3003 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1953 | 21 | B | SS.GM.T0009621 | SS.MH.T0007009 | SS.MH.T0006865 | 80.7452 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1954 | 21 | B | SS.GM.T0009622 | SS.MH.T0006865 | SS.MH.T0006864 | 266.0094 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1955 | 21 | B | SS.GM.T0009623 | SS.MH.T0006864 | SS.MH.T0006863 | 179.1492 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1956 | 21 | D | SS.GM.T0009624 | SS.MH.T0009711 | SS.MH.T0006881 | 298.1 | 6 | Point Repair at 240 ft from 06881 | 4750 | 4750 | Point Repair | Repair
1957 | 21 | B | SS.GM.T0009625 | SS.MH.T0009714 | SS.MH.T0006870 | 96.4427 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1958 | 21 | B | SS.GM.T0009626 | SS.MH.T0006870 | SS.MH.T0006878 | 348.7894 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1959 | 21 | C | SS.GM.T0009627 | SS.MH.T0009713 | SS.MH.T0006871 | 186.1002 | 6 | Point Repair at 14 ft from 06871 | 4750 | 0 | Monitor in CMOM | None
1960 | 21 | B | SS.GM.T0009628 | SS.MH.T0006871 | SS.MH.T0006870 | 398.3839 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1961 | 21 | B | SS.GM.T0009629 | SS.MH.T0009712 | SS.MH.T0013058 | 186.9356 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1962 | 21 | B | SS.GM.T0009630 | SS.MH.T0006869 | SS.MH.T0006868 | 46.7138 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1963 | 21 | C | SS.GM.T0009631 | SS.MH.T0006868 | SS.MH.T0006866 | 414.1631 | 6 | Point Repair at 33 amd 34 ft from 06868 | 9500 | 0 | Monitor in CMOM | None
1964 | 21 | B | SS.GM.T0009633 | SS.MH.T0006866 | SS.MH.T0006878 | 221.928 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1965 | 21 | B | SS.GM.T0009634 | SS.MH.T0006875 | SS.MH.T0006874 | 81.6458 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1966 | 21 | B | SS.GM.T0009635 | SS.MH.T0006874 | SS.MH.T0006873 | 195.1001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1967 | 21 | B | SS.GM.T0009636 | SS.MH.T0006873 | SS.MH.T0006872 | 78.9999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1968 | 21 | B | SS.GM.T0009637 | SS.MH.T0006872 | SS.MH.T0007006 | 401.9946 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1969 | 21 | B | SS.GM.T0009639 | SS.MH.T0007016 | SS.MH.T0007015 | 97.5701 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1970 | 21 | B | SS.GM.T0009640 | SS.MH.T0007015 | SS.MH.T0007014 | 52.7537 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1971 | 21 | B | SS.GM.T0009641 | SS.MH.T0007014 | SS.MH.T0007013 | 192.7245 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1972 | 21 | B | SS.GM.T0009642 | SS.MH.T0007013 | SS.MH.T0007012 | 361.2717 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1973 | 21 | B | SS.GM.T0009643 | SS.MH.T0007012 | SS.MH.T0009036 | 114.2396 | 15 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1974 | 21 | B | SS.GM.T0009644 | SS.MH.T0007017 | SS.MH.T0007897 | 207.2533 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1975 | 21 | B | SS.GM.T0009645 | SS.MH.T0007895 | SS.MH.T0007017 | 402.6628 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1976 | 21 | B | SS.GM.T0009646 | SS.MH.T0006925 | SS.MH.T0006075 | 365.8369 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1977 | 21 | B | SS.GM.T0009656 | SS.MH.T0009715 | SS.MH.T0007028 | 90.5001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1978 | 21 | B | SS.GM.T0009657 | SS.MH.T0007028 | SS.MH.T0006875 | 86.8818 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1979 | 21 | B | SS.GM.T0009658 | SS.MH.T0014726 | SS.MH.T0008605 | 260.8 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1980 | 21 | B | SS.GM.T0009659 | SS.MH.T0010326 | SS.MH.T0006876 | 132.3683 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1981 | 21 | B | SS.GM.T0009660 | SS.MH.T0009685 | SS.MH.T0006886 | 200.3002 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1982 | 21 | B | SS.GM.T0009661 | SS.MH.T0006886 | SS.MH.T0006885 | 164.175 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1983 | 21 | B | SS.GM.T0009662 | SS.MH.T0009686 | SS.MH.T0006885 | 98.4001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1984 | 21 | B | SS.GM.T0009663 | SS.MH.T0006885 | SS.MH.T0006884 | 389.4467 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1985 | 21 | B | SS.GM.T0009664 | SS.MH.T0009716 | SS.MH.T0015737 | 309.4999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1986 | 21 | C | SS.GM.T0009665 | SS.MH.T0006889 | SS.MH.T0006888 | 102.0576 | 6 | Point Repair at 96 ft from 06888 | 4750 | 0 | Monitor in CMOM | None
1987 | 21 | B | SS.GM.T0009666 | SS.MH.T0006888 | SS.MH.T0006887 | 167.7639 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1988 | 21 | B | SS.GM.T0009667 | SS.MH.T0006887 | SS.MH.T0006884 | 139.0054 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1989 | 21 | B | SS.GM.T0009669 | SS.MH.T0010325 | SS.MH.T0006882 | 82.1532 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1990 | 21 | D | SS.GM.T0009670 | SS.MH.T0006882 | SS.MH.T0006883 | 338.7546 | 6 | Point Repair at 311 ft from 06882 | 4750 | 4750 | Point Repair | Repair
1991 | 21 | B | SS.GM.T0009671 | SS.MH.T0000842 | SS.MH.T0006887 | 306.1718 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1992 | 21 | B | SS.GM.T0009672 | SS.MH.T0010327 | SS.MH.T0000842 | 199.5545 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1993 | 21 | B | SS.GM.T0009673 | SS.MH.T0000843 | SS.MH.T0000842 | 312.0752 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1994 | 21 | B | SS.GM.T0009674 | SS.MH.T0010328 | SS.MH.T0000843 | 207.4437 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1995 | 21 | B | SS.GM.T0009675 | SS.MH.T0010329 | SS.MH.T0000843 | 89.9998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1996 | 21 | D | SS.GM.T0009783 | SS.MH.T0011912 | SS.MH.T0000335 | 233 | 6 | Burst to 8" - 4 svc | 19145.0025 | 19145.0025 | Pipe Burst or Replace | Replace
1997 | 21 | D | SS.GM.T0009784 | SS.MH.T0011913 | SS.MH.T0006346 | 454.8735 | 6 | Burst to 8" - 8 svc | 37566.7748 | 37566.7748 | Pipe Burst or Replace | Replace
1998 | 21 | C | SS.GM.T0009785 | SS.MH.T0011914 | SS.MH.T0006415 | 325.1559 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
1999 | 21 | B | SS.GM.T0009786 | SS.MH.T0006794 | SS.MH.T0006359 | 438.7191 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2000 | 21 | D | SS.GM.T0009787 | SS.MH.T0011501 | SS.MH.T0006344 | 181 | 6 | Point Repair at 180 ft from 06344. Crossbore | 4750 | 4750 | Point Repair | Repair
2001 | 21 | B | SS.GM.T0009789 | SS.MH.T0011503 | SS.MH.T0006006 | 29.6998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2002 | 21 | B | SS.GM.T0009790 | SS.MH.T0000643 | SS.MH.T0000642 | 109.4632 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2003 | 21 | B | SS.GM.T0009791 | SS.MH.T0000642 | SS.MH.T0000641 | 109.8185 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2004 | 21 | B | SS.GM.T0009792 | SS.MH.T0011504 | SS.MH.T0006201 | 130.7999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2005 | 21 | B | SS.GM.T0009793 | SS.MH.T0000689 | SS.MH.T0006910 | 209.5018 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2006 | 21 | B | SS.GM.T0009799 | SS.MH.T0011507 | SS.MH.T0007018 | 206.521 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2007 | 21 | B | SS.GM.T0010239 | SS.MH.T0008656 | SS.MH.T0008647 | 402.7564 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2008 | 21 | D | SS.GM.T0010240 | SS.MH.T0009826 | SS.MH.T0008646 | 481.4546 | 6 | Point Repair at 376 ft from 08646 | 4750 | 4750 | Point Repair | Repair
2009 | 21 | B | SS.GM.T0010241 | SS.MH.T0008644 | SS.MH.T0008646 | 380.1934 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2010 | 21 | B | SS.GM.T0010242 | SS.MH.T0008638 | SS.MH.T0008639 | 220.6824 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2011 | 21 | B | SS.GM.T0010243 | SS.MH.T0008643 | SS.MH.T0008644 | 31.0381 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2012 | 21 | B | SS.GM.T0010244 | SS.MH.T0008641 | SS.MH.T0008643 | 196.6208 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2013 | 21 | B | SS.GM.T0010245 | SS.MH.T0010376 | SS.MH.T0008641 | 99.8135 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2014 | 21 | B | SS.GM.T0010246 | SS.MH.T0008642 | SS.MH.T0008643 | 88.6734 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2015 | 21 | B | SS.GM.T0010247 | SS.MH.T0007255 | SS.MH.T0007256 | 160.5526 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2016 | 21 | B | SS.GM.T0010248 | SS.MH.T0009823 | SS.MH.T0007255 | 405.6127 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2017 | 21 | B | SS.GM.T0010249 | SS.MH.T0008637 | SS.MH.T0008636 | 249.2496 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2018 | 21 | B | SS.GM.T0010250 | SS.MH.T0008635 | SS.MH.T0008634 | 186.5831 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2019 | 21 | B | SS.GM.T0010251 | SS.MH.T0008634 | SS.MH.T0008633 | 312.3322 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2020 | 21 | C | SS.GM.T0010252 | SS.MH.T0007794 | SS.MH.T0009289 | 407.6488 | 8 | Point Repair at 356 ft from 07794 | 4750 | 0 | Monitor in CMOM | None
2021 | 21 | B | SS.GM.T0010253 | SS.MH.T0009026 | SS.MH.T0009027 | 400.6302 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2022 | 21 | B | SS.GM.T0010254 | SS.MH.T0007678 | SS.MH.T0007677 | 157.9007 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2023 | 21 | B | SS.GM.T0010255 | SS.MH.T0009012 | SS.MH.T0009013 | 399.6168 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2024 | 21 | B | SS.GM.T0010256 | SS.MH.T0009014 | SS.MH.T0009015 | 385.9101 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2025 | 21 | D | SS.GM.T0010257 | SS.MH.T0009852 | SS.MH.T0009024 | 317.4078 | 6 | Point Repair at 194 ft from 09024 | 4750 | 4750 | Point Repair | Repair
2026 | 21 | B | SS.GM.T0010258 | SS.MH.T0009017 | SS.MH.T0009016 | 119.9202 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2027 | 21 | B | SS.GM.T0010259 | SS.MH.T0009022 | SS.MH.T0009021 | 149.3723 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2028 | 21 | D | SS.GM.T0010261 | SS.MH.T0009015 | SS.MH.T0007678 | 197.5724 | 6 | Burst to 8" - 0 svc | 12842.2063 | 12842.2063 | Pipe Burst or Replace | Replace
2029 | 21 | B | SS.GM.T0010262 | SS.MH.T0009032 | SS.MH.T0009031 | 202.9653 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2030 | 21 | B | SS.GM.T0010263 | SS.MH.T0009034 | SS.MH.T0009033 | 114.498 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2031 | 21 | B | SS.GM.T0010264 | SS.MH.T0009029 | SS.MH.T0007676 | 275.7419 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2032 | 21 | B | SS.GM.T0010431 | SS.MH.T0008661 | SS.MH.T0008660 | 297.0695 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2033 | 21 | B | SS.GM.T0010432 | SS.MH.T0013918 | SS.MH.T0008665 | 316.7415 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2034 | 21 | B | SS.GM.T0010433 | SS.MH.T0008671 | SS.MH.T0008664 | 97.2372 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2035 | 21 | B | SS.GM.T0010434 | SS.MH.T0009830 | SS.MH.T0008666 | 178.3117 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2036 | 21 | B | SS.GM.T0010435 | SS.MH.T0015738 | SS.MH.T0008662 | 356.6092 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2037 | 21 | B | SS.GM.T0010436 | SS.MH.T0009829 | SS.MH.T0008663 | 407.5092 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2038 | 21 | B | SS.GM.T0010437 | SS.MH.T0008689 | SS.MH.T0008688 | 287.5283 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2039 | 21 | B | SS.GM.T0010439 | SS.MH.T0013920 | SS.MH.T0008692 | 239.7999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2040 | 21 | B | SS.GM.T0010440 | SS.MH.T0008690 | SS.MH.T0008685 | 401.3259 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2041 | 21 | B | SS.GM.T0010441 | SS.MH.T0013919 | SS.MH.T0008692 | 139.2999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2042 | 21 | B | SS.GM.T0010443 | SS.MH.T0008685 | SS.MH.T0008684 | 197.1323 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2043 | 21 | B | SS.GM.T0010444 | SS.MH.T0008675 | SS.MH.T0008676 | 494.1117 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2044 | 21 | B | SS.GM.T0010445 | SS.MH.T0008676 | SS.MH.T0008608 | 154.1737 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2045 | 21 | B | SS.GM.T0010446 | SS.MH.T0013921 | SS.MH.T0008680 | 311.2629 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2046 | 21 | B | SS.GM.T0010701 | SS.MH.T0009035 | SS.MH.T0007497 | 394.7617 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2047 | 21 | B | SS.GM.T0010702 | SS.MH.T0007498 | SS.MH.T0007587 | 188.6787 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2048 | 21 | B | SS.GM.T0010703 | SS.MH.T0007497 | SS.MH.T0007498 | 143.8231 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2049 | 21 | B | SS.GM.T0010791 | SS.MH.T0007676 | SS.MH.T0007677 | 214.018 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2050 | 21 | B | SS.GM.T0011030 | SS.MH.T0015228 | SS.MH.T0015224 | 104 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2051 | 21 | B | SS.GM.T0011031 | SS.MH.T0015223 | SS.MH.T0008653 | 159.9999 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2052 | 21 | B | SS.GM.T0011032 | SS.MH.T0008653 | SS.MH.T0008654 | 171.976 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2053 | 21 | B | SS.GM.T0011033 | SS.MH.T0008654 | SS.MH.T0008655 | 146.1524 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2054 | 21 | B | SS.GM.T0011034 | SS.MH.T0008655 | SS.MH.T0008618 | 131.2487 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2055 | 21 | B | SS.GM.T0011035 | SS.MH.T0008618 | SS.MH.T0007790 | 120.8398 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2056 | 21 | D | SS.GM.T0011036 | SS.MH.T0007790 | SS.MH.T0007792 | 351.3804 | 8 | Point Repair at 340 ft from 07790 | 4750 | 4750 | Point Repair | Repair
2057 | 21 | B | SS.GM.T0011037 | SS.MH.T0007792 | SS.MH.T0007791 | 226.8895 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2058 | 21 | B | SS.GM.T0011038 | SS.MH.T0007791 | SS.MH.T0008607 | 225.7416 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2059 | 21 | D | SS.GM.T0011039 | SS.MH.T0008607 | SS.MH.T0007794 | 243.2644 | 8 | Point Repair at 175 ft from 08607 | 4750 | 4750 | Point Repair | Repair
2060 | 21 | B | SS.GM.T0011400 | SS.MH.T0007018 | SS.MH.T0007895 | 195.6848 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2061 | 21 | B | SS.GM.T0011401 | SS.MH.T0007893 | SS.MH.T0007895 | 299.9172 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2062 | 21 | B | SS.GM.T0011402 | SS.MH.T0007894 | SS.MH.T0007893 | 233.3687 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2063 | 21 | B | SS.GM.T0011403 | SS.MH.T0007896 | SS.MH.T0007015 | 176.1428 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2064 | 21 | B | SS.GM.T0011404 | SS.MH.T0007897 | SS.MH.T0007896 | 156.4112 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2065 | 21 | B | SS.GM.T0011527 | SS.MH.T0015212 | SS.MH.T0009034 | 149.9999 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2066 | 21 | D | SS.GM.T0012040 | SS.MH.T0008605 | SS.MH.T0015222 | 136.9999 | 6 | Point Repair at 113 and 139 ft from 08605 and 1 ft from 15222 | 14250 | 14250 | Point Repair | Repair
2067 | 21 | B | SS.GM.T0012050 | SS.MH.T0008640 | SS.MH.T0008641 | 215.3025 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2068 | 21 | B | SS.GM.T0012051 | SS.MH.T0008639 | SS.MH.T0008640 | 129.7942 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2069 | 21 | B | SS.GM.T0012052 | SS.MH.T0009825 | SS.MH.T0008642 | 68.1831 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2070 | 21 | B | SS.GM.T0012053 | SS.MH.T0008645 | SS.MH.T0008644 | 57.8856 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2071 | 21 | B | SS.GM.T0012054 | SS.MH.T0007256 | SS.MH.T0008645 | 118.1623 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2072 | 21 | B | SS.GM.T0012055 | SS.MH.T0008633 | SS.MH.T0007255 | 169.8423 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2073 | 21 | B | SS.GM.T0012056 | SS.MH.T0008636 | SS.MH.T0008634 | 86.1634 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2074 | 21 | B | SS.GM.T0012057 | SS.MH.T0009824 | SS.MH.T0008637 | 149.76 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2075 | 21 | B | SS.GM.T0012062 | SS.MH.T0007793 | SS.MH.T0008619 | 119.9428 | 10 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2076 | 21 | B | SS.GM.T0012081 | SS.MH.T0008606 | SS.MH.T0008607 | 278.0317 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2077 | 21 | B | SS.GM.T0012095 | SS.MH.T0008621 | SS.MH.T0013964 | 80.7322 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2078 | 21 | B | SS.GM.T0012098 | SS.MH.T0008648 | SS.MH.T0008656 | 397.8164 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2079 | 21 | B | SS.GM.T0012099 | SS.MH.T0008662 | SS.MH.T0006916 | 324.4692 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2080 | 21 | B | SS.GM.T0012100 | SS.MH.T0008664 | SS.MH.T0008663 | 305.2388 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2081 | 21 | B | SS.GM.T0012102 | SS.MH.T0009828 | SS.MH.T0008661 | 234.5002 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2082 | 21 | B | SS.GM.T0012103 | SS.MH.T0008665 | SS.MH.T0008667 | 225.3486 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2083 | 21 | B | SS.GM.T0012104 | SS.MH.T0008667 | SS.MH.T0008668 | 237.5937 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2084 | 21 | B | SS.GM.T0012105 | SS.MH.T0008668 | SS.MH.T0008669 | 97.9839 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2085 | 21 | B | SS.GM.T0012106 | SS.MH.T0008669 | SS.MH.T0008670 | 100.509 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2086 | 21 | B | SS.GM.T0012107 | SS.MH.T0008670 | SS.MH.T0008671 | 94.2882 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2087 | 21 | B | SS.GM.T0012108 | SS.MH.T0007004 | SS.MH.T0008622 | 82.2334 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2088 | 21 | C | SS.GM.T0012110 | SS.MH.T0008624 | SS.MH.T0008632 | 309.1061 | 6 | Point Repair at 134 and 305 ft from 08624 | 9500 | 0 | Monitor in CMOM | None
2089 | 21 | C | SS.GM.T0012111 | SS.MH.T0008623 | SS.MH.T0008624 | 218.6208 | 6 | Point Repair at 153 ft from 08623 | 4750 | 0 | Monitor in CMOM | None
2090 | 21 | B | SS.GM.T0012113 | SS.MH.T0008674 | SS.MH.T0008675 | 394.1357 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2091 | 21 | B | SS.GM.T0012114 | SS.MH.T0008677 | SS.MH.T0008676 | 238.6964 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2092 | 21 | B | SS.GM.T0012115 | SS.MH.T0008678 | SS.MH.T0008677 | 73.9395 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2093 | 21 | C | SS.GM.T0012116 | SS.MH.T0008679 | SS.MH.T0008678 | 65.7517 | 6 | Point Repair at 4 ft from 08678 | 4750 | 0 | Monitor in CMOM | None
2094 | 21 | B | SS.GM.T0012117 | SS.MH.T0008680 | SS.MH.T0008679 | 79.3856 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2095 | 21 | B | SS.GM.T0012118 | SS.MH.T0008681 | SS.MH.T0008608 | 96.0543 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2096 | 21 | B | SS.GM.T0012119 | SS.MH.T0008682 | SS.MH.T0008681 | 330.695 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2097 | 21 | B | SS.GM.T0012120 | SS.MH.T0008683 | SS.MH.T0008682 | 100.3284 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2098 | 21 | B | SS.GM.T0012121 | SS.MH.T0008684 | SS.MH.T0008683 | 95.5404 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2099 | 21 | B | SS.GM.T0012122 | SS.MH.T0008686 | SS.MH.T0008685 | 259.0895 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2100 | 21 | B | SS.GM.T0012123 | SS.MH.T0008687 | SS.MH.T0008686 | 82.0037 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2101 | 21 | B | SS.GM.T0012124 | SS.MH.T0008688 | SS.MH.T0008687 | 73.5826 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2102 | 21 | B | SS.GM.T0012125 | SS.MH.T0013922 | SS.MH.T0008689 | 192.0844 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2103 | 21 | B | SS.GM.T0012126 | SS.MH.T0008691 | SS.MH.T0008690 | 164.7407 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2104 | 21 | B | SS.GM.T0012127 | SS.MH.T0008692 | SS.MH.T0008691 | 135.4458 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2105 | 21 | C | SS.GM.T0012129 | SS.MH.T0008658 | SS.MH.T0008657 | 390.4079 | 6 | Point Repair at 332 ft from 06658 | 4750 | 0 | Monitor in CMOM | None
2106 | 21 | B | SS.GM.T0012130 | SS.MH.T0009832 | SS.MH.T0008694 | 242.8 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2107 | 21 | B | SS.GM.T0012131 | SS.MH.T0009827 | SS.MH.T0008695 | 124.4632 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2108 | 21 | B | SS.GM.T0012132 | SS.MH.T0008657 | SS.MH.T0008605 | 52.0617 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2109 | 21 | B | SS.GM.T0012133 | SS.MH.T0008694 | SS.MH.T0014726 | 196.2051 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2110 | 21 | B | SS.GM.T0012135 | SS.MH.T0008695 | SS.MH.T0008659 | 233.6635 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2111 | 21 | B | SS.GM.T0012136 | SS.MH.T0008659 | SS.MH.T0008658 | 97.1958 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2112 | 21 | B | SS.GM.T0012410 | SS.MH.T0008646 | SS.MH.T0008651 | 212.1082 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2113 | 21 | B | SS.GM.T0012634 | SS.MH.T0008649 | SS.MH.T0008648 | 156.0921 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2114 | 21 | C | SS.GM.T0012635 | SS.MH.T0008647 | SS.MH.T0008646 | 398.2673 | 8 | Point Repair at 356 ft from 08647 | 4750 | 0 | Monitor in CMOM | None
2115 | 21 | B | SS.GM.T0012636 | SS.MH.T0009024 | SS.MH.T0009014 | 231.4261 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2116 | 21 | B | SS.GM.T0012637 | SS.MH.T0009851 | SS.MH.T0009023 | 173.6733 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2117 | 21 | B | SS.GM.T0012638 | SS.MH.T0009023 | SS.MH.T0009022 | 251.3681 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2118 | 21 | C | SS.GM.T0012639 | SS.MH.T0009020 | SS.MH.T0009019 | 96.4394 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2119 | 21 | B | SS.GM.T0012640 | SS.MH.T0009021 | SS.MH.T0009020 | 46.8742 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2120 | 21 | B | SS.GM.T0012641 | SS.MH.T0009019 | SS.MH.T0009018 | 220.5602 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2121 | 21 | B | SS.GM.T0012642 | SS.MH.T0009018 | SS.MH.T0009017 | 96.1292 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2122 | 21 | B | SS.GM.T0012643 | SS.MH.T0009016 | SS.MH.T0009015 | 92.3275 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2123 | 21 | B | SS.GM.T0012644 | SS.MH.T0009849 | SS.MH.T0009019 | 92.7404 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2124 | 21 | B | SS.GM.T0012645 | SS.MH.T0009853 | SS.MH.T0009025 | 246.3819 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2125 | 21 | B | SS.GM.T0012646 | SS.MH.T0009025 | SS.MH.T0009026 | 247.4057 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2126 | 21 | B | SS.GM.T0012647 | SS.MH.T0009028 | SS.MH.T0007678 | 218.4408 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2127 | 21 | C | SS.GM.T0012648 | SS.MH.T0009027 | SS.MH.T0009028 | 178.6502 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2128 | 21 | B | SS.GM.T0012649 | SS.MH.T0009033 | SS.MH.T0009031 | 68.665 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2129 | 21 | B | SS.GM.T0012650 | SS.MH.T0009854 | SS.MH.T0009032 | 148.7746 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2130 | 21 | B | SS.GM.T0012651 | SS.MH.T0009031 | SS.MH.T0009030 | 167.6514 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2131 | 21 | B | SS.GM.T0012652 | SS.MH.T0009030 | SS.MH.T0009029 | 117.6897 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2132 | 21 | B | SS.GM.T0012653 | SS.MH.T0013929 | SS.MH.T0009012 | 372.6355 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2133 | 21 | B | SS.GM.T0012654 | SS.MH.T0009013 | SS.MH.T0009014 | 180.6707 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2134 | 21 | B | SS.GM.T0012904 | SS.MH.T0006359 | SS.MH.T0006358 | 145.1137 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2135 | 21 | B | SS.GM.T0012967 | SS.MH.T0007499 | SS.MH.T0009035 | 381.536 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2136 | 21 | C | SS.GM.T0012973 | SS.MH.T0015217 | SS.MH.T0015744 | 151.8001 | 6 | Point Repair at 40 and 49 ft from 15217 | 9500 | 0 | Monitor in CMOM | None
2137 | 21 | B | SS.GM.T0012985 | SS.MH.T0008650 | SS.MH.T0008649 | 80.6022 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2138 | 21 | B | SS.GM.T0012999 | SS.MH.T0007677 | SS.LS.T0000002 | 8.7277 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2139 | 21 | B | SS.GM.T0013150 | SS.MH.T0009289 | SS.MH.T0007793 | 165.5487 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2140 | 21 | B | SS.GM.T0013197 | SS.MH.T0013058 | SS.MH.T0006869 | 68.7094 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2141 | 21 | B | SS.GM.T0013384 | SS.MH.T0013204 | SS.MH.T0008621 | 166.7017 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2142 | 21 | B | SS.GM.T0013700 | SS.MH.T0006930 | SS.MH.T0013691 | 30.9034 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2143 | 21 | B | SS.GM.T0013701 | SS.MH.T0013690 | SS.MH.T0013691 | 129.9605 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2144 | 21 | A | SS.GM.T0013702 | SS.MH.T0013689 | SS.MH.T0013690 | 162.3912 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2145 | 21 | A | SS.GM.T0013703 | SS.MH.T0013688 | SS.MH.T0013689 | 44.4397 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2146 | 21 | A | SS.GM.T0013704 | SS.MH.T0013687 | SS.MH.T0013688 | 211.0407 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2147 | 21 | A | SS.GM.T0013705 | SS.MH.T0013686 | SS.MH.T0013687 | 129.9913 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2148 | 21 | A | SS.GM.T0013706 | SS.MH.T0013685 | SS.MH.T0013686 | 104.5535 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2149 | 21 | A | SS.GM.T0013707 | SS.MH.T0013684 | SS.MH.T0013685 | 214.2059 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2150 | 21 | A | SS.GM.T0013708 | SS.MH.T0013683 | SS.MH.T0013684 | 234.3432 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2151 | 21 | A | SS.GM.T0013748 | SS.MH.T0013795 | SS.MH.T0013802 | 173.9752 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2152 | 21 | A | SS.GM.T0013750 | SS.MH.T0013804 | SS.MH.T0013800 | 351.1682 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2153 | 21 | A | SS.GM.T0013752 | SS.MH.T0013800 | SS.MH.T0013799 | 241.2216 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2154 | 21 | A | SS.GM.T0013753 | SS.MH.T0013799 | SS.MH.T0013798 | 355.206 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2155 | 21 | A | SS.GM.T0013754 | SS.MH.T0013798 | SS.MH.T0013797 | 356.8196 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2156 | 21 | A | SS.GM.T0013755 | SS.MH.T0014876 | SS.MH.T0013797 | 310.7824 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2157 | 21 | A | SS.GM.T0013756 | SS.MH.T0013797 | SS.MH.T0013796 | 56.7799 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2158 | 21 | A | SS.GM.T0013757 | SS.MH.T0013794 | SS.MH.T0013796 | 127.5 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2159 | 21 | A | SS.GM.T0013825 | SS.MH.T0013494 | SS.MH.T0006324 | 220.9999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2160 | 21 | B | SS.GM.T0013960 | SS.MH.T0013964 | SS.MH.T0006862 | 246.7086 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2161 | 21 | B | SS.GM.T0014012 | SS.MH.T0008622 | SS.MH.T0008621 | 95.7189 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2162 | 21 | A | SS.GM.T0014154 | SS.MH.T0014148 | SS.MH.T0014146 | 308.1048 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2163 | 21 | A | SS.GM.T0014155 | SS.MH.T0014146 | SS.MH.T0014147 | 100.4637 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2164 | 21 | A | SS.GM.T0014156 | SS.MH.T0014147 | SS.MH.T0007588 | 33.7947 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2165 | 21 | A | SS.GM.T0014157 | SS.MH.T0014149 | SS.MH.T0014148 | 315.972 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2166 | 21 | B | SS.GM.T0014572 | SS.MH.T0014693 | SS.MH.T0006929 | 63.1999 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2167 | 21 | B | SS.GM.T0014581 | SS.MH.T0007587 | SS.MH.T0007013 | 196.5118 | 12 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2168 | 21 | B | SS.GM.T0014603 | SS.MH.T0014730 | SS.MH.T0014729 | 209.9735 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2169 | 21 | A | SS.GM.T0014703 | SS.MH.T0014873 | SS.MH.T0014882 | 142.9388 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2170 | 21 | A | SS.GM.T0014704 | SS.MH.T0014882 | SS.MH.T0014883 | 123.1389 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2171 | 21 | A | SS.GM.T0014705 | SS.MH.T0014883 | SS.MH.T0014884 | 143.232 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2172 | 21 | A | SS.GM.T0014706 | SS.MH.T0014884 | SS.MH.T0014885 | 103.6381 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2173 | 21 | A | SS.GM.T0014707 | SS.MH.T0014885 | SS.MH.T0014886 | 116.5889 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2174 | 21 | A | SS.GM.T0014708 | SS.MH.T0014886 | SS.MH.T0014887 | 122.0454 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2175 | 21 | A | SS.GM.T0014709 | SS.MH.T0014887 | SS.MH.T0014876 | 220.3108 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2176 | 21 | A | SS.GM.T0014710 | SS.MH.T0014874 | SS.MH.T0014884 | 233.2142 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2177 | 21 | A | SS.GM.T0014711 | SS.MH.T0014880 | SS.MH.T0014879 | 147.4153 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2178 | 21 | A | SS.GM.T0014712 | SS.MH.T0014879 | SS.MH.T0014878 | 146.4278 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2179 | 21 | A | SS.GM.T0014713 | SS.MH.T0014878 | SS.MH.T0014877 | 200.1264 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2180 | 21 | A | SS.GM.T0014714 | SS.MH.T0014877 | SS.MH.T0014876 | 106.2668 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2181 | 21 | A | SS.GM.T0014715 | SS.MH.T0014881 | SS.MH.T0014880 | 109.4754 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2182 | 21 | D | SS.GM.T0015114 | SS.MH.T0014729 | SS.MH.T0006023 | 230.0597 | 6 | Grout Joint at 78 ft from 06023 | 800 | 800 | Grout Joints | Repair
2183 | 21 | A | SS.GM.T0015116 | SS.MH.T0013802 | SS.MH.T0013804 | 344.3377 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2184 | 21 | B | SS.GM.T0015125 | SS.MH.T0007972 | SS.MH.T0015217 | 187.6227 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2185 | 21 | B | SS.GM.T0015126 | SS.MH.T0015218 | SS.MH.T0006073 | 239 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2186 | 21 | B | SS.GM.T0015130 | SS.MH.T0015220 | SS.MH.T0013494 | 85.5 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2187 | 21 | D | SS.GM.T0015131 | SS.MH.T0015222 | SS.MH.T0008606 | 189.6492 | 6 | Replace section from 15222 to 40 ft from 15222. | 4800 | 4800 | Replace Section | Repair
2188 | 21 | D | SS.GM.T0015133 | SS.MH.T0015224 | SS.MH.T0008652 | 148.4113 | 8 | Point Repair at 3 ft from 15224 | 4750 | 4750 | Point Repair | Repair
2189 | 21 | B | SS.GM.T0015134 | SS.MH.T0008651 | SS.MH.T0015228 | 45.0001 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2190 | 21 | B | SS.GM.T0015135 | SS.MH.T0008652 | SS.MH.T0015223 | 23.9998 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2191 | 21 | B | SS.GM.T0015144 | SS.MH.T0015229 | SS.MH.T0008623 | 229 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2192 | 21 | A | SS.GM.T0015155 | SS.MH.T0015234 | SS.MH.T0015233 | 146.3267 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2193 | 21 | A | SS.GM.T0015156 | SS.MH.T0015233 | SS.MH.T0006161 | 63.1352 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2194 | 21 | A | SS.GM.T0015159 | SS.MH.T0015419 | SS.MH.T0015239 | 298.0002 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2195 | 21 | A | SS.GM.T0015160 | SS.MH.T0015239 | SS.MH.T0015238 | 224 | 8 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2196 | 21 | B | SS.GM.T0015532 | SS.MH.T0015735 | SS.MH.T0000646 | 67.4647 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2197 | 21 | C | SS.GM.T0015546 | SS.MH.T0005250 | SS.MH.T0015736 | 131.3557 | 15 | 15" CIPP - 0 svc | 10508.4569 | 0 | Monitor in CMOM | None
2198 | 21 | B | SS.GM.T0015548 | SS.MH.T0015737 | SS.MH.T0006889 | 59.2001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2199 | 21 | B | SS.GM.T0015555 | SS.MH.T0008666 | SS.MH.T0008665 | 154.2153 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2200 | 21 | B | SS.GM.T0015559 | SS.MH.T0008663 | SS.MH.T0015738 | 100.0001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2201 | 21 | B | SS.GM.T0015560 | SS.MH.T0015739 | SS.MH.T0006342 | 19.5001 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2202 | 21 | B | SS.GM.T0015592 | SS.MH.T0006163 | SS.MH.T0015745 | 282.6998 | 6 | No Rehabilitation Recommended | 0 | 0 | Monitor in CMOM | None
2203 | 21 | D | SS.GM.T0015593 | SS.MH.T0006934 | SS.MH.T0015883 | 260.2917 | 6 | Replace section 40 to 20 ft from 15833. | 2400 | 2400 | Replace Section | Repair
7161905.0746

## Mainline Remedial Measures Plan
[15 empty] | Condition Code | Occurrances | Est. Cost
[15 empty] | A | 102 | 0
[15 empty] | B | 1266 | 0
[15 empty] | C | 302 | 0
[15 empty] | D | 528 | 7123631.3062
[15 empty] | E | 5 | 38273.7684
[15 empty] | Total | 2203 | 7161905.0746
[15 empty] | Design and Contingency -15% |  | 1074285.7612
[15 empty] | Total Estimated Cost |  | 8236190.8358
*Note: Preliminary Recommendation may change during Final Design due to utility conflicts, adjacent repairs, etc.
Group 5 - Mainline Condition D and E Remedial Measures Plan
Basins 2, 7, 8, 10, 13, 16, 17, 18, 19, 20, 21
Item | Basin | Condition Rating | Map Grid | City Pipe Asset ID | Upstream Manhole | Downstream Manhole | Pipe Length (GIS) | Pipe Diameter (GIS) | Detailed Preliminary Rehabilitation Recommendation (Note:Preliminary Recommendation may change during Final Design due to utility conflicts, adjacent repairs, etc.) | Repair Cost | Estimated Cost | Comments | Description | Quantity | Estimated Cost
1 | 2 | D | L12 | SS.GM.T0005934 | SS.MH.T0002926 | SS.MH.T0013422 | 173.9318 | 8 | Point Repair at 92 ft and Grout Joint at 173 ft from 13422 | 5550 | 5550 |  | Access; Clean and Inspection - linear feet | 864.0604 | 4806.2416
2 | 7 | D | K13 | SS.GM.T0006595 | SS.MH.T0001113 | SS.MH.T0001116 | 612.3488 | 8 | Access; Clean and Inspection | 2449.3953 | 0 | Addressed in Capacity Remediations | Addressed in Capacity Remediations - linear feet | 2002.3803 | 0
3 | 7 | D | K14 | SS.GM.T0007632 | SS.MH.T0001975 | SS.MH.T0001098 | 455.0002 | 6 | Point Repair at 402 ft from 01098 | 4750 | 4750 |  | Cured In Place Pipe Liner - linear feet | 5277.8349 | 391564.9995
4 | 7 | D | L12 | SS.GM.T0007645 | SS.MH.T0001997 | SS.MH.T0001996 | 257.7503 | 6 | Grout Joint at 16 ft from 01996 | 800 | 800 |  | Grout Joints - each | 15 | 16880.0288
5 | 7 | D | K13 | SS.GM.T0007652 | SS.MH.T0001117 | SS.MH.T0001121 | 688.1153 | 8 | Point Repair at 309 and 562 ft from 01117 | 9500 | 0 | Addressed in Capacity Remediations | Pipe Burst or Replace - linear feet | 45605.2058 | 3423737.4505
6 | 7 | D | K13 | SS.GM.T0007656 | SS.MH.T0001122 | SS.MH.T0001123 | 286.8731 | 8 | Burst to 8" - 0 svc | 18646.7526 | 0 | Addressed in Capacity Remediations | Point Repair - each | 295 | 2610313.2496
7 | 8 | D | L14 | SS.GM.T0000397 | SS.MH.T0015262 | SS.MH.T0012830 | 640.2771 | 8 | Point Repair at 179, 183, 256, 440 and 519 ft from 15262 | 23750 | 23750 |  | Point Repair and Add to Root Removal Program - each | 23 | 213693.3695
8 | 8 | D | L14 | SS.GM.T0006450 | SS.MH.T0011034 | SS.MH.T0001726 | 687.3138 | 6 | Point Repair at 70 and 309 ft from 01726 | 9500 | 9500 |  | Replace - linear feet | 1253.4615 | 174939.402
9 | 8 | D | K13 | SS.GM.T0006645 | SS.MH.T0001036 | SS.MH.T0001035 | 529.825 | 21 | Grout Joint at 350 ft from 01036 | 800 | 800 |  | Replace Section - each | 34 | 325970.3331
10 | 8 | D | L14 | SS.GM.T0006730 | SS.MH.T0001813 | SS.MH.T0001815 | 235.1892 | 12 | 12" CIPP - 0 svc | 16463.247 | 0 | Addressed in Capacity Remediations |  | Total | 7161905.0746
11 | 8 | D | L14 | SS.GM.T0006734 | SS.MH.T0002560 | SS.MH.T0002556 | 408.7401 | 8 | Burst to 10" - 1 svc | 31655.5058 | 31655.5058 |  | Design and Contingency -15% |  | 1074285.7612
12 | 8 | D | L15 | SS.GM.T0006766 | SS.MH.T0011845 | SS.MH.T0001910 | 363.7613 | 6 | Point Repair at 223 ft and Grout Joint at 40 ft from 01910 | 5550 | 5550 |  | Total Estimated Cost |  | 8236190.8358
13 | 8 | D | M15 | SS.GM.T0007150 | SS.MH.T0002617 | SS.MH.T0002616 | 185.7244 | 8 | 8" CIPP - 0 svc | 8357.5965 | 8357.5965
14 | 8 | D | M16 | SS.GM.T0007168 | SS.MH.T0003162 | SS.MH.T0012907 | 40.0144 | 6 | Grout Joint at 17, 23, 25 and 29 ft from 03162 | 3280.0288 | 3280.0288
15 | 8 | D | K14 | SS.GM.T0007617 | SS.MH.T0015647 | SS.MH.T0013042 | 103.8899 | 12 | 12" CIPP - 0 svc | 7272.2947 | 7272.2947
16 | 8 | D | K14 | SS.GM.T0007618 | SS.MH.T0013042 | SS.MH.T0001085 | 49.9164 | 12 | 12" CIPP - 0 svc | 3494.1488 | 3494.1488
17 | 8 | D | L15 | SS.GM.T0007988 | SS.MH.T0001937 | SS.MH.T0012877 | 226.5739 | 8 | Point Repair at 23, 36 and 59 ft from 01937 | 14250 | 14250
18 | 8 | D | L14 | SS.GM.T0013189 | SS.MH.T0001983 | SS.MH.T0015276 | 329.0679 | 12 | Replace - 0 svc | 47714.8432 | 47714.8432
19 | 8 | D | L15 | SS.GM.T0013937 | SS.MH.T0013727 | SS.MH.T0001909 | 627.9981 | 6 | Burst to 8" - 8 svc | 48819.8784 | 48819.8784
20 | 10 | D | M12 | SS.GM.T0004093 | SS.MH.T0002981 | SS.MH.T0002980 | 475.7 | 8 | Point Repair at 165 ft from 02981 | 4750 | 4750
21 | 10 | D | N13 | SS.GM.T0004132 | SS.MH.T0004468 | SS.MH.T0004469 | 87.0829 | 6 | Point Repair at 85 ft from 04468 | 4750 | 4750
22 | 10 | D | M13 | SS.GM.T0007032 | SS.MH.T0000671 | SS.MH.T0002811 | 336.718 | 8 | Point Repair at 85 and 185 ft and Grout Joint at 8 ft from 02811 | 10300 | 10300
23 | 13 | D | N14 | SS.GM.T0004865 | SS.MH.T0010949 | SS.MH.T0005106 | 320.0106 | 6 | Replace section 0 to 80 ft from 05106. Point Repair at 128 ft from 05106 | 14350 | 14350
24 | 13 | D | M13 | SS.GM.T0005511 | SS.MH.T0011758 | SS.MH.T0012797 | 129.8203 | 6 | Point Repair at 109 ft from 12797 | 4750 | 4750
25 | 13 | D | N15 | SS.GM.T0006117 | SS.MH.T0012077 | SS.MH.T0014073 | 66.13 | 6 | Point Repair at 13 ft from 14073 | 4750 | 4750
26 | 13 | D | N15 | SS.GM.T0006132 | SS.MH.T0004928 | SS.MH.T0004925 | 381.8625 | 18 | Point Repair at 100 ft from 04925 | 4750 | 4750
27 | 13 | D | M16 | SS.GM.T0006316 | SS.MH.T0011441 | SS.MH.T0012853 | 350.9693 | 6 | Point Repair at 28 ft from 12853 | 4750 | 4750
28 | 13 | D | M14 | SS.GM.T0006487 | SS.MH.T0012269 | SS.MH.T0003078 | 157.8799 | 6 | Burst to 8" - 4 svc | 14262.1931 | 14262.1931
29 | 13 | D | M16 | SS.GM.T0007113 | SS.MH.T0011444 | SS.MH.T0012855 | 192.3337 | 6 | Point Repair at 111 ft from 12855 | 4750 | 4750
30 | 13 | D | N16 | SS.GM.T0009043 | SS.MH.T0004809 | SS.MH.T0004808 | 39.0774 | 6 | Burst to 8" - 0 svc | 2540.0335 | 2540.0335
31 | 13 | D | N17 | SS.GM.T0009046 | SS.MH.T0004835 | SS.MH.T0004830 | 405.9375 | 8 | Point Repair at 355 ft from 04835 | 4750 | 4750
32 | 13 | D | N15 | SS.GM.T0009716 | SS.MH.T0005035 | SS.MH.T0005043 | 179.8539 | 12 | Access; Clean and Inspection | 719.4155 | 0 | Addressed in Capacity Remediations
33 | 13 | D | N16 | SS.GM.T0009719 | SS.MH.T0005860 | SS.MH.T0003208 | 537.6248 | 6 | Point Repair at 37 ft from 05860(Cross bore) & Replace section 80 to 30 ft from 03208 | 10750 | 10750
34 | 17 | D | M19 | SS.GM.T0000909 | SS.MH.T0013508 | SS.MH.T0003539 | 62.2033 | 15 | Burst to 18" - 0 svc | 5909.3138 | 5909.3138
35 | 17 | D | L18 | SS.GM.T0000926 | SS.MH.T0002397 | SS.MH.T0002398 | 348.9197 | 8 | Burst to 10" - 2 svc | 28168.9742 | 28168.9742
36 | 17 | D | L18 | SS.GM.T0000927 | SS.MH.T0014133 | SS.MH.T0002397 | 307.3874 | 6 | Point Repair at 10, 158 and 211 ft from 14133 | 14250 | 14250
37 | 17 | D | L18 | SS.GM.T0000928 | SS.MH.T0002395 | SS.MH.T0002396 | 326.9398 | 6 | Point Repair at 58, 60, 104, 135 & 152 ft from 02395 | 23750 | 23750
38 | 17 | D | L18 | SS.GM.T0000929 | SS.MH.T0002394 | SS.MH.T0002395 | 360.3383 | 6 | Burst to 8" - 0 svc | 23421.9877 | 23421.9877
39 | 17 | D | M20 | SS.GM.T0001108 | SS.MH.T0003528 | SS.MH.T0015638 | 294.6784 | 12 | Point Repair at 44 and Grout Joint at 218 and 220 ft from 03528 | 6350 | 6350
40 | 17 | D | M20 | SS.GM.T0001118 | SS.MH.T0003597 | SS.MH.T0003598 | 272.1908 | 18 | 18" CIPP - 0 svc | 32662.9011 | 32662.9011
41 | 17 | D | L20 | SS.GM.T0001133 | SS.MH.T0001557 | SS.MH.T0014669 | 38.8154 | 6 | Point Repair at 10 and 34 ft from 01557 | 9500 | 9500
42 | 17 | D | M20 | SS.GM.T0001594 | SS.MH.T0003598 | SS.MH.T0003599 | 91.4484 | 18 | 18" CIPP - 0 svc | 10973.8074 | 10973.8074
43 | 17 | D | M21 | SS.GM.T0001595 | SS.MH.T0003599 | SS.MH.T0014697 | 84.0401 | 18 | 18" CIPP - 0 svc | 10084.8154 | 10084.8154
44 | 17 | D | M21 | SS.GM.T0001596 | SS.MH.T0003549 | SS.MH.T0015480 | 284.3269 | 6 | Point Repair at 82 and 110 ft from 03549 | 9500 | 9500
45 | 17 | D | L21 | SS.GM.T0001923 | SS.MH.T0001700 | SS.MH.T0003557 | 71.1175 | 6 | Burst to 8" - 0 svc | 4622.6378 | 4622.6378
46 | 17 | D | L21 | SS.GM.T0002217 | SS.MH.T0011979 | SS.MH.T0005592 | 136.8958 | 6 | Point Repair at 110 ft from 05592 | 4750 | 4750
47 | 17 | D | M22 | SS.GM.T0002290 | SS.MH.T0003755 | SS.MH.T0003757 | 330.4925 | 10 | 10" CIPP - 0 svc | 16524.6254 | 16524.6254
48 | 17 | D | M18 | SS.GM.T0002489 | SS.MH.T0003435 | SS.MH.T0003433 | 143.9372 | 6 | Point Repair at 36 ft from 03435 | 4750 | 4750
49 | 17 | D | M18 | SS.GM.T0002529 | SS.MH.T0001503 | SS.MH.T0015278 | 364.9959 | 6 | Point Repair at 298 ft from 01503 | 4750 | 4750
50 | 17 | D | N21 | SS.GM.T0002653 | SS.MH.T0009895 | SS.MH.T0000318 | 158.5893 | 6 | Point Repair at 54 ft from 00318 | 4750 | 4750
51 | 17 | D | N21 | SS.GM.T0002656 | SS.MH.T0009892 | SS.MH.T0005479 | 311.8233 | 6 | Point Repair at 29 ft from 05479 | 4750 | 4750
52 | 17 | D | M18 | SS.GM.T0003161 | SS.MH.T0011220 | SS.MH.T0002436 | 486.9999 | 6 | Point Repair at 21 and 58 ft from 02436 | 9500 | 9500
53 | 17 | D | L19 | SS.GM.T0003383 | SS.MH.T0001526 | SS.MH.T0001525 | 282.93 | 8 | Access; Clean and Inspection | 1131.72 | 1131.72
54 | 17 | D | L21 | SS.GM.T0010267 | SS.MH.T0009099 | SS.MH.T0001440 | 339.9034 | 8 | Replace section from 270 ft from 01440 to 09099. | 9100 | 9100
55 | 17 | D | L18 | SS.GM.T0014106 | SS.MH.T0002396 | SS.MH.T0014133 | 47.6917 | 6 | Point Repair at 24 ft from 02396 | 4750 | 4750
56 | 17 | D | M21 | SS.GM.T0014577 | SS.MH.T0014697 | SS.MH.T0003548 | 49.8733 | 18 | 18" CIPP - 0 svc | 5984.7989 | 5984.7989
57 | 18 | D | N18 | SS.GM.T0000345 | SS.MH.T0002531 | SS.MH.T0004298 | 519.3676 | 6 | Burst to 8" - 0 svc | 33758.8935 | 33758.8935
58 | 18 | D | N18 | SS.GM.T0000346 | SS.MH.T0004296 | SS.MH.T0004297 | 378.6413 | 6 | Point Repair at 227 ft from 04296 | 4750 | 4750
59 | 18 | D | N18 | SS.GM.T0000348 | SS.MH.T0004291 | SS.MH.T0004290 | 339.0912 | 6 | Burst to 8" - 2 svc | 24040.9296 | 24040.9296
60 | 18 | D | N18 | SS.GM.T0000349 | SS.MH.T0004299 | SS.MH.T0004291 | 339.2652 | 6 | Burst to 8" - 3 svc | 25052.237 | 25052.237
61 | 18 | D | N18 | SS.GM.T0000356 | SS.MH.T0004275 | SS.MH.T0004274 | 662.2967 | 6 | Burst to 8" - 7 svc | 50049.2873 | 50049.2873
62 | 18 | D | N18 | SS.GM.T0000357 | SS.MH.T0004276 | SS.MH.T0004275 | 319.5469 | 6 | Burst to 8" - 5 svc | 25770.5471 | 25770.5471
63 | 18 | D | N17 | SS.GM.T0000383 | SS.MH.T0012301 | SS.MH.T0002531 | 357.2506 | 6 | Point Repair at 35 and 181 ft from 02531 | 9500 | 9500
64 | 18 | D | N18 | SS.GM.T0000384 | SS.MH.T0012313 | SS.MH.T0004296 | 542.3684 | 6 | Burst to 8" - 7 svc | 42253.9465 | 42253.9465
65 | 18 | D | N18 | SS.GM.T0000385 | SS.MH.T0010685 | SS.MH.T0004296 | 361.5027 | 6 | Point Repair at 89 ft from 04296 | 4750 | 4750
66 | 18 | D | N18 | SS.GM.T0000386 | SS.MH.T0012305 | SS.MH.T0004297 | 264.6486 | 6 | Point Repair at 22 ft from 04297 | 4750 | 4750
67 | 18 | D | N18 | SS.GM.T0000387 | SS.MH.T0011183 | SS.MH.T0004295 | 274.5288 | 6 | Point Repair at 102 ft from 04295 | 4750 | 4750
68 | 18 | D | N18 | SS.GM.T0000388 | SS.MH.T0011518 | SS.MH.T0004291 | 441.8862 | 6 | Point Repair at 7, 102 and 130 ft from 04291 and Add to Root Removal Schedule | 15133.7725 | 15133.7725
69 | 18 | D | N18 | SS.GM.T0000389 | SS.MH.T0010683 | SS.MH.T0004299 | 401.5293 | 6 | Burst to 8" - 0 svc | 26099.4056 | 26099.4056
70 | 18 | D | N18 | SS.GM.T0000390 | SS.MH.T0011939 | SS.MH.T0004275 | 606.0698 | 6 | Burst to 8" - 10 svc | 49394.5355 | 49394.5355
71 | 18 | D | N18 | SS.GM.T0000391 | SS.MH.T0012317 | SS.MH.T0004276 | 644.5432 | 6 | Burst to 8" - 4 svc | 45895.31 | 45895.31
72 | 18 | D | N18 | SS.GM.T0000392 | SS.MH.T0011193 | SS.MH.T0004276 | 243.6771 | 6 | Burst to 8" - 4 svc | 19839.0088 | 19839.0088
73 | 18 | D | N18 | SS.GM.T0000393 | SS.MH.T0010697 | SS.MH.T0004287 | 270.9627 | 6 | Burst to 8" - 2 svc | 19612.5761 | 19612.5761
74 | 18 | D | N17 | SS.GM.T0000394 | SS.MH.T0010846 | SS.MH.T0004248 | 312.3522 | 6 | Burst to 8" - 1 svc | 21302.896 | 21302.896
75 | 18 | D | N17 | SS.GM.T0000395 | SS.MH.T0010851 | SS.MH.T0004249 | 259.3462 | 6 | Point Repair at 191 ft from 04249 | 4750 | 4750
76 | 18 | D | N18 | SS.GM.T0000399 | SS.MH.T0004317 | SS.MH.T0004316 | 396.8171 | 6 | Burst to 8" - 10 svc | 35793.1102 | 35793.1102
77 | 18 | D | N18 | SS.GM.T0000402 | SS.MH.T0006330 | SS.MH.T0006336 | 1053.6361 | 6 | Burst to 8" - 10 svc | 78486.3491 | 78486.3491
78 | 18 | D | N17 | SS.GM.T0000406 | SS.MH.T0000334 | SS.MH.T0006326 | 303.3219 | 6 | Burst to 8" - 2 svc | 21715.9204 | 21715.9204
79 | 18 | D | N18 | SS.GM.T0000410 | SS.MH.T0005999 | SS.MH.T0004307 | 226.5813 | 6 | Burst to 8" - 2 svc | 16727.7861 | 16727.7861
80 | 18 | D | N18 | SS.GM.T0000415 | SS.MH.T0004312 | SS.MH.T0004313 | 323.5381 | 8 | Point Repair at 320 ft from 04213 and Add to Root Removal Schedule | 5397.0761 | 5397.0761
81 | 18 | D | N18 | SS.GM.T0000424 | SS.MH.T0005241 | SS.MH.T0005239 | 363.6878 | 6 | Burst to 8" - 0 svc | 23639.7056 | 23639.7056
82 | 18 | D | N18 | SS.GM.T0000425 | SS.MH.T0005236 | SS.MH.T0005235 | 356.8407 | 6 | Burst to 8" - 0 svc | 23194.6435 | 23194.6435
83 | 18 | D | N18 | SS.GM.T0000427 | SS.MH.T0004331 | SS.MH.T0004330 | 300.0123 | 6 | Point Repair at 71 and 219 ft from 04331 | 9500 | 9500
84 | 18 | D | N18 | SS.GM.T0000430 | SS.MH.T0004332 | SS.MH.T0000749 | 238.5659 | 6 | Grout Joint at 26 ft from 04332 | 800 | 800
85 | 18 | D | N18 | SS.GM.T0000432 | SS.MH.T0005147 | SS.MH.T0005142 | 324.7356 | 6 | Point Repair at 7 and 161 ft from 05147 | 9500 | 9500
86 | 18 | D | N18 | SS.GM.T0000433 | SS.MH.T0004311 | SS.MH.T0005147 | 521.8404 | 6 | Point Repair at 119, 188 and 195 ft from 04310 and 115 ft from 04311 | 14250 | 14250
87 | 18 | D | N18 | SS.GM.T0000447 | SS.MH.T0005149 | SS.MH.T0005150 | 328.8734 | 6 | Point Repair at 90, 100 and 174 ft from 05149 and 54 ft from 05150 | 19000 | 19000
88 | 18 | D | N18 | SS.GM.T0000449 | SS.MH.T0005226 | SS.MH.T0005227 | 185.8646 | 6 | Burst to 8" - 0 svc | 12081.1976 | 12081.1976
89 | 18 | D | N18 | SS.GM.T0000450 | SS.MH.T0005225 | SS.MH.T0005226 | 477.5496 | 6 | Burst to 8" - 7 svc | 38040.7259 | 38040.7259
90 | 18 | D | N19 | SS.GM.T0000451 | SS.MH.T0005232 | SS.MH.T0005226 | 532.418 | 6 | Point Repair at 46 ft from 05232 and 50 ft from 05226 | 9500 | 9500
91 | 18 | D | N19 | SS.GM.T0000452 | SS.MH.T0005233 | SS.MH.T0005232 | 349.9201 | 6 | Point Repair at 164 ft from 05232 and 148 ft from 05233 and Add to Root Removal Schedule | 10199.8402 | 10199.8402
92 | 18 | D | N19 | SS.GM.T0000546 | SS.MH.T0005178 | SS.MH.T0005179 | 462.9796 | 6 | Point Repair at 135, 136 and 176 ft from 05178 | 14250 | 14250
93 | 18 | D | N19 | SS.GM.T0000547 | SS.MH.T0005179 | SS.MH.T0000271 | 150.0166 | 6 | Burst to 8" - 0 svc | 9751.0822 | 9751.0822
94 | 18 | D | N19 | SS.GM.T0000552 | SS.MH.T0005169 | SS.MH.T0005170 | 249.5457 | 6 | Replace section 190 to 245 ft from 05170. | 6600 | 6600
95 | 18 | D | N18 | SS.GM.T0000649 | SS.MH.T0004345 | SS.MH.T0004344 | 72.9197 | 8 | Point Repair at 20 ft from 04344 and 36 ft from 04345 | 9500 | 9500
96 | 18 | D | O18 | SS.GM.T0000650 | SS.MH.T0013994 | SS.MH.T0015434 | 648.504 | 8 | Point Repair at 43 ft from 15434 and Grout Joint at 28, 106, 127 and 275 ft from 13994 | 7950 | 7950
97 | 18 | D | N18 | SS.GM.T0000656 | SS.MH.T0014963 | SS.MH.T0004335 | 656.831 | 6 | Burst to 8" - 10 svc | 52694.0148 | 52694.0148
98 | 18 | D | N18 | SS.GM.T0000657 | SS.MH.T0004340 | SS.MH.T0004338 | 181.0587 | 6 | Point Repair at 160 and 163 ft from 04340 | 9500 | 9500
99 | 18 | D | N18 | SS.GM.T0000659 | SS.MH.T0006399 | SS.MH.T0004338 | 490.8842 | 8 | Burst to 8" - 6 svc | 37907.4706 | 37907.4706
100 | 18 | D | N18 | SS.GM.T0000660 | SS.MH.T0006379 | SS.MH.T0006399 | 900.0069 | 6 | Point Repair at 52 and 75 ft from 06399 and Add to Root Removal Schedule | 11300.0138 | 11300.0138
101 | 18 | E | N18 | SS.GM.T0000663 | SS.MH.T0010862 | SS.MH.T0006399 | 334.3977 | 6 | Point Repair at 16 and 83 ft from 10862. Crossbore @ 83. Telephone pole | 9500 | 9500
102 | 18 | D | N18 | SS.GM.T0000666 | SS.MH.T0004341 | SS.MH.T0004342 | 662.8009 | 6 | Point Repair at 9 and 28 ft from 04341 and 155 and crossbore 227 ft from 04342 | 19000 | 19000
103 | 18 | D | N18 | SS.GM.T0000667 | SS.MH.T0011208 | SS.MH.T0004341 | 156.7598 | 6 | Point Repair at 71 and 81 ft from 04341 | 9500 | 9500
104 | 18 | D | N18 | SS.GM.T0000673 | SS.MH.T0011109 | SS.MH.T0005362 | 793.9355 | 6 | Point Repair at 47, 210, 224 and 239 ft from 05362 | 19000 | 19000
105 | 18 | D | N18 | SS.GM.T0000675 | SS.MH.T0010702 | SS.MH.T0005358 | 202.2603 | 6 | Point Repair at 92 and 95 ft from 05358 | 9500 | 9500
106 | 18 | D | N18 | SS.GM.T0000676 | SS.MH.T0005358 | SS.MH.T0005357 | 246.3239 | 6 | Burst to 8" - 3 svc | 19011.052 | 19011.052
107 | 18 | D | N18 | SS.GM.T0000678 | SS.MH.T0012306 | SS.MH.T0004317 | 463.5231 | 6 | Burst to 8" - 4 svc | 34129.003 | 34129.003
108 | 18 | D | N18 | SS.GM.T0000683 | SS.MH.T0012319 | SS.MH.T0004304 | 144.7359 | 6 | Point Repair at 107 ft from 04304 and Add to Root Removal Schedule | 5039.4717 | 5039.4717
109 | 18 | D | N18 | SS.GM.T0000684 | SS.MH.T0012320 | SS.MH.T0004300 | 180.533 | 6 | Point Repair at 127 ft from 04300 | 4750 | 4750
110 | 18 | D | N18 | SS.GM.T0000685 | SS.MH.T0012318 | SS.MH.T0004300 | 147.028 | 6 | Point Repair at 11 ft from 04300 | 4750 | 4750
111 | 18 | D | N18 | SS.GM.T0000688 | SS.MH.T0011206 | SS.MH.T0005240 | 429.2313 | 6 | Point Repair at 49, 174 and 276 ft from 05240 | 14250 | 14250
112 | 18 | D | N18 | SS.GM.T0000689 | SS.MH.T0010997 | SS.MH.T0005241 | 595.7888 | 6 | Burst to 8" - 4 svc | 42726.275 | 42726.275
113 | 18 | D | N18 | SS.GM.T0000690 | SS.MH.T0011963 | SS.MH.T0005237 | 151.3225 | 6 | Point Repair at 63 ft from 05237 | 4750 | 4750
114 | 18 | D | N18 | SS.GM.T0000691 | SS.MH.T0011964 | SS.MH.T0005224 | 360.1646 | 6 | Point Repair at 136 ft from 05224 and Add to Root Removal Schedule | 5470.3293 | 5470.3293
115 | 18 | D | N18 | SS.GM.T0000693 | SS.MH.T0012343 | SS.MH.T0005235 | 112.8237 | 6 | Point Repair at 23 and 112 ft from 05235 | 9500 | 9500
116 | 18 | D | N18 | SS.GM.T0000694 | SS.MH.T0011959 | SS.MH.T0005236 | 244.5745 | 6 | Burst to 8" - 2 svc | 17897.3455 | 17897.3455
117 | 18 | D | N18 | SS.GM.T0000695 | SS.MH.T0011213 | SS.MH.T0004329 | 213.1631 | 6 | Burst to 8" - 7 svc | 20855.5983 | 20855.5983
118 | 18 | D | N18 | SS.GM.T0000697 | SS.MH.T0010690 | SS.MH.T0004334 | 301.1655 | 6 | Point Repair at 58 ft from 04334 | 4750 | 4750
119 | 18 | D | N18 | SS.GM.T0000698 | SS.MH.T0010689 | SS.MH.T0004331 | 617.594 | 6 | Point Repair at 237 ft from 04331 | 4750 | 4750
120 | 18 | D | N18 | SS.GM.T0000701 | SS.MH.T0010868 | SS.MH.T0005143 | 376.6786 | 6 | Point Repair at 48, 68, 123 and 254 ft from 05143 | 19000 | 19000
121 | 18 | D | N19 | SS.GM.T0000705 | SS.MH.T0006126 | SS.MH.T0013186 | 488.8097 | 6 | Point Repair at 21 ft from 06126 | 4750 | 4750
122 | 18 | D | N18 | SS.GM.T0000710 | SS.MH.T0006375 | SS.MH.T0006376 | 292.5669 | 6 | Point Repair at 99 and 139 ft from 06375 and 32 ft from 06376 Add to Root Removal Schedule | 14835.1337 | 14835.1337
123 | 18 | D | N17 | SS.GM.T0000711 | SS.MH.T0010850 | SS.MH.T0006375 | 426.5562 | 6 | Point Repair at 286 and 318 ft from 06375 | 9500 | 9500
124 | 18 | D | N18 | SS.GM.T0000715 | SS.MH.T0012182 | SS.MH.T0006377 | 296.1481 | 6 | Point Repair at 63 ft from 06377 | 4750 | 4750
125 | 18 | D | N18 | SS.GM.T0000718 | SS.MH.T0004343 | SS.MH.T0005356 | 574.5271 | 6 | Point Repair at 18, 217 and 476 ft from 05356 | 14250 | 14250
126 | 18 | D | O18 | SS.GM.T0000720 | SS.MH.T0004337 | SS.MH.T0004346 | 752.2692 | 6 | Burst to 8" - 1 svc | 49897.4966 | 49897.4966
127 | 18 | D | O18 | SS.GM.T0000731 | SS.MH.T0011936 | SS.MH.T0004356 | 208.9849 | 6 | Access; Clean and Inspection | 835.9396 | 835.9396
128 | 18 | E | O18 | SS.GM.T0000732 | SS.MH.T0004352 | SS.MH.T0004350 | 437.8917 | 6 | Point Repair at 87 and 228 ft from 04352 and Add to Root Removal Schedule | 9773.7684 | 9773.7684
129 | 18 | D | O18 | SS.GM.T0000735 | SS.MH.T0004349 | SS.MH.T0004367 | 642.797 | 6 | Point Repair at 100, 120 and 226 ft from 04349 | 14250 | 14250
130 | 18 | D | N18 | SS.GM.T0000744 | SS.MH.T0010989 | SS.MH.T0005154 | 149.6191 | 6 | Point Repair at 153 ft from 05154 | 4750 | 4750
131 | 18 | D | N18 | SS.GM.T0000746 | SS.MH.T0011968 | SS.MH.T0005150 | 127.1171 | 6 | Point Repair at 50 and 96 ft from 05150 | 9500 | 9500
132 | 18 | D | N18 | SS.GM.T0000748 | SS.MH.T0010704 | SS.MH.T0005225 | 215.7472 | 6 | Point Repair at 106 ft from 05225 | 4750 | 4750
133 | 18 | D | N19 | SS.GM.T0000750 | SS.MH.T0012190 | SS.MH.T0005234 | 204.2418 | 6 | Point Repair at 53 ft from 05234 | 4750 | 4750
134 | 18 | D | N19 | SS.GM.T0000751 | SS.MH.T0010990 | SS.MH.T0005233 | 486.223 | 6 | Burst to 8" - 7 svc | 38604.4969 | 38604.4969
135 | 18 | D | M19 | SS.GM.T0000829 | SS.MH.T0011011 | SS.MH.T0003628 | 120.552 | 6 | Burst to 8" - 0 svc | 7835.8777 | 7835.8777
136 | 18 | D | M19 | SS.GM.T0000832 | SS.MH.T0012358 | SS.MH.T0003625 | 60.7508 | 6 | Point Repair at 12358 | 4750 | 4750
137 | 18 | D | M19 | SS.GM.T0000999 | SS.MH.T0010243 | SS.MH.T0003580 | 388.218 | 8 | Burst to 10" - 1 svc | 30116.3527 | 30116.3527
138 | 18 | D | M19 | SS.GM.T0001000 | SS.MH.T0010244 | SS.MH.T0010243 | 89.6539 | 8 | Burst to 10" - 0 svc | 6724.0409 | 6724.0409
139 | 18 | D | M19 | SS.GM.T0001001 | SS.MH.T0003637 | SS.MH.T0010244 | 79.9127 | 8 | 8" CIPP - 0 svc | 3596.0735 | 3596.0735
140 | 18 | D | M19 | SS.GM.T0001048 | SS.MH.T0003502 | SS.MH.T0014957 | 590.0087 | 6 | Burst to 8" - 12 svc | 50350.5648 | 50350.5648
141 | 18 | D | M19 | SS.GM.T0001049 | SS.MH.T0003441 | SS.MH.T0003442 | 807.8928 | 6 | Burst to 8" - 5 svc | 57513.03 | 57513.03
142 | 18 | D | M19 | SS.GM.T0001050 | SS.MH.T0003440 | SS.MH.T0003441 | 352.4237 | 6 | Burst to 8" - 4 svc | 26907.5394 | 26907.5394
143 | 18 | D | M19 | SS.GM.T0001051 | SS.MH.T0003439 | SS.MH.T0003440 | 292.9135 | 6 | Burst to 8" - 5 svc | 24039.3757 | 24039.3757
144 | 18 | D | M19 | SS.GM.T0001052 | SS.MH.T0005575 | SS.MH.T0003439 | 400.6804 | 6 | Burst to 8" - 2 svc | 28044.2234 | 28044.2234
145 | 18 | D | M19 | SS.GM.T0001054 | SS.MH.T0000340 | SS.MH.T0003446 | 420.853 | 6 | Point Repair at 357 ft from 00340 | 4750 | 4750
146 | 18 | D | M19 | SS.GM.T0001055 | SS.MH.T0003442 | SS.MH.T0003447 | 601.6527 | 6 | Burst to 8" - 2 svc | 41107.4231 | 41107.4231
147 | 18 | D | M19 | SS.GM.T0001056 | SS.MH.T0009338 | SS.MH.T0003442 | 648.913 | 6 | Burst to 8" - 0 svc | 42179.3466 | 42179.3466
148 | 18 | D | M19 | SS.GM.T0001071 | SS.MH.T0003504 | SS.MH.T0003503 | 256.1777 | 8 | Point Repair at 228 ft from 03504 | 4750 | 4750
149 | 18 | D | N19 | SS.GM.T0001153 | SS.MH.T0005305 | SS.MH.T0006216 | 343.7041 | 6 | Burst to 8" - 6 svc | 28340.7642 | 28340.7642
150 | 18 | D | N19 | SS.GM.T0001154 | SS.MH.T0000300 | SS.MH.T0005305 | 575.4202 | 6 | Burst to 8" - 6 svc | 43402.3137 | 43402.3137
151 | 18 | D | N19 | SS.GM.T0001155 | SS.MH.T0000299 | SS.MH.T0000300 | 316.5467 | 6 | Point Repair at 93 ft from 00299 | 4750 | 4750
152 | 18 | D | O18 | SS.GM.T0001205 | SS.MH.T0006097 | SS.MH.T0000286 | 418.2852 | 8 | Point Repair at 302 ft and Grout Joint at 19 ft from 00286 | 5550 | 5550
153 | 18 | D | O18 | SS.GM.T0001214 | SS.MH.T0006409 | SS.MH.T0006408 | 290.3002 | 6 | Point Repair at 224, 266 and 290 ft from 06409 | 14250 | 14250
154 | 18 | D | O18 | SS.GM.T0001215 | SS.MH.T0006408 | SS.MH.T0006407 | 437.9128 | 6 | Burst to 8" - 8 svc | 36464.329 | 36464.329
155 | 18 | D | O18 | SS.GM.T0001216 | SS.MH.T0006407 | SS.MH.T0006104 | 301.5899 | 6 | Replace section 44 ft from 06407 to 222 ft from 06104. | 8400 | 8400
156 | 18 | E | O18 | SS.GM.T0001217 | SS.MH.T0006104 | SS.MH.T0006105 | 218.8267 | 6 | Point Repair at 40 ft from 06105. Crossbore | 4750 | 4750
157 | 18 | D | O18 | SS.GM.T0001219 | SS.MH.T0006105 | SS.MH.T0006106 | 100.3932 | 6 | Point Repair at 43 ft from 06105 | 4750 | 4750
158 | 18 | D | O18 | SS.GM.T0001220 | SS.MH.T0006106 | SS.MH.T0006107 | 244.3824 | 6 | Replace section 20 to 70 ft from 06106. | 6000 | 6000
159 | 18 | D | N19 | SS.GM.T0001226 | SS.MH.T0006266 | SS.MH.T0006265 | 512.0593 | 18 | Point Repair at 49, 72, 96 and 213 ft from 06266 | 19000 | 19000
160 | 18 | D | N19 | SS.GM.T0001227 | SS.MH.T0006267 | SS.MH.T0006266 | 471.9002 | 18 | 18" CIPP - 0 svc | 56628.025 | 56628.025
161 | 18 | D | N19 | SS.GM.T0001228 | SS.MH.T0006233 | SS.MH.T0006267 | 397.9151 | 18 | Point Repair at 5 ft from 06267 | 4750 | 4750
162 | 18 | D | N19 | SS.GM.T0001229 | SS.MH.T0005265 | SS.MH.T0005264 | 430.1357 | 18 | Point Repair at 141 and 165 ft from 05265 | 9500 | 9500
163 | 18 | D | O18 | SS.GM.T0001239 | SS.MH.T0004366 | SS.MH.T0015309 | 97.0002 | 8 | Point Repair at 80 ft from 04366 | 4750 | 4750
164 | 18 | D | O18 | SS.GM.T0001240 | SS.MH.T0004365 | SS.MH.T0004366 | 125.6328 | 8 | Burst to 10" - 0 svc | 9422.458 | 9422.458
165 | 18 | D | O18 | SS.GM.T0001244 | SS.MH.T0004369 | SS.MH.T0015720 | 302.399 | 6 | Point Repair at 200 and 298 ft from 04369 | 9500 | 9500
166 | 18 | D | O18 | SS.GM.T0001246 | SS.MH.T0006384 | SS.MH.T0004371 | 402.218 | 6 | Burst to 8" - 0 svc | 26144.1678 | 26144.1678
167 | 18 | D | O18 | SS.GM.T0001248 | SS.MH.T0006382 | SS.MH.T0006383 | 229.0867 | 6 | Burst to 8" - 0 svc | 14890.6344 | 14890.6344
168 | 18 | D | O18 | SS.GM.T0001249 | SS.MH.T0012333 | SS.MH.T0006381 | 554.6579 | 6 | Point Repair at 120 ft from 06381 and Add to Root Removal Schedule | 5859.3159 | 5859.3159
169 | 18 | D | O18 | SS.GM.T0001250 | SS.MH.T0004370 | SS.MH.T0004369 | 111.9751 | 6 | Burst to 8" - 0 svc | 7278.382 | 7278.382
170 | 18 | D | O18 | SS.GM.T0001261 | SS.MH.T0010699 | SS.MH.T0006135 | 264.8111 | 6 | Grout Joint at 211 and 227 ft from 06135 | 1600 | 1600
171 | 18 | D | M19 | SS.GM.T0001266 | SS.MH.T0014315 | SS.MH.T0015768 | 354.7227 | 8 | Burst to 10" - 0 svc | 26604.1992 | 26604.1992
172 | 18 | D | M19 | SS.GM.T0001281 | SS.MH.T0011017 | SS.MH.T0003440 | 411.7654 | 6 | Burst to 8" - 3 svc | 29764.7491 | 29764.7491
173 | 18 | D | M19 | SS.GM.T0001282 | SS.MH.T0012365 | SS.MH.T0003441 | 617.5323 | 6 | Burst to 8" - 1 svc | 41139.5971 | 41139.5971
174 | 18 | D | M19 | SS.GM.T0001287 | SS.MH.T0004161 | SS.MH.T0004127 | 101.6898 | 6 | Access; Clean and Inspection | 406.7591 | 406.7591
175 | 18 | D | M19 | SS.GM.T0001289 | SS.MH.T0011228 | SS.MH.T0000361 | 119.7339 | 6 | Point Repair at 3 ft from 00361 | 4750 | 4750
176 | 18 | D | M20 | SS.GM.T0001298 | SS.MH.T0011241 | SS.MH.T0003500 | 44.2065 | 6 | Point Repair at 33 ft from 03500 to remove blockage | 4750 | 4750
177 | 18 | D | N19 | SS.GM.T0001323 | SS.MH.T0012375 | SS.MH.T0006146 | 178.4477 | 6 | Point Repair at 46, 63 and 102 ft from 06146 | 14250 | 14250
178 | 18 | D | N19 | SS.GM.T0001326 | SS.MH.T0000284 | SS.MH.T0006089 | 131.4784 | 6 | Burst to 8" - 0 svc | 8546.094 | 8546.094
179 | 18 | D | N19 | SS.GM.T0001328 | SS.MH.T0006086 | SS.MH.T0006088 | 318.521 | 6 | Burst to 8" - 5 svc | 25703.8641 | 25703.8641
180 | 18 | D | N19 | SS.GM.T0001329 | SS.MH.T0006085 | SS.MH.T0006086 | 346.957 | 6 | Point Repair at 203, 271 and 340 ft from 06085 | 14250 | 14250
181 | 18 | D | N19 | SS.GM.T0001330 | SS.MH.T0000283 | SS.MH.T0006083 | 304.5807 | 6 | Point Repair at 155, 175 and 296 ft from 00283 | 14250 | 14250
182 | 18 | D | N19 | SS.GM.T0001331 | SS.MH.T0006083 | SS.MH.T0006085 | 299.6218 | 6 | Burst to 8" - 5 svc | 24475.4171 | 24475.4171
183 | 18 | D | N19 | SS.GM.T0001333 | SS.MH.T0011954 | SS.MH.T0000283 | 146.8205 | 6 | Point Repair at 69 and 154 ft from 00283 | 9500 | 9500
184 | 18 | D | N19 | SS.GM.T0001334 | SS.MH.T0006084 | SS.MH.T0006083 | 148.3852 | 6 | Point Repair at 26 and 36 ft from 06083 | 9500 | 9500
185 | 18 | D | N19 | SS.GM.T0001335 | SS.MH.T0012347 | SS.MH.T0006084 | 149.0586 | 6 | Construct Cleanout at End Of Line | 3000 | 3000
186 | 18 | D | N19 | SS.GM.T0001336 | SS.MH.T0012196 | SS.MH.T0006085 | 193.6532 | 6 | Burst to 8" - 4 svc | 16587.4604 | 16587.4604
187 | 18 | D | N19 | SS.GM.T0001337 | SS.MH.T0011955 | SS.MH.T0006086 | 667.1199 | 6 | Burst to 8" - 2 svc | 45362.7948 | 45362.7948
188 | 18 | D | N19 | SS.GM.T0001339 | SS.MH.T0012355 | SS.MH.T0006087 | 656.6452 | 6 | Point Repair at 92 and 271 ft from 06087 | 9500 | 9500
189 | 18 | D | N19 | SS.GM.T0001348 | SS.MH.T0006264 | SS.MH.T0006262 | 512.3367 | 6 | Point Repair at 484 and 489 ft from 06264 | 9500 | 9500
190 | 18 | D | N19 | SS.GM.T0001350 | SS.MH.T0011121 | SS.MH.T0006263 | 315.0413 | 6 | Construct Cleanout at End Of Line | 3000 | 3000
191 | 18 | D | N19 | SS.GM.T0001351 | SS.MH.T0012370 | SS.MH.T0006263 | 348.4588 | 6 | Burst to 8" - 6 svc | 28649.8219 | 28649.8219
192 | 18 | D | N19 | SS.GM.T0001352 | SS.MH.T0012199 | SS.MH.T0006264 | 353.2997 | 6 | Point Repair at 132 ft from 06264 | 4750 | 4750
193 | 18 | D | O19 | SS.GM.T0001359 | SS.MH.T0005577 | SS.MH.T0005535 | 944.3114 | 6 | Point Repair at 180, 657 and 893 ft from 05577 | 14250 | 14250
194 | 18 | D | N19 | SS.GM.T0001361 | SS.MH.T0011122 | SS.MH.T0000300 | 66.1432 | 6 | Point Repair at 39 and 59 ft from 00300 | 9500 | 9500
195 | 18 | D | N19 | SS.GM.T0001362 | SS.MH.T0011118 | SS.MH.T0000299 | 276.4539 | 6 | Burst to 8" - 4 svc | 21969.5054 | 21969.5054
196 | 18 | D | N19 | SS.GM.T0001367 | SS.MH.T0005376 | SS.MH.T0005524 | 592.729 | 6 | Point Repair at 13, 175, 221, 269, 270 and 364 ft from 05376 and 25 ft from 05524 | 28500 | 28500
197 | 18 | D | O19 | SS.GM.T0001369 | SS.MH.T0005379 | SS.MH.T0014964 | 424.0378 | 6 | Point Repair at 58 ft from 14964 | 4750 | 4750
198 | 18 | D | N20 | SS.GM.T0001413 | SS.MH.T0005595 | SS.MH.T0005594 | 232.286 | 8 | Point Repair at 50 ft from 05595 | 4750 | 4750
199 | 18 | D | N20 | SS.GM.T0001424 | SS.MH.T0005301 | SS.MH.T0005302 | 612.2766 | 6 | Point Repair at 145, 270 and 337 ft from 05301 | 14250 | 14250
200 | 18 | D | N20 | SS.GM.T0001425 | SS.MH.T0005304 | SS.MH.T0005303 | 485.7743 | 6 | Point Repair at 275 and 387 ft from 05304 | 9500 | 9500
201 | 18 | D | M21 | SS.GM.T0001458 | SS.MH.T0004152 | SS.MH.T0000363 | 322.3217 | 6 | Grout Joint at 99 and 193 ft from 04152 | 1600 | 1600
202 | 18 | D | O20 | SS.GM.T0001470 | SS.MH.T0005434 | SS.MH.T0006173 | 322.6411 | 10 | Point Repair at 307 ft from 06173 | 4750 | 4750
203 | 18 | D | O20 | SS.GM.T0001472 | SS.MH.T0005437 | SS.MH.T0005438 | 402.1002 | 10 | Point Repair at 90, 98, 283, 303 and 325 from 05438. | 23750 | 23750
204 | 18 | D | O21 | SS.GM.T0001475 | SS.MH.T0005444 | SS.MH.T0005443 | 157.7616 | 8 | Point Repair at 210 ft from 05444 | 4750 | 4750
205 | 18 | D | N20 | SS.GM.T0001499 | SS.MH.T0005388 | SS.MH.T0005389 | 153.489 | 6 | Point Repair at 69 ft from 05398 and 20 ft from 05388 | 9500 | 9500
206 | 18 | D | P20 | SS.GM.T0001572 | SS.MH.T0006080 | SS.MH.T0006184 | 501.4582 | 6 | Replace section 292 to 390 ft from 06184. | 11760 | 11760
207 | 18 | D | P20 | SS.GM.T0001575 | SS.MH.T0006186 | SS.MH.T0006189 | 238.1468 | 12 | Replace section 166 ft from 06189 to 06186. | 10730 | 10730
208 | 18 | D | P20 | SS.GM.T0001576 | SS.MH.T0006189 | SS.MH.T0006190 | 277.2496 | 12 | Point Repair at 144, 153 and 163 ft from 06189 | 14250 | 14250
209 | 18 | D | O18 | SS.GM.T0001650 | SS.MH.T0009956 | SS.MH.T0006801 | 357.4063 | 6 | Point Repair at 13 and 91 ft from 06801 | 9500 | 9500
210 | 18 | D | N19 | SS.GM.T0001655 | SS.MH.T0005538 | SS.MH.T0015095 | 66.0194 | 12 | Point Repair at 5 and 25 ft from 15095 | 9500 | 9500
211 | 18 | D | O19 | SS.GM.T0001660 | SS.MH.T0004177 | SS.MH.T0004178 | 425.4342 | 6 | Point Repair at 271 ft and Grout Joint at 51, 82 and 146 ft from 04177 | 7150 | 7150
212 | 18 | D | O19 | SS.GM.T0001669 | SS.MH.T0006239 | SS.MH.T0006960 | 551.3878 | 6 | Point Repair at 53 ft from 06239 | 4750 | 4750
213 | 18 | D | O19 | SS.GM.T0001671 | SS.MH.T0006961 | SS.MH.T0006960 | 303.3001 | 6 | Point Repair at 184 and 199 ft from 06961 | 9500 | 9500
214 | 18 | D | O19 | SS.GM.T0001676 | SS.MH.T0006945 | SS.MH.T0006946 | 720.7235 | 6 | Burst to 8" - 9 svc | 55847.0282 | 55847.0282
215 | 18 | D | O19 | SS.GM.T0001680 | SS.MH.T0011018 | SS.MH.T0005367 | 75.4327 | 6 | Point Repair at 15 ft from 05367 | 4750 | 4750
216 | 18 | D | O19 | SS.GM.T0001681 | SS.MH.T0011022 | SS.MH.T0012863 | 112.4204 | 6 | Burst to 8" - 0 svc | 7307.3279 | 7307.3279
217 | 18 | D | O19 | SS.GM.T0001684 | SS.MH.T0006230 | SS.MH.T0006229 | 151.3323 | 8 | Point Repair at 16 and 23 ft from 06229 | 9500 | 9500
218 | 18 | D | O19 | SS.GM.T0001688 | SS.MH.T0012376 | SS.MH.T0006232 | 21.0117 | 6 | Point Repair at 5 ft from 06232 | 4750 | 4750
219 | 18 | D | O19 | SS.GM.T0001689 | SS.MH.T0006232 | SS.MH.T0006231 | 242.6874 | 8 | Replace section 160 to 200 ft from 06232. | 5200 | 5200
220 | 18 | D | O19 | SS.GM.T0001691 | SS.MH.T0006236 | SS.MH.T0006235 | 332.1335 | 6 | Point Repair at 77 and 116 ft from 06236 | 9500 | 9500
221 | 18 | D | O19 | SS.GM.T0001694 | SS.MH.T0006238 | SS.MH.T0006237 | 393.2502 | 6 | Point Repair at 348 and 385 ft from 06238 | 9500 | 9500
222 | 18 | D | O19 | SS.GM.T0001695 | SS.MH.T0006237 | SS.MH.T0015437 | 411.4505 | 6 | Point Repair at 161 and 257 ft from 06237 | 9500 | 9500
223 | 18 | D | O20 | SS.GM.T0001701 | SS.MH.T0006228 | SS.MH.T0006977 | 464.0488 | 12 | Replace section 0 to 100 ft from 06228. | 14500 | 14500
224 | 18 | D | N20 | SS.GM.T0001717 | SS.MH.T0011239 | SS.MH.T0005304 | 481.4771 | 6 | Point Repair at 70 ft from 05304 | 4750 | 4750
225 | 18 | D | N20 | SS.GM.T0001735 | SS.MH.T0012393 | SS.MH.T0005389 | 465.1081 | 6 | Point Repair at 12 ft from 12393 and 232 ft from 05389 | 9500 | 9500
226 | 18 | D | O19 | SS.GM.T0001750 | SS.MH.T0006113 | SS.MH.T0000287 | 539.7058 | 6 | Point Repair at 261 and 504 ft from 06113 | 9500 | 9500
227 | 18 | D | O19 | SS.GM.T0001756 | SS.MH.T0012356 | SS.MH.T0006115 | 275.2578 | 6 | Burst to 8" - 7 svc | 24891.7588 | 24891.7588
228 | 18 | D | O19 | SS.GM.T0001757 | SS.MH.T0012357 | SS.MH.T0014965 | 173.7789 | 6 | Point Repair at 146 ft from 14965 | 4750 | 4750
229 | 18 | D | O19 | SS.GM.T0001758 | SS.MH.T0011958 | SS.MH.T0006112 | 63.0002 | 6 | Burst to 8" - 0 svc | 4095.0106 | 4095.0106
230 | 18 | D | O19 | SS.GM.T0001759 | SS.MH.T0011225 | SS.MH.T0006249 | 126.4998 | 6 | Point Repair at 88 and 101 ft from 06249 | 9500 | 9500
231 | 18 | D | O19 | SS.GM.T0001760 | SS.MH.T0006111 | SS.MH.T0015578 | 379.0865 | 8 | Replace section 180 to 252 ft from 06111. | 9360 | 9360
232 | 18 | D | N19 | SS.GM.T0001762 | SS.MH.T0006139 | SS.MH.T0006118 | 320.076 | 8 | Point Repair at 7, 32, 142 and 175 ft from 06139 | 19000 | 19000
233 | 18 | D | P20 | SS.GM.T0001774 | SS.MH.T0006278 | SS.MH.T0006279 | 371.1081 | 6 | Point Repair at 178, 182 and 350 ft from 06279 | 14250 | 14250
234 | 18 | D | P21 | SS.GM.T0001788 | SS.MH.T0000329 | SS.MH.T0007744 | 228.5176 | 10 | Point Repair at 73, 77 and 87 ft from 07744 | 19000 | 19000
235 | 18 | D | N18 | SS.GM.T0002025 | SS.MH.T0005982 | SS.MH.T0004332 | 344.8335 | 6 | Point Repair at 5 ft from 05982 | 4750 | 4750
236 | 18 | D | N19 | SS.GM.T0002026 | SS.MH.T0015152 | SS.MH.T0005609 | 285.1612 | 8 | Point Repair at 10 ft from 05609 and Access; Clean and Inspection | 5890.645 | 5890.645
237 | 18 | D | N19 | SS.GM.T0002033 | SS.MH.T0006146 | SS.MH.T0001687 | 289.3101 | 6 | Point Repair at 68 ft from 01687 and Grout Joint at 19 ft from 06146 | 5550 | 5550
238 | 18 | D | M19 | SS.GM.T0002048 | SS.MH.T0003577 | SS.MH.T0004133 | 39.0228 | 8 | Burst to 10" - 0 svc | 2926.7109 | 2926.7109
239 | 18 | D | M19 | SS.GM.T0002253 | SS.MH.T0000692 | SS.MH.T0003439 | 288.0697 | 6 | Burst to 8" - 2 svc | 20724.5282 | 20724.5282
240 | 18 | D | M19 | SS.GM.T0002419 | SS.MH.T0003629 | SS.MH.T0003628 | 157.9327 | 6 | Point Repair at 43 ft from 03629 | 4750 | 4750
241 | 18 | D | M19 | SS.GM.T0002420 | SS.MH.T0003628 | SS.MH.T0005171 | 392.2822 | 6 | Point Repair at 97 ft from 03628 | 4750 | 4750
242 | 18 | D | M20 | SS.GM.T0002437 | SS.MH.T0003575 | SS.MH.T0003576 | 108.4469 | 8 | Burst to 8" - 0 svc | 7049.047 | 7049.047
243 | 18 | D | M19 | SS.GM.T0002487 | SS.MH.T0003445 | SS.MH.T0015765 | 233.1963 | 6 | Point Repair at 46 ft from 03445 | 4750 | 4750
244 | 18 | D | M19 | SS.GM.T0002488 | SS.MH.T0003446 | SS.MH.T0015763 | 394.7996 | 6 | Burst to 8" - 1 svc | 26661.9742 | 26661.9742
245 | 18 | D | N18 | SS.GM.T0002543 | SS.MH.T0004333 | SS.MH.T0005982 | 623.2267 | 6 | Point Repair at 27 and 224 ft and Grout Joint 449 from 04333 and Grout Joint at 92 and 167 ft from 05982 | 15850 | 15850
246 | 18 | D | N18 | SS.GM.T0002556 | SS.MH.T0004313 | SS.MH.T0004314 | 117.1642 | 8 | Point Repair at 46, 86 and 104 ft from 04314 | 14250 | 14250
247 | 18 | D | N18 | SS.GM.T0002557 | SS.MH.T0004310 | SS.MH.T0004305 | 238.8002 | 6 | Point Repair at 109, 112 and 219 ft from 04310 | 14250 | 14250
248 | 18 | D | N18 | SS.GM.T0002558 | SS.MH.T0004309 | SS.MH.T0004307 | 322.0978 | 6 | Burst to 8" - 4 svc | 24936.3585 | 24936.3585
249 | 18 | D | N18 | SS.GM.T0002560 | SS.MH.T0004290 | SS.MH.T0004289 | 584.823 | 6 | Burst to 8" - 5 svc | 43013.4934 | 43013.4934
250 | 18 | D | N18 | SS.GM.T0002562 | SS.MH.T0004288 | SS.MH.T0004281 | 878.1234 | 6 | Point Repair at 33 ft from 04281 | 4750 | 4750
251 | 18 | D | N18 | SS.GM.T0002564 | SS.MH.T0004283 | SS.MH.T0004284 | 325.1102 | 8 | Point Repair at 194 ft from 04283 and Add to Root Removal Schedule | 5400.2204 | 5400.2204
252 | 18 | D | N18 | SS.GM.T0002565 | SS.MH.T0004251 | SS.MH.T0004280 | 402.921 | 6 | Point Repair at 137, 147 and 210 ft from 04280 | 14250 | 14250
253 | 18 | D | N18 | SS.GM.T0002566 | SS.MH.T0004277 | SS.MH.T0004278 | 334.0815 | 6 | Point Repair at 14 & 16 and 271 ft from 04278 and 16 ft from 04277 | 19000 | 19000
254 | 18 | D | N18 | SS.GM.T0002567 | SS.MH.T0004280 | SS.MH.T0004277 | 368.0723 | 6 | Point Repair at 61 ft from 04277 | 4750 | 4750
255 | 18 | D | N18 | SS.GM.T0002570 | SS.MH.T0010167 | SS.MH.T0004267 | 895.4034 | 6 | Point Repair at 216, 226 and 240 ft from 04267 | 14250 | 14250
256 | 18 | D | N19 | SS.GM.T0002621 | SS.MH.T0005374 | SS.MH.T0005373 | 201.7994 | 6 | Point Repair at 58 ft from 05373 | 4750 | 4750
257 | 18 | D | N19 | SS.GM.T0002622 | SS.MH.T0005373 | SS.MH.T0005372 | 395.1372 | 6 | Point Repair at 240, 280 and 313 ft from 05373 | 14250 | 14250
258 | 18 | D | N19 | SS.GM.T0002623 | SS.MH.T0005371 | SS.MH.T0005372 | 590.0594 | 6 | Point Repair at 168 ft from 05371 | 4750 | 4750
259 | 18 | D | N20 | SS.GM.T0002625 | SS.MH.T0009321 | SS.MH.T0006214 | 297.0986 | 6 | Point Repair at 48, 271, 281 and 290 ft from 06124 | 19000 | 19000
260 | 18 | D | N20 | SS.GM.T0002628 | SS.MH.T0006212 | SS.MH.T0015027 | 304.867 | 6 | Grout Joint at 101 ft from 15027 | 800 | 800
261 | 18 | D | N19 | SS.GM.T0002632 | SS.MH.T0005523 | SS.MH.T0005524 | 311.2647 | 6 | Point Repair at 182 ft from 05523 | 4750 | 4750
262 | 18 | D | N19 | SS.GM.T0002633 | SS.MH.T0005524 | SS.MH.T0005522 | 520.1665 | 6 | Replace section from 05522 to 20 ft from 05522 | 3440.3331 | 3440.3331
263 | 18 | D | N18 | SS.GM.T0002682 | SS.MH.T0004347 | SS.MH.T0004345 | 323.5798 | 6 | Point Repair at 18, 22 and 152 ft from 04345 | 14250 | 14250
264 | 18 | D | N18 | SS.GM.T0002683 | SS.MH.T0004342 | SS.MH.T0005360 | 338.0319 | 6 | Burst to 8" - 3 svc | 24972.0743 | 24972.0743
265 | 18 | E | N18 | SS.GM.T0002684 | SS.MH.T0000338 | SS.MH.T0004339 | 704.8913 | 6 | Point Repair of Crossbore at 85 ft from 00338 | 4750 | 4750
266 | 18 | D | O18 | SS.GM.T0002687 | SS.MH.T0006406 | SS.MH.T0006407 | 399.9959 | 6 | Point Repair at 361 ft from 06406 | 4750 | 4750
267 | 18 | D | O18 | SS.GM.T0002688 | SS.MH.T0006405 | SS.MH.T0006406 | 258.1974 | 6 | Point Repair at 149 ft from 06405 | 4750 | 4750
268 | 18 | D | O18 | SS.GM.T0002697 | SS.MH.T0006392 | SS.MH.T0006391 | 847.1232 | 6 | Point Repair at 125, 303, 360 ft from 06392 and 38 ft from 06391 | 19000 | 19000
269 | 18 | D | O18 | SS.GM.T0002698 | SS.MH.T0006390 | SS.MH.T0013211 | 271.4127 | 6 | Point Repair at 191 ft from 13211 | 4750 | 4750
270 | 18 | D | O18 | SS.GM.T0002699 | SS.MH.T0006389 | SS.MH.T0006388 | 459.2614 | 6 | Point Repair at 235 ft from 06388 and 163 ft from 06389 | 9500 | 9500
271 | 18 | D | O18 | SS.GM.T0002702 | SS.MH.T0006388 | SS.MH.T0006386 | 167.5458 | 6 | Replace section 139 ft from 06388 to 06386. | 3840 | 3840
272 | 18 | D | O18 | SS.GM.T0002703 | SS.MH.T0006381 | SS.MH.T0006382 | 274.0254 | 6 | Replace section 120 to 350 ft from 06381. | 27600 | 27600
273 | 18 | D | O19 | SS.GM.T0002710 | SS.MH.T0000337 | SS.MH.T0005589 | 88.8853 | 6 | Point Repair at 42 ft from 00337 | 4750 | 4750
274 | 18 | D | N18 | SS.GM.T0002719 | SS.MH.T0013973 | SS.MH.T0005358 | 321.0329 | 6 | Point Repair at 9 ft from 05358 | 4750 | 4750
275 | 18 | D | O20 | SS.GM.T0002757 | SS.MH.T0006172 | SS.MH.T0006173 | 314.7701 | 6 | Point Repair at 78 ft from 06173 | 4750 | 4750
276 | 18 | D | N20 | SS.GM.T0002777 | SS.MH.T0005411 | SS.MH.T0005390 | 508.368 | 6 | Point Repair at 158 ft from 05390 | 4750 | 4750
277 | 18 | D | N19 | SS.GM.T0002798 | SS.MH.T0009527 | SS.MH.T0000297 | 186.167 | 6 | Grout Joint at 150 ft from 00297 | 800 | 800
278 | 18 | D | N18 | SS.GM.T0002882 | SS.MH.T0005240 | SS.MH.T0000274 | 371.5913 | 6 | Point Repair at 166, 206 and 308 ft from 05240 | 14250 | 14250
279 | 18 | D | N18 | SS.GM.T0002883 | SS.MH.T0000274 | SS.MH.T0005239 | 34.8233 | 6 | Burst to 8" - 0 svc | 2263.5163 | 2263.5163
280 | 18 | D | N18 | SS.GM.T0002884 | SS.MH.T0005239 | SS.MH.T0005237 | 265.6886 | 6 | Burst to 8" - 0 svc | 17269.7564 | 17269.7564
281 | 18 | D | N18 | SS.GM.T0002885 | SS.MH.T0005224 | SS.MH.T0005223 | 255.3485 | 6 | Point Repair at 16, 29 and 182 ft from 05224 | 14250 | 14250
282 | 18 | D | N19 | SS.GM.T0002908 | SS.MH.T0009302 | SS.MH.T0005178 | 108.4572 | 6 | Point Repair at 23 ft from 09302 | 4750 | 4750
283 | 18 | D | N18 | SS.GM.T0002920 | SS.MH.T0005146 | SS.MH.T0005221 | 1010.6186 | 8 | Replace section 450 to 580 ft from 05146. Point Repair at 90 and 121 ft from 05221 | 26400 | 26400
284 | 18 | D | N18 | SS.GM.T0002922 | SS.MH.T0000750 | SS.MH.T0005221 | 424.512 | 6 | Burst to 8" - 0 svc | 27593.2815 | 27593.2815
285 | 18 | D | N19 | SS.GM.T0003026 | SS.MH.T0006261 | SS.MH.T0006260 | 741.1326 | 6 | Point Repair at 12, 69, 99 and 374 ft from 06261 | 19000 | 19000
286 | 18 | D | N19 | SS.GM.T0003028 | SS.MH.T0006258 | SS.MH.T0006257 | 324.9853 | 6 | Point Repair at 128 ft from 06257 | 4750 | 4750
287 | 18 | D | N19 | SS.GM.T0003030 | SS.MH.T0006256 | SS.MH.T0006255 | 194.6617 | 6 | Replace - 0 svc | 23359.4022 | 23359.4022
288 | 18 | D | N19 | SS.GM.T0003031 | SS.MH.T0006255 | SS.MH.T0006254 | 35.9489 | 6 | Burst to 8" - 0 svc | 2336.678 | 2336.678
289 | 18 | D | N19 | SS.GM.T0003032 | SS.MH.T0006254 | SS.MH.T0006251 | 95.5752 | 6 | Point Repair at 70 ft from 06254 | 4750 | 4750
290 | 18 | D | N19 | SS.GM.T0003036 | SS.MH.T0013995 | SS.MH.T0005545 | 490.7916 | 6 | Point Repair at 297, 389, 412 and 452 ft from 13995 | 19000 | 19000
291 | 18 | D | N19 | SS.GM.T0003037 | SS.MH.T0005542 | SS.MH.T0005543 | 639.1969 | 6 | Burst to 8" - 13 svc | 54547.7985 | 54547.7985
292 | 18 | D | N19 | SS.GM.T0003041 | SS.MH.T0005535 | SS.MH.T0005536 | 304.9886 | 6 | Point Repair at 86, 144 and 165 ft from 05536 | 14250 | 14250
293 | 18 | D | N19 | SS.GM.T0003042 | SS.MH.T0014477 | SS.MH.T0005535 | 503.6249 | 6 | Point Repair at 113, 150 and 186 ft from 05535 | 14250 | 14250
294 | 18 | D | N19 | SS.GM.T0003045 | SS.MH.T0000322 | SS.MH.T0005532 | 34.8429 | 6 | Point Repair at 38 ft from 00322 | 4750 | 4750
295 | 18 | D | N19 | SS.GM.T0003046 | SS.MH.T0005531 | SS.MH.T0006234 | 43.4839 | 6 | Point Repair at 29 ft from 05531 | 4750 | 4750
296 | 18 | D | O19 | SS.GM.T0003049 | SS.MH.T0006248 | SS.MH.T0006249 | 474.9362 | 6 | Point Repair at 352 ft from 06249 and Roor Removal Program | 5699.8725 | 5699.8725
297 | 18 | D | O19 | SS.GM.T0003053 | SS.MH.T0006243 | SS.MH.T0006244 | 308.2855 | 8 | Replace section 70 to 130 ft from 06244. | 7800 | 7800
298 | 18 | D | O19 | SS.GM.T0003064 | SS.MH.T0006965 | SS.MH.T0006964 | 425.1749 | 6 | Point Repair at 149 ft from 06965 | 4750 | 4750
299 | 18 | D | O19 | SS.GM.T0003065 | SS.MH.T0000292 | SS.MH.T0006957 | 473.2223 | 8 | Point Repair at 245 ft from 06957 and Add to Root Removal Schedule | 5696.4445 | 5696.4445
300 | 18 | D | O19 | SS.GM.T0003071 | SS.MH.T0005290 | SS.MH.T0005289 | 196.6339 | 8 | Point Repair at 173 ft from 05290 | 4750 | 4750
301 | 18 | D | O19 | SS.GM.T0003072 | SS.MH.T0005289 | SS.MH.T0005288 | 397.9717 | 8 | Replace section 65 to 95 ft from 05288 and Point Repair at 142 and 157 ft from 05289 | 13400 | 13400
302 | 18 | D | P20 | SS.GM.T0003073 | SS.MH.T0005285 | SS.MH.T0006984 | 403.33 | 8 | Point Repair at 104 and 131 ft from 05285 and 224, 253 and 274 from 06984. | 23750 | 23750
303 | 18 | D | O19 | SS.GM.T0003074 | SS.MH.T0005281 | SS.MH.T0005282 | 498.1408 | 8 | Replace section 60 to 90 ft and Point Repair at 152, 176, 200, 230 and 263 ft from 05281 | 27650 | 27650
304 | 18 | D | O19 | SS.GM.T0003075 | SS.MH.T0015204 | SS.MH.T0005281 | 430.9269 | 8 | Point Repair at 66 ft from 15204 | 4750 | 4750
305 | 18 | D | P20 | SS.GM.T0003077 | SS.MH.T0005276 | SS.MH.T0006271 | 45.1952 | 6 | Burst to 8" - 0 svc | 2937.6868 | 2937.6868
306 | 18 | D | O19 | SS.GM.T0003082 | SS.MH.T0009585 | SS.MH.T0005271 | 35.3269 | 8 | Point Repair at 09585 | 4750 | 4750
307 | 18 | D | O19 | SS.GM.T0003095 | SS.MH.T0006132 | SS.MH.T0000290 | 232.2515 | 6 | Point Repair at 102, 185, 194, 197 and 215 ft from 06132 | 23750 | 23750
308 | 18 | D | O19 | SS.GM.T0003096 | SS.MH.T0000290 | SS.MH.T0006117 | 63.1573 | 6 | Point Repair at 65 ft from 06117 | 4750 | 4750
309 | 18 | D | O19 | SS.GM.T0003099 | SS.MH.T0013181 | SS.MH.T0000287 | 678.5928 | 8 | 8" CIPP - 2 svc | 32536.6757 | 32536.6757
310 | 18 | D | O19 | SS.GM.T0003116 | SS.MH.T0012868 | SS.MH.T0004180 | 241.4956 | 6 | Point Repair at 62 and 84 ft from 04180 | 9500 | 9500
311 | 18 | D | M19 | SS.GM.T0003138 | SS.MH.T0009612 | SS.MH.T0000725 | 132.0711 | 6 | Point Repair at 122 ft from 00725 | 4750 | 4750
312 | 18 | D | M19 | SS.GM.T0003313 | SS.MH.T0003626 | SS.MH.T0005170 | 593.1477 | 6 | Point Repair at 333 and 354 ft from 03626 | 9500 | 9500
313 | 18 | D | M19 | SS.GM.T0003314 | SS.MH.T0003422 | SS.MH.T0003629 | 548.8495 | 6 | Point Repair at 95 and 373 ft and Grout Joint at 120 ft from 03422 | 10300 | 10300
314 | 18 | D | M19 | SS.GM.T0003327 | SS.MH.T0015020 | SS.MH.T0003575 | 207.4379 | 8 | Point Repair at 17 ft from 15020 | 4750 | 4750
315 | 18 | D | M19 | SS.GM.T0003358 | SS.MH.T0003453 | SS.MH.T0003446 | 250.0932 | 6 | Point Repair at 56, 88, 176 and 179 ft from 03446 | 19000 | 19000
316 | 18 | D | M19 | SS.GM.T0003359 | SS.MH.T0003450 | SS.MH.T0003447 | 263.8089 | 6 | Burst to 8" - 1 svc | 18147.5809 | 18147.5809
317 | 18 | D | N18 | SS.GM.T0003405 | SS.MH.T0004293 | SS.MH.T0004312 | 420.8257 | 6 | Burst to 8" - 3 svc | 30353.6674 | 30353.6674
318 | 18 | D | N18 | SS.GM.T0003408 | SS.MH.T0004282 | SS.MH.T0004283 | 285.9237 | 6 | Replace section 20 to 42 ft from 04283. | 2640 | 2640
319 | 18 | D | N18 | SS.GM.T0003409 | SS.MH.T0004281 | SS.MH.T0004282 | 319.7838 | 6 | Point Repair at 124, 135, 193 and 208 ft from 04281 | 19000 | 19000
320 | 18 | D | N18 | SS.GM.T0003410 | SS.MH.T0004274 | SS.MH.T0004281 | 353.4259 | 6 | Burst to 8" - 6 svc. Crossbore @ 96 & 320 ft from 04274 | 28972.6843 | 28972.6843
321 | 18 | D | N18 | SS.GM.T0003411 | SS.MH.T0004287 | SS.MH.T0004283 | 527.7107 | 8 | Point Repair at 483 ft from 04287 and Add to Root Removal Schedule | 5805.4214 | 5805.4214
322 | 18 | D | O20 | SS.GM.T0003448 | SS.MH.T0010163 | SS.MH.T0006214 | 295.3129 | 6 | Point Repair at 41, 179, 109 and 287 ft from 06214 | 19000 | 19000
323 | 18 | D | N20 | SS.GM.T0003449 | SS.MH.T0005526 | SS.MH.T0006210 | 281.7043 | 6 | Point Repair at 2 ft from 05526 | 4750 | 4750
324 | 18 | D | M19 | SS.GM.T0003537 | SS.MH.T0011231 | SS.MH.T0005575 | 456.0842 | 6 | Burst to 8" - 8 svc | 37645.4711 | 37645.4711
325 | 18 | D | O18 | SS.GM.T0003554 | SS.MH.T0004357 | SS.MH.T0004358 | 327.9129 | 6 | Point Repair at 50 ft from 04358 and Add to Root Removal Schedule | 5405.8258 | 5405.8258
326 | 18 | D | O18 | SS.GM.T0003555 | SS.MH.T0004354 | SS.MH.T0013193 | 216.5256 | 6 | Point Repair at 104 ft from 04354 | 4750 | 4750
327 | 18 | D | O18 | SS.GM.T0003557 | SS.MH.T0004359 | SS.MH.T0004368 | 427.9334 | 8 | Burst to 10" - 0 svc | 32095.0044 | 32095.0044
328 | 18 | D | N18 | SS.GM.T0003561 | SS.MH.T0011217 | SS.MH.T0005361 | 229.517 | 6 | Burst to 8" - 3 svc | 17918.6072 | 17918.6072
329 | 18 | D | N18 | SS.GM.T0003563 | SS.MH.T0012326 | SS.MH.T0000338 | 362.2548 | 6 | Point Repair at 145 ft from 00338 | 4750 | 4750
330 | 18 | D | O18 | SS.GM.T0003578 | SS.MH.T0011215 | SS.MH.T0006394 | 182.9219 | 6 | Point Repair at 11215 | 4750 | 4750
331 | 18 | D | O18 | SS.GM.T0003583 | SS.MH.T0009953 | SS.MH.T0006390 | 236.8812 | 6 | Burst to 8" - 0 svc | 15397.2791 | 15397.2791
332 | 18 | D | O18 | SS.GM.T0003584 | SS.MH.T0006377 | SS.MH.T0006378 | 384.5263 | 6 | Burst to 8" - 0 svc | 24994.2115 | 24994.2115
333 | 18 | D | N18 | SS.GM.T0003585 | SS.MH.T0006376 | SS.MH.T0006377 | 331.3335 | 6 | Point Repair at 102 and 257 ft from 06376 and Add to Root Removal Schedule | 10162.6669 | 10162.6669
334 | 18 | D | N18 | SS.GM.T0003592 | SS.MH.T0012180 | SS.MH.T0004309 | 431.9029 | 6 | Point Repair at 9, 16, 44 and 52 ft from 04309 | 19000 | 19000
335 | 18 | D | N18 | SS.GM.T0003593 | SS.MH.T0012328 | SS.MH.T0004310 | 324.3882 | 6 | Point Repair at 47 ft from 04310 | 4750 | 4750
336 | 18 | D | N18 | SS.GM.T0003594 | SS.MH.T0011187 | SS.MH.T0004313 | 620.1447 | 6 | Burst to 8" - 8 svc | 48309.408 | 48309.408
337 | 18 | D | N18 | SS.GM.T0003596 | SS.MH.T0011519 | SS.MH.T0004290 | 519.7516 | 6 | Burst to 8" - 3 svc | 36783.8566 | 36783.8566
338 | 18 | D | N17 | SS.GM.T0003600 | SS.MH.T0012303 | SS.MH.T0014988 | 419.2039 | 6 | Point Repair at 95 ft from 14988 | 4750 | 4750
339 | 18 | D | N18 | SS.GM.T0003604 | SS.MH.T0011198 | SS.MH.T0000274 | 559.5547 | 6 | Point Repair at 74 ft from 00274 | 4750 | 4750
340 | 18 | D | O19 | SS.GM.T0003607 | SS.MH.T0006117 | SS.MH.T0015721 | 219.6152 | 6 | Point Repair at 25 ft from 06117 | 4750 | 4750
341 | 18 | D | N18 | SS.GM.T0003616 | SS.MH.T0005360 | SS.MH.T0006364 | 323.8401 | 6 | Point Repair at 80, 243, 261 and 286 ft from 05360 | 19000 | 19000
342 | 18 | D | N18 | SS.GM.T0003621 | SS.MH.T0011203 | SS.MH.T0006364 | 484.3835 | 6 | Point Repair at 223, 309 and 316 ft from 06364 | 14250 | 14250
343 | 18 | D | N18 | SS.GM.T0003622 | SS.MH.T0005363 | SS.MH.T0015646 | 487.7117 | 6 | Point Repair at 32 ft and Grout Joint at 19 ft from 15646 | 5550 | 5550
344 | 18 | D | N21 | SS.GM.T0003741 | SS.MH.T0005412 | SS.MH.T0005411 | 563.7068 | 6 | Point Repair at 222 ft from 05412 and 123 ft from 05411 | 9500 | 9500
345 | 18 | D | N20 | SS.GM.T0003749 | SS.MH.T0005390 | SS.MH.T0005389 | 54.3082 | 6 | Point Repair at 28 ft from 05389 | 4750 | 4750
346 | 18 | D | N20 | SS.GM.T0003755 | SS.MH.T0000579 | SS.MH.T0005604 | 322.7589 | 6 | Replace 240 ft from 05604 to 00579 | 9960 | 9960
347 | 18 | D | N20 | SS.GM.T0003756 | SS.MH.T0000578 | SS.MH.T0000305 | 130.2064 | 8 | Burst to 8" - 0 svc | 8463.4173 | 8463.4173
348 | 18 | D | N20 | SS.GM.T0003763 | SS.MH.T0006153 | SS.MH.T0005307 | 296.4378 | 18 | Point Repair at 67, 82 and 91 ft from 06153 | 14250 | 14250
349 | 18 | D | N19 | SS.GM.T0003771 | SS.MH.T0001687 | SS.MH.T0013834 | 142.1911 | 6 | Point Repair at 136 ft from 01687 | 4750 | 4750
350 | 18 | D | N19 | SS.GM.T0003824 | SS.MH.T0005186 | SS.MH.T0013654 | 221.2362 | 6 | Point Repair at 4 ft from 13654 and Access; Clean and Inspection | 5634.945 | 5634.945
351 | 18 | D | N18 | SS.GM.T0003832 | SS.MH.T0004315 | SS.MH.T0005145 | 440.0745 | 8 | Point Repair at 27, 37, 161 and 164 ft from 04315 | 19000 | 19000
352 | 18 | D | P20 | SS.GM.T0003952 | SS.MH.T0006271 | SS.MH.T0006274 | 430.5374 | 6 | Point Repair at 93 ft from 06274 | 4750 | 4750
353 | 18 | D | P20 | SS.GM.T0003956 | SS.MH.T0006289 | SS.MH.T0006288 | 259.8719 | 6 | Point Repair at 250 ft from 06288 | 4750 | 4750
354 | 18 | D | N20 | SS.GM.T0003970 | SS.MH.T0011245 | SS.MH.T0005311 | 550.9249 | 6 | Point Repair at 249 ft from 05311 | 4750 | 4750
355 | 18 | D | N19 | SS.GM.T0003980 | SS.MH.T0000323 | SS.MH.T0000322 | 301.7528 | 6 | Point Repair at 164, 190, 199 and 226 ft from 00323 | 19000 | 19000
356 | 18 | D | N19 | SS.GM.T0003981 | SS.MH.T0012198 | SS.MH.T0005534 | 166.664 | 6 | Point Repair at 10, 21, 46, 56 and 60 ft from 05534 | 23750 | 23750
357 | 18 | D | O19 | SS.GM.T0003984 | SS.MH.T0010881 | SS.MH.T0005537 | 734.9365 | 6 | Point Repair at 169 and 210 ft from 05537 | 9500 | 9500
358 | 18 | D | O19 | SS.GM.T0003987 | SS.MH.T0010870 | SS.MH.T0005542 | 641.3262 | 6 | Burst to 8" - 2 svc | 43686.2061 | 43686.2061
359 | 18 | D | N19 | SS.GM.T0003988 | SS.MH.T0011012 | SS.MH.T0005531 | 479.4263 | 6 | Burst to 8" - 8 svc | 39162.7085 | 39162.7085
360 | 18 | D | O19 | SS.GM.T0003989 | SS.MH.T0011009 | SS.MH.T0005544 | 456.1101 | 6 | Point Repair at 175 ft from 05544 and Add to Root Removal Schedule | 5662.2203 | 5662.2203
361 | 18 | D | O19 | SS.GM.T0003990 | SS.MH.T0012360 | SS.MH.T0006248 | 357.8505 | 6 | Point Repair at 49 ft from 06248 | 4750 | 4750
362 | 18 | D | O19 | SS.GM.T0004001 | SS.MH.T0006226 | SS.MH.T0006227 | 70.2401 | 10 | Point Repair at 14 ft from 06226 | 4750 | 4750
363 | 18 | D | O19 | SS.GM.T0004002 | SS.MH.T0006227 | SS.MH.T0006228 | 355.4217 | 12 | Point Repair at 94 and 127 ft from 06227 and 27 and 53 ft from 06228 | 19000 | 19000
364 | 18 | D | O19 | SS.GM.T0004003 | SS.MH.T0006960 | SS.MH.T0006959 | 400.1205 | 6 | Point Repair at 162 ft from 06960 | 4750 | 4750
365 | 18 | D | O19 | SS.GM.T0004004 | SS.MH.T0010214 | SS.MH.T0006963 | 377.3519 | 6 | Point Repair at 172, 245 and 255 ft from 06963 and Add to Root Removal Schedule | 15004.7037 | 15004.7037
366 | 18 | D | O19 | SS.GM.T0004006 | SS.MH.T0006964 | SS.MH.T0006958 | 441.7023 | 6 | Point Repair at 117 and 308 ft from 06964 | 9500 | 9500
367 | 18 | D | O19 | SS.GM.T0004009 | SS.MH.T0005286 | SS.MH.T0005287 | 312.1472 | 6 | Burst to 8" - 5 svc | 25289.5672 | 25289.5672
368 | 18 | D | P20 | SS.GM.T0004015 | SS.MH.T0005284 | SS.MH.T0005285 | 358.209 | 8 | Point Repair at 134, 137, 140, 255, 264 and 272 ft from 05284 | 28500 | 28500
369 | 18 | D | O19 | SS.GM.T0004018 | SS.MH.T0005282 | SS.MH.T0000321 | 222.0628 | 8 | Point Repair at 54 ft from 00321 | 4750 | 4750
370 | 18 | D | O19 | SS.GM.T0004022 | SS.MH.T0005267 | SS.MH.T0006098 | 253.262 | 8 | Point Repair at 28 and 53 ft from 05267 | 9500 | 9500
371 | 18 | D | O19 | SS.GM.T0004029 | SS.MH.T0000287 | SS.MH.T0015723 | 389.9481 | 8 | 8" CIPP - 2 svc | 19547.6623 | 19547.6623
372 | 18 | D | O19 | SS.GM.T0004031 | SS.MH.T0006249 | SS.MH.T0006111 | 614.9576 | 6 | Point Repair at 110 ft from 06249 | 4750 | 4750
373 | 18 | D | N19 | SS.GM.T0004034 | SS.MH.T0012193 | SS.MH.T0005244 | 671.1629 | 6 | Point Repair at 15, 82 and 137 ft from 05244 | 14250 | 14250
374 | 18 | D | N18 | SS.GM.T0004036 | SS.MH.T0010995 | SS.MH.T0005240 | 773.0088 | 6 | Point Repair at 36, 12, 295 and 301 ft from 05240 | 19000 | 19000
375 | 18 | D | N18 | SS.GM.T0004037 | SS.MH.T0011952 | SS.MH.T0005238 | 232.1432 | 6 | Burst to 8" - 2 svc | 17089.3049 | 17089.3049
376 | 18 | D | N18 | SS.GM.T0004041 | SS.MH.T0011113 | SS.MH.T0000750 | 618.6347 | 6 | Burst to 8" - 7 svc | 47211.2583 | 47211.2583
377 | 18 | D | N18 | SS.GM.T0009459 | SS.MH.T0010062 | SS.MH.T0000631 | 210.2832 | 6 | Point Repair at 208 ft from 00631 | 4750 | 4750
378 | 18 | D | N18 | SS.GM.T0009460 | SS.MH.T0010063 | SS.MH.T0004315 | 497.5681 | 6 | Burst to 8" - 12 svc | 44341.9246 | 44341.9246
379 | 18 | D | N18 | SS.GM.T0009461 | SS.MH.T0006336 | SS.MH.T0000632 | 161.8312 | 8 | Point Repair at 39 ft from 06336 | 4750 | 4750
380 | 18 | D | N18 | SS.GM.T0009464 | SS.MH.T0000633 | SS.MH.T0004282 | 211.5387 | 6 | Point Repair at 33 and 63 ft from 04282 | 9500 | 9500
381 | 18 | D | N18 | SS.GM.T0009466 | SS.MH.T0000634 | SS.MH.T0004283 | 235.4945 | 6 | Grout Joint at 41 ft from 04283 | 800 | 800
382 | 18 | D | N18 | SS.GM.T0009469 | SS.MH.T0005222 | SS.MH.T0005978 | 129.4936 | 8 | Burst to 8" - 0 svc | 8417.0839 | 8417.0839
383 | 18 | D | N18 | SS.GM.T0014969 | SS.MH.T0005978 | SS.MH.T0015099 | 120 | 8 | Burst to 8" - 0 svc | 7800 | 7800
384 | 18 | D | N18 | SS.GM.T0009470 | SS.MH.T0015099 | SS.MH.T0005242 | 160.5069 | 8 | Burst to 8" - 0 svc | 10432.9461 | 10432.9461
385 | 18 | D | N18 | SS.GM.T0009471 | SS.MH.T0005242 | SS.MH.T0005977 | 375.0701 | 8 | Burst to 8" - 0 svc | 24379.5571 | 24379.5571
386 | 18 | D | N18 | SS.GM.T0009472 | SS.MH.T0005977 | SS.MH.T0005976 | 33.5029 | 8 | Burst to 8" - 0 svc | 2177.6907 | 2177.6907
387 | 18 | D | N18 | SS.GM.T0009474 | SS.MH.T0005235 | SS.MH.T0005980 | 164.8907 | 6 | Burst to 8" - 0 svc | 10717.8967 | 10717.8967
388 | 18 | D | N18 | SS.GM.T0009477 | SS.MH.T0004329 | SS.MH.T0004332 | 351.7733 | 6 | Point Repair at 276 and 347 ft and Grout Joint at 16 ft from 04329 and Add to Root Removal Schedule | 11003.5466 | 11003.5466
389 | 18 | D | N18 | SS.GM.T0009478 | SS.MH.T0005142 | SS.MH.T0005981 | 748.0122 | 6 | Burst to 8" - 10 svc | 58620.7903 | 58620.7903
390 | 18 | D | N18 | SS.GM.T0009480 | SS.MH.T0005238 | SS.MH.T0005235 | 339.2255 | 6 | Burst to 8" - 0 svc | 22049.66 | 22049.66
391 | 18 | D | P20 | SS.GM.T0009652 | SS.MH.T0006192 | SS.MH.T0007024 | 374.0961 | 12 | Point Repair at 196, 342, 354, 369 and 374 ft from 06192 and Add to Root Removal Schedule | 24498.1921 | 24498.1921
392 | 18 | D | N20 | SS.GM.T0009676 | SS.MH.T0005311 | SS.MH.T0000844 | 285.934 | 6 | Point Repair at 66, 165 and 247 ft from 05311 | 14250 | 14250
393 | 18 | D | N20 | SS.GM.T0009684 | SS.MH.T0005313 | SS.MH.T0000848 | 313.7999 | 8 | Point Repair at 126, 131 and 139 ft from 05313 | 14250 | 14250
394 | 18 | D | N20 | SS.GM.T0009688 | SS.MH.T0006211 | SS.MH.T0006209 | 264.0802 | 6 | Replace section 34 to 48 ft from 06209. Point Repair at 167 ft from 06209 | 6430 | 6430
395 | 18 | D | O19 | SS.GM.T0009690 | SS.MH.T0006894 | SS.MH.T0000320 | 31.3907 | 6 | Burst to 8" - 1 svc | 3040.3954 | 3040.3954
396 | 18 | D | O21 | SS.GM.T0009704 | SS.MH.T0015732 | SS.MH.T0000654 | 316.3034 | 6 | Point Repair at 312 ft from 15732 | 4750 | 4750
397 | 18 | D | N18 | SS.GM.T0009767 | SS.MH.T0011102 | SS.MH.T0000631 | 398.8428 | 6 | Burst to 8" - 2 svc | 27924.7836 | 27924.7836
398 | 18 | D | N18 | SS.GM.T0009768 | SS.MH.T0011189 | SS.MH.T0010063 | 221.7245 | 6 | Point Repair at 152 and 193 ft from 10063 | 9500 | 9500
399 | 18 | D | N18 | SS.GM.T0009773 | SS.MH.T0012750 | SS.MH.T0005975 | 498.3869 | 6 | Point Repair at 23 ft from 05975 | 4750 | 4750
400 | 18 | D | N18 | SS.GM.T0009775 | SS.MH.T0012752 | SS.MH.T0005241 | 126.113 | 6 | Point Repair at 44 ft from 05241 | 4750 | 4750
401 | 18 | D | N20 | SS.GM.T0010341 | SS.MH.T0005331 | SS.MH.T0006154 | 439.0476 | 15 | 15" CIPP - 1 svc | 36123.8107 | 36123.8107
402 | 18 | D | N20 | SS.GM.T0010342 | SS.MH.T0000569 | SS.MH.T0005332 | 500.7548 | 15 | Point Repair at 157, 470 and 478 ft from 00569 | 14250 | 14250
403 | 18 | D | Q19 | SS.GM.T0010442 | SS.MH.T0007669 | SS.MH.T0007668 | 89.6427 | 8 | Grout Joint at 5 ft from 07668 | 800 | 800
404 | 18 | D | O21 | SS.GM.T0010839 | SS.MH.T0007701 | SS.MH.T0007699 | 407.6806 | 6 | Burst to 8" - 10 svc | 36499.2398 | 36499.2398
405 | 18 | D | O21 | SS.GM.T0010861 | SS.MH.T0007695 | SS.MH.T0007694 | 501.5605 | 6 | Burst to 8" - 1 svc | 33601.431 | 33601.431
406 | 18 | D | O20 | SS.GM.T0011431 | SS.MH.T0015436 | SS.MH.T0006973 | 446.4479 | 12 | 12" CIPP - 0 svc | 31251.3523 | 31251.3523
407 | 18 | D | O20 | SS.GM.T0011530 | SS.MH.T0007979 | SS.MH.T0007980 | 85.0328 | 8 | Point Repair at 26 ft from 07979 | 4750 | 4750
408 | 18 | D | O20 | SS.GM.T0011695 | SS.MH.T0010457 | SS.MH.T0008123 | 187.9735 | 6 | Construct Cleanout at End Of Line | 3000 | 3000
409 | 18 | D | Q19 | SS.GM.T0012058 | SS.MH.T0008598 | SS.MH.T0009285 | 402.7001 | 10 | Point Repair at 124 ft from 08598 | 4750 | 4750
410 | 18 | D | N20 | SS.GM.T0012772 | SS.MH.T0009884 | SS.MH.T0005336 | 87.0049 | 6 | Point Repair at 9 ft from 05336 | 4750 | 4750
411 | 18 | D | O20 | SS.GM.T0012829 | SS.MH.T0001473 | SS.MH.T0001472 | 364.304 | 8 | Grout Joint at 199 ft from 01473 | 800 | 800
412 | 18 | D | N20 | SS.GM.T0012879 | SS.MH.T0005332 | SS.MH.T0005330 | 380.6832 | 15 | 15" CIPP - 2 svc | 32454.6528 | 32454.6528
413 | 18 | D | N20 | SS.GM.T0012880 | SS.MH.T0005330 | SS.MH.T0005331 | 114.5445 | 15 | Point Repair at 39 ft from 05330 | 4750 | 4750
414 | 18 | D | O20 | SS.GM.T0012900 | SS.MH.T0005443 | SS.MH.T0005441 | 270.4557 | 8 | Locate and Expose 13056; Clean and CCTV | 2431.8228 | 2431.8228
415 | 18 | D | N20 | SS.GM.T0012902 | SS.MH.T0006154 | SS.MH.T0006153 | 199.6464 | 15 | 15" CIPP - 0 svc | 15971.7081 | 15971.7081
416 | 18 | D | N18 | SS.GM.T0012995 | SS.MH.T0005163 | SS.MH.T0013309 | 477.5874 | 6 | Point Repair at 35 and 344 ft from 05163 | 9500 | 9500
417 | 18 | D | O19 | SS.GM.T0013273 | SS.MH.T0011226 | SS.MH.T0013096 | 393.2816 | 6 | Point Repair at 75 and 81 ft from 13096 | 9500 | 9500
418 | 18 | D | O19 | SS.GM.T0013367 | SS.MH.T0006109 | SS.MH.T0006110 | 157.7413 | 6 | Burst to 8" - 0 svc | 10253.1852 | 10253.1852
419 | 18 | D | N19 | SS.GM.T0013373 | SS.MH.T0013185 | SS.MH.T0013186 | 16.9109 | 10 | Point Repair at 13 ft from 13185 | 4750 | 4750
420 | 18 | D | O18 | SS.GM.T0013377 | SS.MH.T0010988 | SS.MH.T0006138 | 10.4361 | 6 | Burst to 8" - 0 svc | 678.3455 | 678.3455
421 | 18 | D | Q19 | SS.GM.T0013396 | SS.MH.T0013205 | SS.MH.T0013206 | 213.5094 | 8 | Point Repair at 188 and 121 ft from 13205 | 9500 | 9500
422 | 18 | D | N21 | SS.GM.T0013420 | SS.MH.T0005422 | SS.MH.T0009277 | 259.7341 | 6 | Burst to 8" - 0 svc | 16882.7193 | 16882.7193
423 | 18 | D | N19 | SS.GM.T0013427 | SS.MH.T0013948 | SS.MH.T0000323 | 227.6438 | 6 | Construct Cleanout at End Of Line | 3000 | 3000
424 | 18 | D | O20 | SS.GM.T0013455 | SS.MH.T0013277 | SS.MH.T0013279 | 281.3647 | 12 | Point Repair at 166 ft from 13279 | 4750 | 4750
425 | 18 | D | O19 | SS.GM.T0013457 | SS.MH.T0005541 | SS.MH.T0013284 | 325.5508 | 8 | Replace section from 05541 to 20 ft from 05541 | 2600 | 2600
426 | 18 | D | N19 | SS.GM.T0013458 | SS.MH.T0005536 | SS.MH.T0013286 | 209.2345 | 6 | Point Repair at 113 ft from 05536 | 4750 | 4750
427 | 18 | D | N19 | SS.GM.T0013461 | SS.MH.T0013285 | SS.MH.T0015026 | 56.79 | 12 | Burst to 18" - 1 svc | 6395.0457 | 6395.0457
428 | 18 | D | N18 | SS.GM.T0014031 | SS.MH.T0013992 | SS.MH.T0004278 | 535.3812 | 8 | Point Repair at 161 ft from 13992 and Add to Root Removal Schedule | 5820.7624 | 5820.7624
429 | 18 | D | N18 | SS.GM.T0014033 | SS.MH.T0004344 | SS.MH.T0013994 | 643.1355 | 8 | Replace section 30 to 70 ft from 04344. | 5200 | 5200
430 | 18 | D | O19 | SS.GM.T0014034 | SS.MH.T0005544 | SS.MH.T0013995 | 441.225 | 6 | Burst to 8" - 8 svc | 36679.6266 | 36679.6266
431 | 18 | D | N19 | SS.GM.T0014401 | SS.MH.T0005534 | SS.MH.T0014477 | 458.4323 | 6 | Point Repair at 36 and 57 ft from 05534 | 9500 | 9500
432 | 18 | D | N19 | SS.GM.T0014496 | SS.MH.T0005154 | SS.MH.T0005155 | 345.049 | 6 | Point Repair at 327 ft from 05154 | 4750 | 4750
433 | 18 | D | M19 | SS.GM.T0014843 | SS.MH.T0014957 | SS.MH.T0003442 | 539.1347 | 8 | Burst to 8" - 5 svc | 40043.7548 | 40043.7548
434 | 18 | D | O19 | SS.GM.T0014846 | SS.MH.T0014964 | SS.MH.T0005376 | 339.7005 | 6 | Point Repair at 33, 59, 105, 128, 196 and 302 ft from 14964 | 28500 | 28500
435 | 18 | E | O19 | SS.GM.T0014849 | SS.MH.T0014971 | SS.MH.T0013986 | 224.607 | 6 | Point Repair at 122 and 158 ft from 13986 | 9500 | 9500
436 | 18 | D | M19 | SS.GM.T0014852 | SS.MH.T0014968 | SS.MH.T0011011 | 267.9371 | 6 | Point Repair at 123 ft from 14968 | 4750 | 4750
437 | 18 | D | O19 | SS.GM.T0014869 | SS.MH.T0014994 | SS.MH.T0014993 | 313.7998 | 8 | Replace - 1 svc | 41793.9753 | 41793.9753
438 | 18 | D | O19 | SS.GM.T0014871 | SS.MH.T0014995 | SS.MH.T0014994 | 415.9322 | 8 | Replace - 8 svc | 62071.1812 | 62071.1812
439 | 18 | D | N19 | SS.GM.T0014897 | SS.MH.T0014998 | SS.MH.T0005608 | 149.6685 | 8 | Point Repair at 50 ft from 05608 | 4750 | 4750
440 | 18 | D | P20 | SS.GM.T0014928 | SS.MH.T0015030 | SS.MH.T0012387 | 196.2057 | 6 | Grout Joint at 63 ft from 12387 | 800 | 800
441 | 18 | D | N19 | SS.GM.T0014949 | SS.MH.T0015094 | SS.MH.T0000324 | 509.3116 | 6 | Burst to 8" - 5 svc | 38105.253 | 38105.253
442 | 18 | D | N19 | SS.GM.T0014950 | SS.MH.T0000324 | SS.MH.T0000323 | 404.5365 | 6 | Point Repair at 11 and 210 ft from 00324 | 9500 | 9500
443 | 18 | D | N18 | SS.GM.T0014968 | SS.MH.T0015098 | SS.MH.T0005223 | 19.7377 | 6 | Point Repair at 11 ft from 05223 | 4750 | 4750
444 | 18 | D | O18 | SS.GM.T0014974 | SS.MH.T0015104 | SS.MH.T0006401 | 98.1367 | 6 | Point Repair at 100 ft from 06401 | 4750 | 4750
445 | 18 | D | N19 | SS.GM.T0015069 | SS.MH.T0015439 | SS.MH.T0005263 | 92.8681 | 12 | 12" CIPP - 0 svc | 6500.7656 | 6500.7656
446 | 18 | D | O20 | SS.GM.T0015098 | SS.MH.T0015313 | SS.MH.T0007914 | 105.2895 | 6 | Point Repair at 45 ft from 07914 and Access; Clean and Inspection | 5171.1581 | 5171.1581
447 | 18 | D | O18 | SS.GM.T0015117 | SS.MH.T0015208 | SS.MH.T0013213 | 199.9998 | 8 | Burst to 8" - 1 svc | 13999.9879 | 13999.9879
448 | 18 | D | O18 | SS.GM.T0015118 | SS.MH.T0015207 | SS.MH.T0013212 | 280.3046 | 6 | Burst to 8" - 1 svc | 19219.7991 | 19219.7991
449 | 18 | D | N18 | SS.GM.T0015323 | SS.MH.T0015646 | SS.MH.T0005359 | 390.1413 | 6 | Point Repair at 89 and 263 ft from 05359 and Add to Root Removal Schedule | 10280.2825 | 10280.2825
450 | 18 | D | M19 | SS.GM.T0015407 | SS.MH.T0015763 | SS.MH.T0003445 | 53.7448 | 6 | Burst to 8" - 1 svc | 4493.4108 | 4493.4108
451 | 18 | D | M19 | SS.GM.T0015422 | SS.MH.T0015765 | SS.MH.T0003450 | 168.3448 | 6 | Point Repair at 32, 46 and 64 ft from 03450 | 14250 | 14250
452 | 18 | D | M19 | SS.GM.T0015428 | SS.MH.T0010878 | SS.MH.T0014315 | 200.0845 | 8 | Burst to 10" - 0 svc | 15006.3411 | 15006.3411
453 | 18 | D | O19 | SS.GM.T0015484 | SS.MH.T0015722 | SS.MH.T0000288 | 59.0652 | 0 | Point Repair at 55 ft from 00288 | 4750 | 4750
454 | 18 | D | O18 | SS.GM.T0015693 | SS.MH.T0006360 | SS.MH.T0015851 | 119.9 | 6 | Burst to 8" - 1 svc | 8793.5 | 8793.5
455 | 21 | D | P18 | SS.GM.T0000972 | SS.MH.T0006347 | SS.MH.T0006348 | 346.3268 | 6 | Point Repair at 53, 81, 137 and 294 ft from 06347 | 19000 | 19000
456 | 21 | D | P18 | SS.GM.T0000973 | SS.MH.T0006346 | SS.MH.T0006347 | 322.7464 | 6 | Point Repair at 34, 88, 139, 159, 170 and 231 ft from 06346 | 28500 | 28500
457 | 21 | D | O18 | SS.GM.T0000974 | SS.MH.T0000335 | SS.MH.T0006352 | 317.7599 | 6 | Burst to 8" - 5 svc | 25654.3962 | 25654.3962
458 | 21 | D | O18 | SS.GM.T0000976 | SS.MH.T0006345 | SS.MH.T0006346 | 278.3719 | 6 | Point Repair at 276 ft from 06346 | 4750 | 4750
459 | 21 | D | O18 | SS.GM.T0001181 | SS.MH.T0006415 | SS.MH.T0004375 | 643.9673 | 6 | Point Repair at 505 ft from 06415 | 4750 | 4750
460 | 21 | D | O18 | SS.GM.T0001183 | SS.MH.T0012316 | SS.MH.T0004205 | 184.4117 | 6 | Point Repair at 127, 148 and 164 ft from 04205 | 14250 | 14250
461 | 21 | D | O18 | SS.GM.T0001184 | SS.MH.T0011195 | SS.MH.T0004205 | 232.2457 | 6 | Burst to 8" - 4 svc | 19095.9735 | 19095.9735
462 | 21 | D | O18 | SS.GM.T0001186 | SS.MH.T0006413 | SS.MH.T0006415 | 360.6926 | 6 | Point Repair at 91, 195, 225 and 227 ft from 06413 and Add to Root Removal Schedule | 19721.3852 | 19721.3852
463 | 21 | D | O18 | SS.GM.T0001187 | SS.MH.T0010861 | SS.MH.T0006413 | 272.0111 | 6 | Point Repair at 30 ft from 06413 | 4750 | 4750
464 | 21 | D | P18 | SS.GM.T0001189 | SS.MH.T0011935 | SS.MH.T0006347 | 78.4 | 6 | Construct Cleanout at End Of Line | 3000 | 3000
465 | 21 | D | P19 | SS.GM.T0001391 | SS.MH.T0006927 | SS.MH.T0006926 | 194.7454 | 6 | Point Repair at 77 ft from 06926 | 4750 | 4750
466 | 21 | D | P18 | SS.GM.T0001509 | SS.MH.T0005260 | SS.MH.T0005259 | 430.1071 | 6 | Replace section 220 to 130 ft from 05260. | 10800 | 10800
467 | 21 | D | P18 | SS.GM.T0001510 | SS.MH.T0009519 | SS.MH.T0005260 | 321.6001 | 6 | Point Repair at 254 and 263 ft from 05260 | 9500 | 9500
468 | 21 | D | P18 | SS.GM.T0001514 | SS.MH.T0006049 | SS.MH.T0005567 | 201.928 | 6 | Replace section 29 to 50 ft from 05567 and Point Repair at 5 ft from 06049. | 7270 | 7270
469 | 21 | D | P18 | SS.GM.T0001515 | SS.MH.T0006050 | SS.MH.T0006049 | 127.5111 | 6 | Replace section 12 to 30 ft from 06049. | 2160 | 2160
470 | 21 | D | P18 | SS.GM.T0001516 | SS.MH.T0006007 | SS.MH.T0006050 | 306.4676 | 6 | Point Repair at 238 ft from 06007 | 4750 | 4750
471 | 21 | D | P18 | SS.GM.T0001517 | SS.MH.T0005257 | SS.MH.T0005572 | 385.8977 | 15 | Point Repair at 60 ft from 05257 and CIPP - 0 svc | 22115.3947 | 22115.3947
472 | 21 | D | P18 | SS.GM.T0001544 | SS.MH.T0006023 | SS.MH.T0006022 | 126.7977 | 6 | Point Repair at 89 ft from 06023 | 4750 | 4750
473 | 21 | D | P19 | SS.GM.T0001552 | SS.MH.T0006046 | SS.MH.T0000279 | 61.2789 | 6 | Replace section 8 to 45 ft from 06046 and Point Repair at 5 ft from 00279. | 9190 | 9190
474 | 21 | D | P19 | SS.GM.T0001553 | SS.MH.T0006045 | SS.MH.T0006046 | 182.1683 | 6 | Replace section 12 to 30 ft from 06045. | 2160 | 2160
475 | 21 | D | P19 | SS.GM.T0001704 | SS.MH.T0011119 | SS.MH.T0006207 | 115.1328 | 6 | Point Repair at 64 and 84 ft from 06207 | 9500 | 9500
476 | 21 | D | P18 | SS.GM.T0002586 | SS.MH.T0006325 | SS.MH.T0006321 | 224.3518 | 6 | Point Repair at 106, 115 and 221 ft from 06325 | 14250 | 14250
477 | 21 | D | P19 | SS.GM.T0002600 | SS.MH.T0007029 | SS.MH.T0006317 | 103.8182 | 6 | Point Repair at 67 ft from 07029 | 4750 | 4750
478 | 21 | D | O18 | SS.GM.T0002686 | SS.MH.T0006412 | SS.MH.T0004375 | 1023.5235 | 6 | Point Repair at 28 and 109 ft from 06412 and 11 and 129 ft from 04375 | 19000 | 19000
479 | 21 | D | O19 | SS.GM.T0002791 | SS.MH.T0006161 | SS.MH.T0006162 | 295.9632 | 6 | Point Repair at 292 ft from 06161 | 4750 | 4750
480 | 21 | D | O19 | SS.GM.T0002792 | SS.MH.T0006160 | SS.MH.T0006161 | 393.5708 | 6 | Point Repair at 156 ft from 06160 | 4750 | 4750
481 | 21 | D | P19 | SS.GM.T0002818 | SS.MH.T0006079 | SS.MH.T0006078 | 326.1797 | 6 | Point Repair at 40 ft from 06078 | 4750 | 4750
482 | 21 | D | P19 | SS.GM.T0002820 | SS.MH.T0006073 | SS.MH.T0006074 | 244.7302 | 6 | Point Repair at 274 ft from 06074 | 4750 | 4750
483 | 21 | D | P19 | SS.GM.T0002821 | SS.MH.T0009882 | SS.MH.T0006072 | 413.1594 | 6 | Point Repair at 228 ft from 06072 | 4750 | 4750
484 | 21 | D | P19 | SS.GM.T0002823 | SS.MH.T0013966 | SS.MH.T0007972 | 213.6001 | 6 | Point Repair at 187 ft from 07972 | 4750 | 4750
485 | 21 | D | P19 | SS.GM.T0002833 | SS.MH.T0006915 | SS.MH.T0006916 | 267.0999 | 8 | Point Repair at 146, 149 and 218 ft from 06915 | 14250 | 14250
486 | 21 | D | P19 | SS.GM.T0002835 | SS.MH.T0006913 | SS.MH.T0006914 | 398.325 | 8 | Point Repair at 217 ft from 06913 and Add to Root Removal Schedule | 5546.65 | 5546.65
487 | 21 | D | P19 | SS.GM.T0002837 | SS.MH.T0006911 | SS.MH.T0006912 | 176.1918 | 8 | Point Repair at 5 ft from 06912 | 4750 | 4750
488 | 21 | D | P19 | SS.GM.T0002840 | SS.MH.T0006906 | SS.MH.T0006317 | 517.0098 | 8 | Grout Joint at 29 and 492 ft from 06906 | 1600 | 1600
489 | 21 | D | P19 | SS.GM.T0002842 | SS.MH.T0006904 | SS.MH.T0006903 | 86.6456 | 6 | Point Repair at 20 ft from 06904 | 4750 | 4750
490 | 21 | D | P19 | SS.GM.T0002853 | SS.MH.T0006044 | SS.MH.T0006045 | 114.3765 | 6 | Point Repair at 24 ft from 06045 | 4750 | 4750
491 | 21 | D | P18 | SS.GM.T0002868 | SS.MH.T0006320 | SS.MH.T0006016 | 392.2723 | 8 | Point Repair at 86, 114, 120, 226, 256 and 345 ft from 06320 | 28500 | 28500
492 | 21 | D | P18 | SS.GM.T0002869 | SS.MH.T0006016 | SS.MH.T0006015 | 66.9447 | 8 | Replace section 42 to 20 ft from 06016. | 2860 | 2860
493 | 21 | D | P19 | SS.GM.T0002959 | SS.MH.T0006076 | SS.MH.T0006075 | 110.6002 | 8 | Point Repair at 39 ft from 06075 | 4750 | 4750
494 | 21 | D | P19 | SS.GM.T0003119 | SS.MH.T0012865 | SS.MH.T0006076 | 404.5667 | 8 | Point Repair at 128 ft from 06076 | 4750 | 4750
495 | 21 | D | P18 | SS.GM.T0003141 | SS.MH.T0011197 | SS.MH.T0006007 | 289.255 | 6 | Point Repair at 5 ft from 06007 | 4750 | 4750
496 | 21 | D | P18 | SS.GM.T0003399 | SS.MH.T0006344 | SS.MH.T0006349 | 615.0001 | 6 | Point Repair at 310 ft from 06344 and Add to Root Removal Schedule | 5980.0002 | 5980.0002
497 | 21 | D | P18 | SS.GM.T0003443 | SS.MH.T0006309 | SS.MH.T0006308 | 388.8692 | 6 | Point Repair at 164 and 267 ft from 06309 | 9500 | 9500
498 | 21 | D | O19 | SS.GM.T0003456 | SS.MH.T0015745 | SS.MH.T0006071 | 335.3848 | 6 | Point Repair at 188 and 210 ft from 06071 | 9500 | 9500
499 | 21 | D | O18 | SS.GM.T0003566 | SS.MH.T0011107 | SS.MH.T0000335 | 244.1001 | 6 | Burst to 8" - 6 svc | 21866.5088 | 21866.5088
500 | 21 | D | O18 | SS.GM.T0003567 | SS.MH.T0010698 | SS.MH.T0006351 | 485.8435 | 6 | Burst to 8" - 12 svc | 43579.8273 | 43579.8273
501 | 21 | D | P18 | SS.GM.T0003803 | SS.MH.T0006034 | SS.MH.T0005571 | 102.7689 | 6 | Replace section 85 ft from 06034 to 05571. | 5400 | 5400
502 | 21 | D | P18 | SS.GM.T0003816 | SS.MH.T0006006 | SS.MH.T0005259 | 274.1123 | 6 | Burst to 8" - 5 svc | 22817.3021 | 22817.3021
503 | 21 | D | P18 | SS.GM.T0003817 | SS.MH.T0006322 | SS.MH.T0005255 | 407.2722 | 15 | 15" CIPP - 0 svc | 32581.7778 | 32581.7778
504 | 21 | D | P19 | SS.GM.T0004020 | SS.MH.T0006081 | SS.MH.T0012865 | 615.7387 | 6 | Point Repair at 3 ft from 12865 and Access; Clean and Inspection | 7212.9549 | 7212.9549
505 | 21 | D | P17 | SS.GM.T0004605 | SS.MH.T0010279 | SS.MH.T0006479 | 374.2 | 6 | Point Repair at 228 ft from 06479 | 4750 | 4750
506 | 21 | D | P17 | SS.GM.T0004922 | SS.MH.T0006797 | SS.MH.T0006461 | 138.0423 | 10 | 10" CIPP - 0 svc | 6902.1128 | 6902.1128
507 | 21 | D | P18 | SS.GM.T0004925 | SS.MH.T0006791 | SS.MH.T0006794 | 227.1247 | 6 | Point Repair at 111 ft from 06791 | 4750 | 4750
508 | 21 | D | P17 | SS.GM.T0008551 | SS.MH.T0006548 | SS.MH.T0006550 | 399.1675 | 10 | Replace section 157 ft from 06548 to 06550. | 34020 | 34020
509 | 21 | D | P17 | SS.GM.T0008569 | SS.MH.T0006532 | SS.MH.T0006481 | 273.2804 | 6 | Burst to 8" - 13 svc | 30763.2249 | 30763.2249
510 | 21 | D | P17 | SS.GM.T0008608 | SS.MH.T0009641 | SS.MH.T0000393 | 383.0907 | 6 | Point Repair at 83 and 105 ft from 00393. Corss bore at 105. | 9500 | 9500
511 | 21 | D | P17 | SS.GM.T0009563 | SS.MH.T0006460 | SS.MH.T0006459 | 247.5924 | 10 | Grout Joint at 201 ft from 06460 | 800 | 800
512 | 21 | D | P18 | SS.GM.T0009565 | SS.MH.T0004208 | SS.MH.T0004207 | 237.9531 | 12 | Point Repair at 177, 182 and 224 ft from 04208 | 14250 | 14250
513 | 21 | D | P18 | SS.GM.T0009566 | SS.MH.T0004207 | SS.MH.T0004206 | 273.1784 | 12 | Point Repair at 111 ft from 04207 | 4750 | 4750
514 | 21 | D | P18 | SS.GM.T0009583 | SS.MH.T0006853 | SS.MH.T0006852 | 266.5962 | 6 | Point Repair at 86 ft from 06853 | 4750 | 4750
515 | 21 | D | P18 | SS.GM.T0009586 | SS.MH.T0000639 | SS.MH.T0000638 | 57.9986 | 6 | Burst to 8" - 0 svc | 3769.9064 | 3769.9064
516 | 21 | D | P18 | SS.GM.T0009588 | SS.MH.T0000641 | SS.MH.T0000640 | 226.313 | 6 | Replace section 12 to 32 ft from 00641. | 1200 | 1200
517 | 21 | D | P18 | SS.GM.T0009589 | SS.MH.T0000646 | SS.MH.T0000645 | 395.9231 | 6 | Point Repair at 22 ft from 00645 | 4750 | 4750
518 | 21 | D | P19 | SS.GM.T0009599 | SS.MH.T0006071 | SS.MH.T0006070 | 452.211 | 6 | Point Repair at 349 ft from 06070 | 4750 | 4750
519 | 21 | D | P18 | SS.GM.T0009624 | SS.MH.T0009711 | SS.MH.T0006881 | 298.1 | 6 | Point Repair at 240 ft from 06881 | 4750 | 4750
520 | 21 | D | Q19 | SS.GM.T0009670 | SS.MH.T0006882 | SS.MH.T0006883 | 338.7546 | 6 | Point Repair at 311 ft from 06882 | 4750 | 4750
521 | 21 | D | O18 | SS.GM.T0009783 | SS.MH.T0011912 | SS.MH.T0000335 | 233 | 6 | Burst to 8" - 4 svc | 19145.0025 | 19145.0025
522 | 21 | D | O18 | SS.GM.T0009784 | SS.MH.T0011913 | SS.MH.T0006346 | 454.8735 | 6 | Burst to 8" - 8 svc | 37566.7748 | 37566.7748
523 | 21 | D | P18 | SS.GM.T0009787 | SS.MH.T0011501 | SS.MH.T0006344 | 181 | 6 | Point Repair at 180 ft from 06344. Crossbore | 4750 | 4750
524 | 21 | D | Q19 | SS.GM.T0010240 | SS.MH.T0009826 | SS.MH.T0008646 | 481.4546 | 6 | Point Repair at 376 ft from 08646 | 4750 | 4750
525 | 21 | D | P17 | SS.GM.T0010257 | SS.MH.T0009852 | SS.MH.T0009024 | 317.4078 | 6 | Point Repair at 194 ft from 09024 | 4750 | 4750
526 | 21 | D | P17 | SS.GM.T0010261 | SS.MH.T0009015 | SS.MH.T0007678 | 197.5724 | 6 | Burst to 8" - 0 svc | 12842.2063 | 12842.2063
527 | 21 | D | Q19 | SS.GM.T0011036 | SS.MH.T0007790 | SS.MH.T0007792 | 351.3804 | 8 | Point Repair at 340 ft from 07790 | 4750 | 4750
528 | 21 | D | Q19 | SS.GM.T0011039 | SS.MH.T0008607 | SS.MH.T0007794 | 243.2644 | 8 | Point Repair at 175 ft from 08607 | 4750 | 4750
529 | 21 | D | Q19 | SS.GM.T0012040 | SS.MH.T0008605 | SS.MH.T0015222 | 136.9999 | 6 | Point Repair at 113 and 139 ft from 08605 and 1 ft from 15222 | 14250 | 14250
530 | 21 | D | P18 | SS.GM.T0015114 | SS.MH.T0014729 | SS.MH.T0006023 | 230.0597 | 6 | Grout Joint at 78 ft from 06023 | 800 | 800
531 | 21 | D | Q19 | SS.GM.T0015131 | SS.MH.T0015222 | SS.MH.T0008606 | 189.6492 | 6 | Replace section from 15222 to 40 ft from 15222. | 4800 | 4800
532 | 21 | D | Q19 | SS.GM.T0015133 | SS.MH.T0015224 | SS.MH.T0008652 | 148.4113 | 8 | Point Repair at 3 ft from 15224 | 4750 | 4750
533 | 21 | D | P19 | SS.GM.T0015593 | SS.MH.T0006934 | SS.MH.T0015883 | 260.2917 | 6 | Replace section 40 to 20 ft from 15833. | 2400 | 2400
[9 empty] | Total Estimated Cost |  | 7161905.0746
[9 empty] | Design and Contingency -15% |  | 1074285.7612
[9 empty] | Total Estimated Cost |  | 8236190.8358
8236190.8358